## dbo_CircuitCapabilities
Id | BankId | Afid | DivisionName | SubstationName | BankName | CircuitName | LastChangedBy | DateRevised | CedsaId | CORRECTED CEDSA ID | OperatingVoltageId | SummerLoadFactorId | WinterLoadFactorId | LocationId | SummerNormalOperationalCapabilityAmps | SummerNormalOperationalCapabilityMva | SummerNormalOperationalCapabilityMw | SummerNormalPlanningCapabilityAmps | SummerNormalPlanningCapabilityMva | SummerNormalPlanningCapabilityMw | SummerEmergencyOperationalCapabilityAmps | SummerEmergencyOperationalCapabilityMva | SummerEmergencyOperationalCapabilityMw | SummerEmergencyPlanningCapabilityAmps | SummerEmergencyPlanningCapabilityMva | SummerEmergencyPlanningCapabilityMw | WinterNormalOperationalCapabilityAmps | WinterNormalOperationalCapabilityMva | WinterNormalOperationalCapabilityMw | WinterNormalPlanningCapabilityAmps | WinterNormalPlanningCapabilityMva | WinterNormalPlanningCapabilityMw | WinterEmergencyOperationalCapabilityAmps | WinterEmergencyOperationalCapabilityMva | WinterEmergencyOperationalCapabilityMw | WinterEmergencyPlanningCapabilityAmps | WinterEmergencyPlanningCapabilityMva | WinterEmergencyPlanningCapabilityMw | Notes | TransformerNotes | TransformerDerate | TransformerPlo | TransformerSummerNormalAmps | TransformerSummerEmergencyAmps | TransformerWinterNormalAmps | TransformerWinterEmergencyAmps | DmsGuid
7 | 1016 | {A4EDE244-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SAN LUIS OBISPO | Bank 6 | CB 1104 | PGE\A9S5 | 2016-11-11 10:45:08.1767984 -08:00 | 182631104 | 182631104 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {E826CD21-981A-4BD7-97F3-AE003873C3D1}
8 | 1018 | {A8F9ABC3-671D-11E5-80CA-005056A729E5} | FRESNO | AIRWAYS | Bank 1 | CB 1101 | PGE\JJV7 | 2017-05-01 08:17:45.4738900 -07:00 | 2520401101 | 252041101 | 8 | 3 | 3 | 1 | 550 | 12 | 11.88 | 512 | 11.17 | 11.06 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {6D8A614F-E0C1-41AB-80C0-5E683AC20EB4}
11 | 1018 | {A8F9ABCB-671D-11E5-80CA-005056A729E5} | FRESNO | AIRWAYS | Bank 1 | CB 1102 | PGE\JJV7 | 2017-05-01 08:18:24.0534319 -07:00 | 2520401102 | 252041102 | 8 | 3 | 3 | 1 | 550 | 12 | 11.88 | 512 | 11.17 | 11.06 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {86E3F6A4-99E6-41FA-9EDD-9BE3EDA628E2}
12 | 1018 | {A8F9ABDF-671D-11E5-80CA-005056A729E5} | FRESNO | AIRWAYS | Bank 1 | CB 1103 | PGE\JJV7 | 2016-12-22 13:37:13.9309631 -08:00 | 2520401103 | 252041103 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {88CA398B-BC77-4F83-B2AA-5577A2D396D2}
13 | 1018 | {2717D59C-A5BE-11E5-A1F0-D4BED91EFF1A} | FRESNO | AIRWAYS | Bank 1 | CB 1104 | PGE\JJV7 | 2016-12-22 15:55:34.5859800 -08:00 | 252041104 | 252041104 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | FUTURE- Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {04A1F419-E45C-4D29-B0AD-674C4E00E809}
14 | 1015 | {E1A5F49B-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | GABILAN | Bank 1 | CB 1101 | PGE\ACT0 | 2016-11-23 10:37:37.4720437 -08:00 | 1823301101 | 182331101 | 8 | 3 | 2 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 962 | {B8F10DCD-E4C2-4631-970E-C3777FD64EC0}
15 | 1019 | {A8F9ABF9-671D-11E5-80CA-005056A729E5} | FRESNO | AIRWAYS | Bank 2 | CB 1105 | PGE\JJV7 | 2017-05-01 08:18:59.4661129 -07:00 | 2520401105 | 252041105 | 8 | 3 | 3 | 1 | 550 | 12 | 11.88 | 512 | 11.17 | 11.06 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {737BD670-18A2-44A9-9C99-F7F3D2C72817}
16 | 1019 | {A8F9ABFE-671D-11E5-80CA-005056A729E5} | FRESNO | AIRWAYS | Bank 2 | CB 1106 | PGE\JJV7 | 2016-12-22 15:31:38.1940732 -08:00 | 2520401106 | 252041106 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {65465FB0-52BF-4387-AFF8-1D4396BF5EF9}
17 | 1019 | {2717D5A1-A5BE-11E5-A1F0-D4BED91EFF1A} | FRESNO | AIRWAYS | Bank 2 | CB 1107 | PGE\JJV7 | 2016-12-22 15:54:42.4033110 -08:00 | 252041107 | 252041107 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Future - Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. | This is an idle breaker not online yet | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {7297A148-6CA1-4760-8B72-5E8D6763A4CA}
18 | 1019 | {2717D5A4-A5BE-11E5-A1F0-D4BED91EFF1A} | FRESNO | AIRWAYS | Bank 2 | CB 1108 | PGE\JJV7 | 2016-12-22 15:54:56.0222856 -08:00 | 2520401108 | 252041108 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | In construction 2016 Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {A643F6F4-EF8F-460F-A7B0-C830E9905CFC}
20 | 1020 | {BC692778-0B43-11E6-9D37-D4BED91EFF1A} | FRESNO | ALPAUGH | BANK 1 (Non SCADA) | CB 1103 (Non SCADA) | PGE\JWCp | 2017-03-06 17:28:56.0172997 -08:00 | 2540001103 | 254001103 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 489 | 10.67 | 10.56 | 600 | 13.09 | 12.96 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {422108D3-64E5-4071-B095-571F3047C879}
21 | 1020 | {B41673D9-0B43-11E6-9D37-D4BED91EFF1A} | FRESNO | ALPAUGH | BANK 1 (Non SCADA) | CB 1104 (Non SCADA) | PGE\JWCp | 2017-03-06 17:28:29.0400585 -08:00 | 2540001104 | 254001104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 489 | 10.67 | 10.56 | 600 | 13.09 | 12.96 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {3AE37D76-8E3A-42A2-B690-832C9E640672}
22 | 1022 | {A8F9AC0C-671D-11E5-80CA-005056A729E5} | FRESNO | ALPAUGH | Bank 2 (Non SCADA) | CB 1105 (Non SCADA) | PGE\A6C7 | 2016-07-12 14:38:41.3738270 -07:00 | 254001105 | 254001105 | 8 | 4 | 3 | 1 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {00000000-0000-0000-0000-000000000000}
23 | 1022 | {A8F9AC0F-671D-11E5-80CA-005056A729E5} | FRESNO | ALPAUGH | Bank 2 (Non SCADA) | CB 1106 | PGE\JWCp | 2017-03-06 17:27:54.0429781 -08:00 | 2540001106 | 254001106 | 8 | 4 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 550 | 12 | 11.88 | 549 | 11.98 | 11.86 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {4B99BBE7-C03E-44BC-A439-875091D8476B}
25 | 1023 | {A8F9AC1D-671D-11E5-80CA-005056A729E5} | FRESNO | ANGIOLA | Bank 1 | CB 1102 (Non SCADA) | PGE\HSB5 | 2016-12-27 14:47:37.1371722 -08:00 | 2521501102 | 252151102 | 8 | 4 | 3 | 1 | 435 | 9.49 | 9.4 | 435 | 9.49 | 9.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {15E71369-1EAD-4B2B-B5E4-275A41914351}
26 | 1023 | {A8F9AC26-671D-11E5-80CA-005056A729E5} | FRESNO | ANGIOLA | Bank 1 | CB 1103 (Non SCADA) | PGE\BXYD | 2017-01-25 16:55:21.8016314 -08:00 | 2521501103 | 252151103 | 8 | 4 | 3 | 1 | 376 | 8.21 | 8.13 | 357 | 7.79 | 7.71 | 383 | 8.36 | 8.28 | 383 | 8.36 | 8.28 | 383 | 8.36 | 8.28 | 383 | 8.36 | 8.28 | 383 | 8.36 | 8.28 | 383 | 8.36 | 8.28 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {B6DB0635-3F04-440C-ADB1-CCB976CE3202}
27 | 1023 | {A8F9AC29-671D-11E5-80CA-005056A729E5} | FRESNO | ANGIOLA | Bank 1 | CB 1104 (Non SCADA) | PGE\BXYD | 2016-09-22 11:23:29.8181895 -07:00 | 2521501104 | 252151104 | 8 | 4 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {B11E2E45-2524-4531-AF39-57229D0DB182}
28 | 1015 | {E7DF13D2-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | GABILAN | Bank 1 | CB 1102 | PGE\ACT0 | 2016-11-23 10:41:23.2521013 -08:00 | 1823301102 | 182331102 | 8 | 3 | 2 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 962 | {16AC856E-7F87-4E83-BDBE-C6A8611712B4}
30 | 1024 | {A8F9AC38-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 1 | CB 1102 | PGE\BXYD | 2016-09-22 13:03:45.3496715 -07:00 | 2520501102 | 252051102 | 8 | 3 | 3 | 1 | 326 | 7.11 | 7.04 | 326 | 7.11 | 7.04 | 413 | 9.01 | 8.92 | 413 | 9.01 | 8.92 | 361 | 7.88 | 7.8 | 361 | 7.88 | 7.8 | 436 | 9.52 | 9.42 | 436 | 9.52 | 9.42 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 3207 | 4169 | 3849 | 4811 | {53D521B7-D6D7-4517-90E1-0158F6F0FB0C}
1030 | 1024 | {A8F9AC40-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 1 | CB 1107 | PGE\BXYD | 2016-12-29 13:25:15.8960512 -08:00 | 2520501107 | 252051107 | 8 | 3 | 3 | 1 | 377 | 8.23 | 8.15 | 377 | 8.23 | 8.15 | 478 | 10.43 | 10.33 | 478 | 10.43 | 10.33 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 505 | 11.02 | 10.91 | 505 | 11.02 | 10.91 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 3207 | 3545 | 3545 | 3545 | {FFAB56ED-FB72-417B-8212-8C444433E907}
1031 | 1024 | {A8F9AC4E-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 1 | CB 1114 | PGE\BXYD | 2016-12-29 13:42:25.6940556 -08:00 | 2520501114 | 252051114 | 8 | 3 | 3 | 1 | 351 | 7.66 | 7.58 | 351 | 7.66 | 7.58 | 445 | 9.71 | 9.61 | 445 | 9.71 | 9.61 | 388 | 8.47 | 8.39 | 388 | 8.47 | 8.39 | 470 | 10.26 | 10.16 | 470 | 10.26 | 10.16 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 3207 | 3545 | 3545 | 3545 | {D82CC4F0-AA88-41FE-8D48-DA93BE416B7C}
1033 | 1024 | {A8F9AC5C-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 1 | CB 2105 | PGE\BXYD | 2016-12-29 14:26:44.0490168 -08:00 | 2520502105 | 252052105 | 8 | 3 | 3 | 1 | 607 | 13.25 | 13.12 | 607 | 13.25 | 13.12 | 770 | 16.8 | 16.63 | 770 | 16.8 | 16.63 | 672 | 14.67 | 14.52 | 672 | 14.67 | 14.52 | 814 | 17.76 | 17.58 | 814 | 17.76 | 17.58 | NOTE 1: Phase relay /1.2 or -50 amps, whichever is less. NOTE 3: UG cable ratings were calculated with the actual daily load factor. NOTE 4: Direct buried (DB) cables have custom ratings obtained from G.O. Normal Capacity is limited to 90% for second-day emergencies. |  | FALSE | FALSE | 3207 | 3545 | 3545 | 3545 | {883E309A-D306-4689-9637-B2B2FCF28F46}
1034 | 1024 | {A8F9AC73-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 1 | CB 2110 | PGE\BXYD | 2017-01-25 15:08:41.8877585 -08:00 | 2520502110 | 252052110 | 8 | 3 | 3 | 1 | 653 | 14.25 | 14.11 | 653 | 14.25 | 14.11 | 827 | 18.05 | 17.87 | 827 | 18.05 | 17.87 | 722 | 15.76 | 15.6 | 722 | 15.76 | 15.6 | 833 | 18.18 | 18 | 833 | 18.18 | 18 | NOTE 1: Phase relay /1.2 or -50 amps, whichever is less. NOTE 3: UG cable ratings were calculated with the actual daily load factor. NOTE 4: Direct buried (DB) cables have custom ratings obtained from G.O. Normal Capacity is limited to 90% for second-day emergencies. |  | FALSE | FALSE | 3207 | 3545 | 3545 | 3545 | {55AA4788-4723-45B3-9272-85B38274B664}
1035 | 1024 | {A8F9AC7E-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 1 | CB 2119 | PGE\BXYD | 2016-12-29 14:46:52.7056072 -08:00 | 2520502119 | 252052119 | 8 | 3 | 3 | 1 | 774 | 16.89 | 16.72 | 760 | 16.59 | 16.42 | 800 | 17.46 | 17.29 | 760 | 16.59 | 16.42 | 800 | 17.46 | 17.29 | 760 | 16.59 | 16.42 | 800 | 17.46 | 17.29 | 760 | 16.59 | 16.42 | NOTE 1: Phase relay /1.2 or -50 amps, whichever is less. Normal Capacity is limited to 90% for second-day emergencies. |  | FALSE | FALSE | 3207 | 3545 | 3545 | 3545 | {6D72CF43-FA2E-455E-9241-008394CF481F}
1036 | 1026 | {A8F9AC95-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 2 | CB 1103 | PGE\BXYD | 2016-12-29 15:25:46.8998568 -08:00 | 2520501103 | 252051103 | 8 | 3 | 3 | 1 | 447 | 9.76 | 9.66 | 447 | 9.76 | 9.66 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 3207 | 3545 | 3545 | 3545 | {37492315-E1A8-46B8-BC5E-DE789DD5FC13}
1037 | 1026 | {A8F9AC9A-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 2 | CB 1109 | PGE\BXYD | 2017-01-25 16:27:52.3351115 -08:00 | 2520501109 | 252051109 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 3207 | 3545 | 3545 | 3545 | {49AB6A5F-4975-4CA3-8D76-3D847E23CE77}
1038 | 1026 | {A8F9ACA8-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 2 | CB 1111 | PGE\BXYD | 2017-01-25 16:28:37.7163842 -08:00 | 2520501111 | 252051111 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | PVC RISER: Winter Normal - 691, Winter Emergency - 868; verified in field 11/25/08 VXLA. Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 3207 | 3545 | 3545 | 3545 | {A0510A8B-79E7-4B48-A982-6DF273E1364B}
1039 | 1026 | {A8F9ACB9-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 2 | CB 1112 | PGE\A6C7 | 2016-07-13 14:16:52.8570579 -07:00 | 2520501112 | 252051112 | 8 | 3 | 3 | 1 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 3207 | 4169 | 3849 | 4811 | {0279843D-4AA1-41A2-85D7-D247E6B8CDFC}
1041 | 1026 | {A8F9ACD6-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 2 | CB 1113 | PGE\BXYD | 2017-01-25 16:30:57.4638716 -08:00 | 2520501113 | 252051113 | 8 | 3 | 3 | 1 | 476 | 10.39 | 10.29 | 476 | 10.39 | 10.29 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 528 | 11.52 | 11.4 | 528 | 11.52 | 11.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 3207 | 3545 | 3545 | 3545 | {F17B904D-D705-4D29-8349-CFD9EC0A1762}
1043 | 1026 | {A8F9ACE1-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 2 | CB 2115 | PGE\A6C7 | 2016-07-15 08:05:16.0896635 -07:00 | 2520502115 | 252052115 | 8 | 3 | 3 | 1 | 422 | 9.21 | 9.12 | 422 | 9.21 | 9.12 | 536 | 11.7 | 11.58 | 536 | 11.7 | 11.58 | 468 | 10.21 | 10.11 | 468 | 10.21 | 10.11 | 566 | 12.35 | 12.23 | 566 | 12.35 | 12.23 | NOTE 1: Phase relay /1.2 or -50 amps, whichever is less. NOTE 3: UG cable ratings were calculated with the actual daily load factor. NOTE 4: Direct buried (DB) cables have custom ratings obtained from G.O. Normal Capacity is limited to 90% for second-day emergencies. |  | FALSE | FALSE | 3207 | 4169 | 3849 | 4811 | {AEE32513-E861-460D-99A8-6DE331BF3B37}
1044 | 1026 | {A8F9ACEF-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 2 | CB 2117 | PGE\JLDe | 2017-01-19 10:43:54.1984396 -08:00 | 2520502117 | 252052117 | 8 | 3 | 3 | 1 | 188 | 4.1 | 4.06 | 188 | 4.1 | 4.06 | 240 | 5.24 | 5.19 | 240 | 5.24 | 5.19 | 204 | 4.45 | 4.41 | 204 | 4.45 | 4.41 | 255 | 5.57 | 5.51 | 255 | 5.57 | 5.51 | NOTE 1: Phase relay /1.2 or -50 amps, whichever is less. NOTE 3: UG cable ratings were calculated with the actual daily load factor. |  | FALSE | FALSE | 3207 | 3545 | 3545 | 3545 | {30A226E4-92A1-4803-87DA-8670B5A6283F}
1045 | 1027 | {A8F9ACFD-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 3 | CB 1104 | PGE\BXYD | 2017-01-25 16:39:35.3002298 -08:00 | 2520501104 | 252051104 | 8 | 3 | 3 | 1 | 422 | 9.21 | 9.12 | 422 | 9.21 | 9.12 | 536 | 11.7 | 11.58 | 536 | 11.7 | 11.58 | 468 | 10.21 | 10.11 | 468 | 10.21 | 10.11 | 566 | 12.35 | 12.23 | 566 | 12.35 | 12.23 | ADD 1/0 CU OH CONDUCTOR IF REQUIRED Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 3207 | 3545 | 3545 | 3545 | {2B005CE3-44C0-4B80-8764-AF98F18E1896}
1046 | 1027 | {A8F9AD05-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 3 | CB 1106 | PGE\BXYD | 2017-01-25 16:41:08.0128127 -08:00 | 2520501106 | 252051106 | 8 | 3 | 3 | 1 | 495 | 10.8 | 10.69 | 470 | 10.26 | 10.16 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 3207 | 3545 | 3545 | 3545 | {89C6A86D-9E49-4D8F-A62F-5B8D98AC8B49}
1047 | 1027 | {A8F9AD14-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 3 | CB 1108 | PGE\BXYD | 2017-01-25 16:43:33.9380189 -08:00 | 2520501108 | 252051108 | 8 | 3 | 3 | 1 | 495 | 10.8 | 10.69 | 470 | 10.26 | 10.16 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 3207 | 3545 | 3545 | 3545 | {4D981F69-D59C-4248-962F-C08FBA5F12DC}
1048 | 1027 | {A8F9AD25-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 3 | CB 1116 | PGE\BXYD | 2017-01-25 16:47:14.3702579 -08:00 | 2520501116 | 252051116 | 8 | 3 | 3 | 1 | 584 | 12.75 | 12.62 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. |  | FALSE | FALSE | 3207 | 3545 | 3545 | 3545 | {7F074E3A-80FF-4ADE-B88A-40DAE268AA26}
1051 | 1027 | {A8F9AD39-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 3 | CB 2101 | PGE\BXYD | 2016-12-29 08:49:11.6194584 -08:00 | 2520502101 | 252052101 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 639 | 13.95 | 13.81 | 639 | 13.95 | 13.81 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 674 | 14.71 | 14.56 | 674 | 14.71 | 14.56 | Normal capacity is limited to 90% for second-day emergencies. NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 3207 | 4169 | 3849 | 4811 | {879BF4D7-D9AA-46C3-8081-B159AB0F2C19}
1052 | 1027 | {A8F9AD3E-671D-11E5-80CA-005056A729E5} | FRESNO | ASHLAN AVE | Bank 3 | CB 2118 | PGE\BXYD | 2016-12-29 08:48:42.5716998 -08:00 | 2520502118 | 252052118 | 8 | 3 | 3 | 1 | 447 | 9.76 | 9.66 | 447 | 9.76 | 9.66 | 568 | 12.4 | 12.28 | 568 | 12.4 | 12.28 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 629 | 13.73 | 13.59 | 629 | 13.73 | 13.59 | Normal capacity is limited to 90% for second-day emergencies. NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 3207 | 4169 | 3849 | 4811 | {660F8A48-3CB2-46BA-A8B3-8DD1BAE5205E}
1054 | 1028 | {B31C1E4B-671D-11E5-80CA-005056A729E5} | FRESNO | AUBERRY | Bank 1 (Non SCADA) | CB 1102 (Non SCADA) | PGE\A6C7 | 2016-07-15 09:37:03.6855560 -07:00 | 2541501102 | 254151102 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. NOTE 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 572 | 744 | 687 | 842 | {AABCAA68-316C-41AE-8941-BF94AFA3D896}
1055 | 1029 | {B31C1E54-671D-11E5-80CA-005056A729E5} | FRESNO | AUBERRY | Bank 2 | CB 1101 (Non SCADA) | PGE\A6C7 | 2016-07-15 10:07:27.0347066 -07:00 | 2541501101 | 254151101 | 8 | 3 | 3 | 1 | 572 | 12.48 | 12.36 | 572 | 12.48 | 12.36 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. NOTE 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 572 | 744 | 687 | 842 | {8E12E706-ACBC-44AC-8AE3-4363D337B86D}
1056 | 1030 | {B31C1E6C-671D-11E5-80CA-005056A729E5} | FRESNO | AVENAL | Bank 1 | CB 2101 (Non SCADA) | PGE\BXYD | 2017-01-25 08:57:50.0876648 -08:00 | 2550002101 | 255002101 | 12 | 3 | 3 | 1 | 423 | 15.99 | 15.83 | 423 | 15.99 | 15.83 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 423 | 550 | 508 | 635 | {3B1A9881-2BEF-498C-A512-11C90BFF49A7}
1057 | 1031 | {B31C1E7E-671D-11E5-80CA-005056A729E5} | FRESNO | BALCH NO 1 | Bank 1 (Non SCADA) | CB 1101 (Non SCADA) | PGE\VxLa | 2017-05-08 09:41:33.2372498 -07:00 | 2525001101 | 252501101 | 8 | 4 | 4 | 1 | 50 | 1.09 | 1.08 | 47 | 1.03 | 1.02 | 50 | 1.09 | 1.08 | 47 | 1.03 | 1.02 | 50 | 1.09 | 1.08 | 47 | 1.03 | 1.02 | 50 | 1.09 | 1.08 | 47 | 1.03 | 1.02 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 91 | 119 | 110 | 137 | {A435E848-2257-424E-94D0-001583D55735}
1058 | 1032 | {B31C1E87-671D-11E5-80CA-005056A729E5} | FRESNO | BARTON | Bank 1 | CB 1101 | PGE\BXYD | 2016-09-26 10:11:05.9878648 -07:00 | 2535701101 | 253571101 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {2825331F-DE75-436F-9BE5-BCEA623963BC}
1059 | 1032 | {B31C1E92-671D-11E5-80CA-005056A729E5} | FRESNO | BARTON | Bank 1 | CB 1102 | PGE\BXYD | 2016-09-26 10:12:32.2731848 -07:00 | 2535701102 | 253571102 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {D32C6E5B-90E1-4906-B3EB-CDF156595431}
1060 | 1032 | {B31C1E9A-671D-11E5-80CA-005056A729E5} | FRESNO | BARTON | Bank 1 | CB 1104 | PGE\BXYD | 2016-12-29 11:36:40.0846944 -08:00 | 2535701104 | 253571104 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {281CA81A-02B7-4917-A92E-BE363E56CFFF}
1061 | 1032 | {B31C1EA8-671D-11E5-80CA-005056A729E5} | FRESNO | BARTON | Bank 1 | CB 1105 | PGE\BXYD | 2016-09-26 10:19:06.7470323 -07:00 | 2535701105 | 253571105 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {0E4365B8-0D74-4890-89D8-1A1C61BE09D0}
1062 | 1032 | {B31C1EB3-671D-11E5-80CA-005056A729E5} | FRESNO | BARTON | Bank 1 | CB 1106 | PGE\BXYD | 2016-12-29 11:49:32.0499396 -08:00 | 2535701106 | 253571106 | 8 | 3 | 3 | 1 | 434 | 9.47 | 9.38 | 412 | 8.99 | 8.9 | 486 | 10.61 | 10.5 | 461 | 10.06 | 9.96 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {C4A766C7-E10D-4226-BE5F-F391216D9D45}
1063 | 1032 | {B31C1EBB-671D-11E5-80CA-005056A729E5} | FRESNO | BARTON | Bank 1 | CB 1108 | PGE\BXYD | 2016-09-26 10:30:05.0089196 -07:00 | 2535701108 | 253571108 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {81C5309A-E943-4DC9-9B25-BCF0BA304F94}
1064 | 1017 | {B31C1ECF-671D-11E5-80CA-005056A729E5} | FRESNO | BARTON | Bank 2 | CB 1109 | PGE\BXYD | 2017-01-25 08:36:20.1300584 -08:00 | 2535701109 | 253571109 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 2000 | 2400 | 2000 | 2400 | {2D9FF31D-F0E0-42F5-895E-F27D9C7366BA}
1065 | 1017 | {B31C1ED7-671D-11E5-80CA-005056A729E5} | FRESNO | BARTON | Bank 2 | CB 1110 | PGE\BXYD | 2017-01-25 08:37:56.2279064 -08:00 | 2535701110 | 253571110 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 2000 | 2400 | 2000 | 2400 | {C0631381-200B-4333-A020-0DA809148703}
1067 | 1017 | {B31C1EDF-671D-11E5-80CA-005056A729E5} | FRESNO | BARTON | Bank 2 | CB 1111 | PGE\BXYD | 2017-01-25 08:42:14.2724687 -08:00 | 2535701111 | 253571111 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 2000 | 2400 | 2000 | 2400 | {C5DBDF18-8665-4E24-B0F4-FA19CFB37681}
1068 | 1017 | {B31C1EEA-671D-11E5-80CA-005056A729E5} | FRESNO | BARTON | Bank 2 | CB 1112 | PGE\BXYD | 2016-09-26 11:28:45.8730738 -07:00 | 2535701112 | 253571112 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {D9830237-ECE2-46DA-BD51-AD837F5788E5}
1071 | 1033 | {B31C1EF8-671D-11E5-80CA-005056A729E5} | FRESNO | BARTON | Bank 3 | CB 1114 | PGE\BXYD | 2016-12-29 13:10:47.3749820 -08:00 | 2535701114 | 253571114 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {D22261A5-0864-48C9-AF74-3B4F605B2C4D}
1072 | 1033 | {B31C1F00-671D-11E5-80CA-005056A729E5} | FRESNO | BARTON | Bank 3 | CB 1115 | PGE\BXYD | 2017-01-25 08:49:19.4274446 -08:00 | 2535701115 | 253571115 | 8 | 3 | 3 | 1 | 477 | 10.41 | 10.31 | 477 | 10.41 | 10.31 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 528 | 11.52 | 11.4 | 528 | 11.52 | 11.4 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | +53A to Summer Norm and Winter Norm NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F0979F81-3B4E-4F15-9732-083237EBA6F9}
1073 | 1033 | {B31C1F11-671D-11E5-80CA-005056A729E5} | FRESNO | BARTON | Bank 3 | CB 1116 | PGE\BXYD | 2016-09-26 11:39:20.5624706 -07:00 | 2535701116 | 253571116 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {CC181A61-F4CA-4585-AF6C-D0B08BA1EF5A}
1074 | 1034 | {B31C1F25-671D-11E5-80CA-005056A729E5} | FRESNO | BIOLA | Bank 1 | CB 1101 (Non SCADA) | PGE\BXYD | 2016-09-26 11:47:10.9490391 -07:00 | 2522101101 | 252211101 | 8 | 3 | 3 | 1 | 282 | 6.15 | 6.09 | 282 | 6.15 | 6.09 | 315 | 6.87 | 6.8 | 315 | 6.87 | 6.8 | 358 | 7.81 | 7.73 | 358 | 7.81 | 7.73 | 382 | 8.34 | 8.26 | 382 | 8.34 | 8.26 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 561 | 730 | 674 | 842 | {7AC253C8-3473-4F94-85D3-22BE6A9C624E}
1075 | 1034 | {B31C1F2B-671D-11E5-80CA-005056A729E5} | FRESNO | BIOLA | Bank 1 | CB 1102 (Non SCADA) | PGE\BXYD | 2016-09-26 11:47:54.7356807 -07:00 | 2522101102 | 252211102 | 8 | 3 | 3 | 1 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 561 | 730 | 674 | 842 | {0EC44E19-15DC-4852-A83A-4F1A369B8C9F}
1076 | 1034 | {B31C1F31-671D-11E5-80CA-005056A729E5} | FRESNO | BIOLA | Bank 1 | CB 1103 (Non SCADA) | PGE\BXYD | 2017-01-25 08:19:57.5763635 -08:00 | 2522101103 | 252211103 | 8 | 3 | 3 | 1 | 420 | 9.17 | 9.08 | 420 | 9.17 | 9.08 | 420 | 9.17 | 9.08 | 420 | 9.17 | 9.08 | 420 | 9.17 | 9.08 | 420 | 9.17 | 9.08 | 420 | 9.17 | 9.08 | 420 | 9.17 | 9.08 | -60A due to generation/emergency reserve NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 916 | 1191 | 1100 | 1375 | {03E310EE-A8CE-4FC4-BF8B-F3E74C2AB194}
1077 | 1034 | {B31C1F37-671D-11E5-80CA-005056A729E5} | FRESNO | BIOLA | Bank 1 | CB 1104 (Non SCADA) | PGE\BXYD | 2017-01-25 08:20:57.7155200 -08:00 | 2522101104 | 252211104 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 916 | 1191 | 1100 | 1375 | {EBF9CEBD-83C0-4656-BF1E-140E908CF91E}
1078 | 1035 | {B31C1F46-671D-11E5-80CA-005056A729E5} | FRESNO | BOSWELL | Bank 1 | CB 1101 | PGE\A6C7 | 2016-07-18 15:40:20.2542938 -07:00 | 253961101 | 253961101 | 8 | 4 | 4 | 1 | 561 | 12.24 | 12.12 | 561 | 12.24 | 12.12 | 561 | 12.24 | 12.12 | 561 | 12.24 | 12.12 | 561 | 12.24 | 12.12 | 561 | 12.24 | 12.12 | 561 | 12.24 | 12.12 | 561 | 12.24 | 12.12 | No Capability Sheet found on SharePoint |  | FALSE | FALSE | 561 | 561 | 561 | 561 | {FB6CF944-3951-4764-82A8-EADEB468325B}
1080 | 1036 | {B31C1F54-671D-11E5-80CA-005056A729E5} | FRESNO | BOWLES | Bank 1 | CB 1101 (Non SCADA) | PGE\BXYD | 2016-09-26 13:05:39.1649442 -07:00 | 2535301101 | 253531101 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {3F12F7C0-C521-4629-A248-086F2DA9CD12}
1081 | 1036 | {B31C1F60-671D-11E5-80CA-005056A729E5} | FRESNO | BOWLES | Bank 1 | CB 1102 (Non SCADA) | PGE\BXYD | 2016-09-26 13:08:43.3891843 -07:00 | 2535301102 | 253531102 | 8 | 3 | 3 | 1 | 376 | 8.21 | 8.13 | 376 | 8.21 | 8.13 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {244820D7-4D62-4E5D-9186-2787ECC083C8}
1082 | 1036 | {B31C1F63-671D-11E5-80CA-005056A729E5} | FRESNO | BOWLES | Bank 1 | CB 1103 (Non SCADA) | PGE\BXYD | 2017-01-24 17:13:04.1001591 -08:00 | 2535301103 | 253531103 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 859 | 1116 | 1030 | 1200 | {E5BE02C9-6C5E-4C7C-A31A-15440E302DF1}
1083 | 1036 | {B31C1F66-671D-11E5-80CA-005056A729E5} | FRESNO | BOWLES | Bank 1 | CB 1104 (Non SCADA) | PGE\BXYD | 2016-09-26 13:11:18.1647010 -07:00 | 2535301104 | 253531104 | 8 | 3 | 3 | 1 | 376 | 8.21 | 8.13 | 376 | 8.21 | 8.13 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {C33C7EC1-8E8C-48E7-93E2-6E27B1E4CAD8}
1085 | 1037 | {B31C1F75-671D-11E5-80CA-005056A729E5} | FRESNO | BULLARD | Bank 1 | CB 2111 | PGE\JWCp | 2017-02-13 13:31:02.0826652 -08:00 | 2539602111 | 253962111 | 12 | 3 | 3 | 1 | 573 | 21.66 | 21.44 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | St Agnes Cogen: 2 units for 3.5 MVA total output (86 Amps). De-rate feeder by 86 Amps to allow for cogeneration dropping offline unexpectedly. NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {F9C9EAA5-5B1B-4CA4-BC7D-213FDBC6413B}
1086 | 1037 | {B31C1F7D-671D-11E5-80CA-005056A729E5} | FRESNO | BULLARD | Bank 1 | CB 2112 | PGE\BXYD | 2016-09-26 13:33:10.1398851 -07:00 | 2539602112 | 253962112 | 12 | 3 | 3 | 1 | 553 | 20.9 | 20.69 | 553 | 20.9 | 20.69 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 | 613 | 23.17 | 22.94 | 613 | 23.17 | 22.94 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. NOTE 3: UG cable ratings were calculated with the actual daily load factor. |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {26853FC7-DA6B-4BAA-8CD9-83469999AF1B}
1087 | 1037 | {B31C1F97-671D-11E5-80CA-005056A729E5} | FRESNO | BULLARD | Bank 1 | CB 2114 | PGE\JWCp | 2017-02-15 09:16:43.9884184 -08:00 | 2539602114 | 253962114 | 12 | 3 | 3 | 1 | 566 | 21.39 | 21.18 | 566 | 21.39 | 21.18 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 | 678 | 25.62 | 25.36 | 678 | 25.62 | 25.36 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. NOTE 3: UG cable ratings were calculated with the actual daily load factor. |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {B9AB2A25-7B89-4D17-B332-634631B0E4A1}
1088 | 1038 | {B31C1FB7-671D-11E5-80CA-005056A729E5} | FRESNO | BULLARD | Bank 2 | CB 1105 | PGE\BXYD | 2016-09-26 13:41:05.3992964 -07:00 | 2539601105 | 253961105 | 8 | 3 | 3 | 1 | 447 | 9.76 | 9.66 | 447 | 9.76 | 9.66 | 568 | 12.4 | 12.28 | 568 | 12.4 | 12.28 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 3207 | 4169 | 3849 | 4811 | {BDD792B9-BA1F-4689-B7D9-D50A85B496D9}
1089 | 1038 | {B31C1FCB-671D-11E5-80CA-005056A729E5} | FRESNO | BULLARD | Bank 2 | CB 1106 | PGE\BXYD | 2016-09-26 13:42:54.4116090 -07:00 | 2539601106 | 253961106 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 3207 | 4169 | 3849 | 4811 | {D2BA7A5E-B7C4-4657-BC97-654FB829D930}
1090 | 1038 | {B31C1FD6-671D-11E5-80CA-005056A729E5} | FRESNO | BULLARD | Bank 2 | CB 1107 | PGE\BXYD | 2016-09-26 13:45:14.5388800 -07:00 | 2539601107 | 253961107 | 8 | 3 | 3 | 1 | 447 | 9.76 | 9.66 | 447 | 9.76 | 9.66 | 568 | 12.4 | 12.28 | 568 | 12.4 | 12.28 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 3207 | 4169 | 3849 | 4811 | {546129BE-9A29-4694-AB6E-A320037463BB}
1091 | 1038 | {B31C1FDB-671D-11E5-80CA-005056A729E5} | FRESNO | BULLARD | Bank 2 | CB 1108 | PGE\BXYD | 2017-01-24 14:52:40.2189645 -08:00 | 2539601108 | 253961108 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 2200 | 2640 | 2200 | 2640 | {0D9B1F24-B5B3-49E8-BAA5-E753769E80C9}
1092 | 1038 | {B31C1FE3-671D-11E5-80CA-005056A729E5} | FRESNO | BULLARD | Bank 2 | CB 1109 | PGE\BXYD | 2016-09-26 13:54:45.7502892 -07:00 | 2539601109 | 253961109 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 3207 | 4169 | 3849 | 4811 | {355CBB83-84D0-43DB-ABAC-076BD51FC477}
1093 | 1038 | {B31C1FE8-671D-11E5-80CA-005056A729E5} | FRESNO | BULLARD | Bank 2 | CB 1110 | PGE\BXYD | 2016-09-26 13:55:54.3273909 -07:00 | 2539601110 | 253961110 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 3207 | 4169 | 3849 | 4811 | {3E1ED496-3D11-4881-9A88-6152D3939AC9}
1094 | 1041 | {B31C1FF6-671D-11E5-80CA-005056A729E5} | FRESNO | BULLARD | Bank 3 | CB 1101 | PGE\BXYD | 2016-09-26 14:08:32.2264919 -07:00 | 2539601101 | 253961101 | 8 | 3 | 3 | 1 | 553 | 12.07 | 11.95 | 553 | 12.07 | 11.95 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {FB6CF944-3951-4764-82A8-EADEB468325B}
1095 | 1041 | {B31C200A-671D-11E5-80CA-005056A729E5} | FRESNO | BULLARD | Bank 3 | CB 1102 | PGE\VxLa | 2017-06-07 13:00:18.8855425 -07:00 | 2539601102 | 253961102 | 8 | 3 | 3 | 1 | 492 | 10.74 | 10.63 | 492 | 10.74 | 10.63 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Voltage Base was altered to more closely reflect parallel UG cables that are not part of EDPI database. NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {100C1ABA-6FFB-4C6E-B943-3F71E6F3E454}
1096 | 1041 | {B31C2018-671D-11E5-80CA-005056A729E5} | FRESNO | BULLARD | Bank 3 | CB 1103 | PGE\BXYD | 2017-01-24 15:10:21.0237642 -08:00 | 2539601103 | 253961103 | 8 | 3 | 3 | 1 | 414 | 9.04 | 8.95 | 414 | 9.04 | 8.95 | 460 | 10.04 | 9.94 | 460 | 10.04 | 9.94 | 426 | 9.3 | 9.21 | 426 | 9.3 | 9.21 | 474 | 10.34 | 10.24 | 474 | 10.34 | 10.24 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9D3C7A82-74A0-4B23-9FA9-0884D715B51B}
1097 | 1041 | {B31C2026-671D-11E5-80CA-005056A729E5} | FRESNO | BULLARD | Bank 3 | CB 1104 | PGE\BXYD | 2016-09-28 15:36:38.8878827 -07:00 | 2539601104 | 253961104 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {DA05816D-4669-4DA5-86B2-0D5F3F78416F}
1098 | 1041 | {B31C203D-671D-11E5-80CA-005056A729E5} | FRESNO | BULLARD | Bank 3 | CB 1113 | PGE\BXYD | 2016-09-26 14:34:14.3496226 -07:00 | 2539601113 | 253961113 | 8 | 3 | 3 | 1 | 553 | 12.07 | 11.95 | 553 | 12.07 | 11.95 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B37CAC99-1E99-47A0-B0DA-9FCCA44EA2C1}
1099 | 1043 | {B31C2060-671D-11E5-80CA-005056A729E5} | FRESNO | CALFLAX | Bank 1 | CB 1101 (Non SCADA) | PGE\BXYD | 2017-01-24 14:41:36.5666022 -08:00 | 2534401101 | 253441101 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. NOTE 3: UG cable ratings were calculated with the actual daily load factor. |  | FALSE | FALSE | 859 | 1116 | 1030 | 1200 | {3DBDA190-23BA-41FC-8C1E-84245261B18E}
1101 | 1043 | {B31C2063-671D-11E5-80CA-005056A729E5} | FRESNO | CALFLAX | Bank 1 | CB 1102 (Non SCADA) | PGE\BXYD | 2016-09-26 15:18:04.4913973 -07:00 | 2534401102 | 253441102 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. NOTE 3: UG cable ratings were calculated with the actual daily load factor. |  | FALSE | FALSE | 842 | 1095 | 1010 | 1263 | {3A8E5061-67CF-4AE8-8EDE-AABC931A4DB0}
1102 | 1043 | {B31C2066-671D-11E5-80CA-005056A729E5} | FRESNO | CALFLAX | Bank 1 | CB 1103 (Non SCADA) | PGE\BXYD | 2016-09-26 15:19:02.8854482 -07:00 | 2534401103 | 253441103 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. NOTE 3: UG cable ratings were calculated with the actual daily load factor. |  | FALSE | FALSE | 842 | 1095 | 1010 | 1263 | {E68A4B33-01F3-49E0-BEA5-B73D9F8F0557}
1103 | 1043 | {B31C2069-671D-11E5-80CA-005056A729E5} | FRESNO | CALFLAX | Bank 1 | CB 1104 (Non SCADA) | PGE\A6C7 | 2016-07-29 12:01:50.2355099 -07:00 | 2534401104 | 253441104 | 8 | 3 | 3 | 1 | 367 | 8.01 | 7.93 | 367 | 8.01 | 7.93 | 367 | 8.01 | 7.93 | 367 | 8.01 | 7.93 | 367 | 8.01 | 7.93 | 367 | 8.01 | 7.93 | 367 | 8.01 | 7.93 | 367 | 8.01 | 7.93 | NOTE 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. NOTE 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. NOTE 3: UG cable ratings were calculated with the actual daily load factor. |  | FALSE | FALSE | 842 | 1095 | 1010 | 1263 | {52E85E43-E4F5-4B12-80B5-71A6405C21D8}
1104 | 1044 | {8C3C5B72-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | PASO ROBLES | Bank 3 | CB 1108 | PGE\A9S5 | 2016-11-11 10:29:59.9216602 -08:00 | 1826101108 | 182611108 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {D9847950-4247-4FB3-B579-DE6E677678B0}
1106 | 1047 | {C89EFB6F-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | DOLAN ROAD | Bank 1 | CB 1101 | PGE\ACT0 | 2016-09-28 10:01:47.0510134 -07:00 | 1823801101 | 182381101 | 8 | 3 | 3 | 2 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {8BE09573-B92D-4FBD-B340-3B33C61FBEF4}
1107 | 1047 | {CEEBC999-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | DOLAN ROAD | Bank 1 | CB 1103 | PGE\JLDe | 2016-09-14 17:04:55.9561774 -07:00 | 1823801103 | 182381103 | 8 | 3 | 3 | 2 | 468 | 10.21 | 10.11 | 468 | 10.21 | 10.11 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {0B0DF2F8-F94A-4F26-8341-50CBE61134B6}
1250 | 1051 | {5A8ACA42-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | ARCATA | Bank 1 | CB 1106 | PGE\C8M4 | 2017-07-19 10:04:41.3167058 -07:00 | 1920201106 | 192021106 | 8 | 3 | 3 | 2 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | TRUE | 1374 | 1787 | 1649 | 2000 | {452AFDA5-58A6-4D84-A79C-3EF7CCE0522B}
1251 | 1119 | {B91B8CBE-671D-11E5-80CA-005056A729E5} | FRESNO | CANTUA | Bank 1 | CB 1101 | PGE\BXYD | 2016-09-28 14:07:12.4305665 -07:00 | 2535901101 | 253591101 | 8 | 3 | 3 | 1 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1099 | 1429 | 1319 | 1649 | {6D147665-41D3-45E9-8192-6E6F33514354}
1254 | 1117 | {CEEBC9CA-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | FORT ORD | Bank 1 | CB 1101 (Non-SCADA) | PGE\ACT0 | 2016-11-23 11:55:50.4503709 -08:00 | 1824001101 | 182401101 | 8 | 3 | 3 | 2 | 229 | 5 | 4.95 | 217 | 4.74 | 4.69 | 298 | 6.5 | 6.44 | 283 | 6.18 | 6.12 | 275 | 6 | 5.94 | 261 | 5.7 | 5.64 | 344 | 7.51 | 7.43 | 326 | 7.11 | 7.04 |  |  | TRUE | FALSE | 859 | 1116 | 1030 | 1288 | {D080D5A5-E292-4C79-BAFA-EAAE78860947}
1255 | 1117 | {2EBBA051-0B42-11E6-9D37-D4BED91EFF1A} | CENTRAL COAST | FORT ORD | Bank 1 | CB 1102 (Non-SCADA) | PGE\ACT0 | 2016-11-23 11:55:26.1159309 -08:00 | 1824001102 | 182401102 | 8 | 3 | 3 | 2 | 859 | 18.75 | 18.56 | 816 | 17.81 | 17.63 | 900 | 19.64 | 19.44 | 855 | 18.66 | 18.47 | 900 | 19.64 | 19.44 | 855 | 18.66 | 18.47 | 900 | 19.64 | 19.44 | 855 | 18.66 | 18.47 |  |  | TRUE | FALSE | 859 | 1116 | 1030 | 1288 | {1CCE38AE-5F29-4C9D-9EFF-BCB7A7FE6159}
1256 | 1119 | {B91B8CC9-671D-11E5-80CA-005056A729E5} | FRESNO | CANTUA | Bank 1 | CB 1102 | PGE\BXYD | 2016-09-28 14:06:49.3580186 -07:00 | 2535901102 | 253591102 | 8 | 4 | 4 | 2 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1099 | 1429 | 1319 | 1649 | {B2889074-11A0-44D1-84FA-C3BD653B0687}
1257 | 1051 | {5A8ACAAB-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | ARCATA | Bank 1 | CB 1123 | PGE\C8M4 | 2017-07-19 10:08:47.7998658 -07:00 | 1920201123 | 192021123 | 8 | 3 | 3 | 2 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | TRUE | 1374 | 1787 | 1649 | 2000 | {AFBABF54-4765-472A-92C6-B54795D341EE}
1258 | 1119 | {B91B8CCE-671D-11E5-80CA-005056A729E5} | FRESNO | CANTUA | Bank 1 | CB 1103 | PGE\JWCp | 2017-01-24 12:44:08.7384464 -08:00 | 2535901103 | 253591103 | 8 | 3 | 3 | 1 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 940 | 1160 | 1315 | 1465 | {6ACB4D92-7BC9-4548-BDAE-E5A8E8992A13}
1259 | 1119 | {B91B8CD6-671D-11E5-80CA-005056A729E5} | FRESNO | CANTUA | Bank 1 | CB 1104 | PGE\BXYD | 2017-01-24 14:07:25.4391582 -08:00 | 2535901104 | 253591104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1099 | 1429 | 1319 | 1500 | {F02ECA33-4F22-4B13-A5E5-A311FEB1AE6A}
1262 | 1119 | {B91B8CDB-671D-11E5-80CA-005056A729E5} | FRESNO | CANTUA | Bank 1 | CB 1105 | PGE\BXYD | 2016-09-28 16:15:30.7744994 -07:00 | 2535901105 | 253591105 | 8 | 3 | 3 | 1 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1099 | 1429 | 1319 | 1649 | {B1BC4319-758C-4392-97F7-26D0C248EBBA}
1263 | 1103 | {A723308E-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PENRYN | Bank 2 | CB 1105 | PGE\SDK6 | 2016-09-28 14:17:15.2626520 -07:00 | 1525601105 | 152561105 | 8 | 3 | 3 | 1 | 745 | 16.26 | 16.1 | 745 | 16.26 | 16.1 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {66EB4074-E00B-4B20-8522-0E7593D68CD9}
1264 | 1103 | {A72330B3-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PENRYN | Bank 2 | CB 1106 | PGE\SDK6 | 2016-09-28 14:23:08.2617369 -07:00 | 1525601106 | 152561106 | 8 | 3 | 3 | 1 | 636 | 13.88 | 13.74 | 636 | 13.88 | 13.74 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 717 | 15.65 | 15.49 | 717 | 15.65 | 15.49 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9E0E5AB5-41F8-4980-B3D6-74216EB882F0}
1266 | 1103 | {A72330C3-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PENRYN | Bank 2 | CB 1107 | PGE\SDK6 | 2016-09-28 14:26:22.2066086 -07:00 | 1525601107 | 152561107 | 8 | 4 | 4 | 2 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F58DA4E3-0E2B-4227-BB1E-403995206580}
1268 | 1123 | {AD80BECA-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PLEASANT GROVE | Bank 1 | CB 2103 | PGE\SDK6 | 2016-09-28 15:14:56.8752512 -07:00 | 1524402103 | 152442103 | 12 | 3 | 3 | 1 | 745 | 28.16 | 27.88 | 745 | 28.16 | 27.88 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {711CC74E-6C52-4169-9D90-4A1BBFB2EA36}
1269 | 1123 | {AD80BEDA-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PLEASANT GROVE | Bank 1 | CB 2104 | PGE\SDK6 | 2016-09-28 15:42:51.5450269 -07:00 | 1524402104 | 152442104 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 792 | 29.93 | 29.63 | 792 | 29.93 | 29.63 | 717 | 27.1 | 26.83 | 717 | 27.1 | 26.83 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {D6DE5B89-2A37-4BBD-ABEA-A84564218B4D}
1618 | 1271 | {4C486FBD-671D-11E5-80CA-005056A729E5} | YOSEMITE | BEAR VALLEY | Bank 1 (Non SCADA) | CB 2101 (Non-SCADA) | PGE\BXYD | 2016-11-08 15:35:20.5107238 -08:00 | 2521902101 | 252192101 | 12 | 3 | 3 | 1 | 330 | 12.47 | 12.35 | 330 | 12.47 | 12.35 | 333 | 12.59 | 12.46 | 333 | 12.59 | 12.46 | 333 | 12.59 | 12.46 | 333 | 12.59 | 12.46 | 333 | 12.59 | 12.46 | 333 | 12.59 | 12.46 |  |  | FALSE | FALSE | 330 | 429 | 396 | 486 | {CD928643-A373-4C7D-9E49-979135835694}
1620 | 1271 | {4C486FC0-671D-11E5-80CA-005056A729E5} | YOSEMITE | BEAR VALLEY | Bank 1 (Non SCADA) | CB 2105 (Non-SCADA) | PGE\BXYD | 2016-11-08 15:35:34.5824650 -08:00 | 2521902105 | 252192105 | 12 | 3 | 3 | 1 | 183 | 6.92 | 6.85 | 183 | 6.92 | 6.85 | 211 | 7.97 | 7.89 | 211 | 7.97 | 7.89 | 266 | 10.05 | 9.95 | 266 | 10.05 | 9.95 | 284 | 10.73 | 10.62 | 284 | 10.73 | 10.62 |  |  | FALSE | FALSE | 330 | 429 | 396 | 486 | {0680817C-1C3A-4E04-B85D-872FA0582752}
1621 | 1272 | {4C486FD2-671D-11E5-80CA-005056A729E5} | YOSEMITE | BONITA | Bank 1 | CB 1101 | PGE\BXYD | 2016-10-13 13:50:29.8816560 -07:00 | 2553901101 | 255391101 | 8 | 3 | 3 | 1 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 |  |  | FALSE | FALSE | 702 | 702 | 702 | 702 | {202B86A2-47DB-44D8-9D5B-52D0F38179C6}
1622 | 1272 | {4C486FDD-671D-11E5-80CA-005056A729E5} | YOSEMITE | BONITA | Bank 1 | CB 1102 | PGE\BXYD | 2016-10-13 13:50:17.2889859 -07:00 | 2553901102 | 255391102 | 8 | 3 | 3 | 1 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 |  |  | FALSE | FALSE | 702 | 702 | 702 | 702 | {3E94F375-E54E-475D-AF0A-AFA6E87EEC4E}
1623 | 1272 | {523E8C88-671D-11E5-80CA-005056A729E5} | YOSEMITE | BONITA | Bank 1 | CB 1103 | PGE\JWCp | 2017-01-18 17:56:23.8133837 -08:00 | 2553901103 | 255391103 | 8 | 3 | 3 | 1 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 |  |  | FALSE | FALSE | 702 | 702 | 702 | 702 | {26C2090B-F80A-474C-9FC3-26528190115A}
1624 | 1273 | {523E8C96-671D-11E5-80CA-005056A729E5} | YOSEMITE | BORDEN | Bank 2 | CB 1101 | PGE\BXYD | 2016-10-13 13:51:40.9695812 -07:00 | 2551201101 | 255121101 | 8 | 3 | 3 | 1 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {0E663E9E-1F12-421F-9261-99E0DFE6A0F8}
1626 | 1273 | {523E8CA1-671D-11E5-80CA-005056A729E5} | YOSEMITE | BORDEN | Bank 2 | CB 1102 | PGE\BXYD | 2016-10-13 13:51:50.5335459 -07:00 | 2551201102 | 255121102 | 8 | 3 | 3 | 1 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {A7FBF53E-6831-4B21-83DA-652DCED3266C}
1627 | 1273 | {523E8CB8-671D-11E5-80CA-005056A729E5} | YOSEMITE | BORDEN | Bank 2 | CB 1103 | PGE\JWCp | 2016-10-28 09:39:09.6143464 -07:00 | 2551201103 | 255121103 | 8 | 3 | 3 | 1 | 617 | 13.47 | 13.34 | 515 | 11.24 | 11.13 | 617 | 13.47 | 13.34 | 578 | 12.61 | 12.48 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {B4B0F82E-7DF3-45F7-B1A5-1F13DC84792A}
1629 | 1274 | {523E8CC9-671D-11E5-80CA-005056A729E5} | YOSEMITE | CANAL | Bank 1 | CB 1101 | PGE\BXYD | 2016-10-05 15:42:41.5366646 -07:00 | 2520901101 | 252091101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F820CACD-3A14-45BD-9251-B1971518A73F}
1630 | 1274 | {523E8CCE-671D-11E5-80CA-005056A729E5} | YOSEMITE | CANAL | Bank 1 | CB 1104 | PGE\BXYD | 2016-10-13 14:06:01.3013171 -07:00 | 2520901104 | 252091104 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {2B538604-B6BC-4008-B8B4-6A4913CA6FB8}
1633 | 1274 | {523E8CD6-671D-11E5-80CA-005056A729E5} | YOSEMITE | CANAL | Bank 1 | CB 1106 | PGE\BXYD | 2016-10-05 15:49:12.9743138 -07:00 | 2520901106 | 252091106 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {A1E513A3-CE3A-487F-9385-377E3933EF17}
1634 | 1275 | {523E8CE1-671D-11E5-80CA-005056A729E5} | YOSEMITE | CANAL | Bank 2 | CB 1102 | PGE\BXYD | 2016-10-05 15:56:50.5944446 -07:00 | 2520901102 | 252091102 | 8 | 3 | 3 | 1 | 636 | 13.88 | 13.74 | 636 | 13.88 | 13.74 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {D4D21B0F-69D7-4626-BB86-F75A2651FC08}
1635 | 1275 | {523E8CEC-671D-11E5-80CA-005056A729E5} | YOSEMITE | CANAL | Bank 2 | CB 1103 | PGE\BXYD | 2016-10-05 15:58:42.0118196 -07:00 | 2520901103 | 252091103 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {903A60BD-1897-4D2B-A57A-301C6E9588D1}
1637 | 1275 | {523E8CF4-671D-11E5-80CA-005056A729E5} | YOSEMITE | CANAL | Bank 2 | CB 1105 | PGE\BXYD | 2016-10-05 16:00:14.6976638 -07:00 | 2520901105 | 252091105 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {1E75070F-38F0-4AFA-B0EE-2F30A9D0F281}
1638 | 1276 | {523E8D05-671D-11E5-80CA-005056A729E5} | YOSEMITE | CASSIDY | Bank 2 | CB 2107 | PGE\BXYD | 2016-10-05 16:23:51.7742728 -07:00 | 2542702107 | 254272107 | 8 | 3 | 3 | 1 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 |  |  | FALSE | FALSE | 572 | 744 | 687 | 842 | {D975D538-F1A6-4CA5-8820-AA731AF76381}
1640 | 1276 | {523E8D13-671D-11E5-80CA-005056A729E5} | YOSEMITE | CASSIDY | Bank 2 | CB 2108 | PGE\BXYD | 2016-10-05 16:29:43.0731497 -07:00 | 2542702108 | 254272108 | 8 | 3 | 3 | 1 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 |  |  | FALSE | FALSE | 572 | 744 | 687 | 842 | {754DBE0E-7777-4D69-AFDE-EA40187D30A3}
1641 | 1280 | {523E8D39-671D-11E5-80CA-005056A729E5} | YOSEMITE | CHOWCHILLA | Bank 1 | CB 1101 | PGE\BXYD | 2016-10-06 08:17:25.0913748 -07:00 | 2541001101 | 254101101 | 8 | 3 | 3 | 1 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {C66F4734-8BB8-4240-92F4-0BFAB70A193E}
1642 | 1280 | {523E8D50-671D-11E5-80CA-005056A729E5} | YOSEMITE | CHOWCHILLA | Bank 1 | CB 1102 | PGE\JWCp | 2017-02-27 14:57:18.2930084 -08:00 | 2541001102 | 254101102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {AA191738-6709-4CC2-8FCD-F03ABD2FC500}
1643 | 1280 | {523E8D58-671D-11E5-80CA-005056A729E5} | YOSEMITE | CHOWCHILLA | Bank 1 | CB 1103 | PGE\JWCp | 2017-02-27 14:55:55.7986220 -08:00 | 2541001103 | 254101103 | 8 | 3 | 3 | 1 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {1A7FFA15-5437-4A02-81FE-AAF385B934E7}
1645 | 1280 | {523E8D66-671D-11E5-80CA-005056A729E5} | YOSEMITE | CHOWCHILLA | Bank 1 | CB 1104 (Non-SCADA) | PGE\BXYD | 2016-10-06 08:45:25.5580885 -07:00 | 2541001104 | 254101104 | 8 | 3 | 3 | 1 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {13148D9D-BD83-40F0-92FA-72D91B1B3EEE}
1648 | 1282 | {523E8D24-671D-11E5-80CA-005056A729E5} | YOSEMITE | CHOWCHILLA | Bank 2 | CB 1105 (Non-SCADA) | PGE\BXYD | 2016-10-06 08:59:13.0339009 -07:00 | 2541001105 | 254101105 | 8 | 3 | 3 | 1 | 282 | 6.15 | 6.09 | 282 | 6.15 | 6.09 | 315 | 6.87 | 6.8 | 315 | 6.87 | 6.8 | 358 | 7.81 | 7.73 | 358 | 7.81 | 7.73 | 382 | 8.34 | 8.26 | 382 | 8.34 | 8.26 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {ADE7BB5D-AC4F-4594-8F04-6F951EC96E48}
1649 | 1282 | {523E8D2D-671D-11E5-80CA-005056A729E5} | YOSEMITE | CHOWCHILLA | Bank 2 | CB 1106 (Non-SCADA) | PGE\BXYD | 2016-10-06 09:03:24.3376456 -07:00 | 2541001106 | 254101106 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {944A06B3-BC62-4EFC-8735-8588D0CC135A}
1650 | 1284 | {523E8D84-671D-11E5-80CA-005056A729E5} | YOSEMITE | COARSEGOLD | Bank 2 | CB 2103 | PGE\JWCp | 2016-11-03 12:19:53.0865108 -07:00 | 2544302103 | 254432103 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1773 | {CDE7184A-EAD1-45AB-8ED6-26961D913AD0}
1651 | 1284 | {523E8D89-671D-11E5-80CA-005056A729E5} | YOSEMITE | COARSEGOLD | Bank 2 | CB 2104 | PGE\JWCp | 2016-11-03 12:20:31.2777540 -07:00 | 2544302104 | 254432104 | 12 | 3 | 2 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1773 | {90333AD9-4E8A-4F8D-8980-EE8262BF6FB2}
1652 | 1285 | {523E8E4F-671D-11E5-80CA-005056A729E5} | YOSEMITE | CURTIS | Bank 1 | CB 1701 | PGE\BXYD | 2016-10-06 10:22:54.2307971 -07:00 | 1633501701 | 163351701 | 10 | 3 | 3 | 1 | 515 | 15.92 | 15.76 | 515 | 15.92 | 15.76 | 578 | 17.87 | 17.69 | 578 | 17.87 | 17.69 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 |  |  | FALSE | FALSE | 1455 | 1892 | 1746 | 2183 | {90BA7B9A-DACD-4BD8-93B2-6CC91315D701}
1655 | 1285 | {523E8E60-671D-11E5-80CA-005056A729E5} | YOSEMITE | CURTIS | Bank 1 | CB 1702 | PGE\BXYD | 2016-10-06 10:25:33.1130416 -07:00 | 1633501702 | 163351702 | 10 | 3 | 3 | 1 | 515 | 15.92 | 15.76 | 515 | 15.92 | 15.76 | 578 | 17.87 | 17.69 | 578 | 17.87 | 17.69 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 |  |  | FALSE | FALSE | 1455 | 1892 | 1746 | 2183 | {E19BBCD0-2B4A-423D-82CF-82B5014E1A6A}
1656 | 1285 | {523E8E68-671D-11E5-80CA-005056A729E5} | YOSEMITE | CURTIS | Bank 1 | CB 1703 | PGE\BXYD | 2016-10-06 10:27:42.2856665 -07:00 | 1633501703 | 163351703 | 10 | 3 | 3 | 1 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 |  |  | FALSE | FALSE | 1455 | 1892 | 1746 | 2183 | {DEFBA1FF-203B-4DC5-8BDA-C8CA9C0A3797}
1659 | 1286 | {58406AFC-671D-11E5-80CA-005056A729E5} | YOSEMITE | CURTIS | Bank 2 | CB 1704 | PGE\BXYD | 2016-10-06 10:35:07.2071330 -07:00 | 1633501704 | 163351704 | 10 | 3 | 3 | 1 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 |  |  | FALSE | FALSE | 1455 | 1892 | 1746 | 2183 | {55CC51AA-AB25-4E5A-B7F4-3800FBFCA70A}
1660 | 1286 | {58406B07-671D-11E5-80CA-005056A729E5} | YOSEMITE | CURTIS | Bank 2 | CB 1705 | PGE\BXYD | 2016-10-06 10:38:59.2030678 -07:00 | 1633501705 | 163351705 | 10 | 3 | 3 | 1 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 |  |  | FALSE | FALSE | 1455 | 1892 | 1746 | 2183 | {ADAD3BC2-0914-4359-B7AD-3D66880123EC}
1662 | 1287 | {58406B18-671D-11E5-80CA-005056A729E5} | YOSEMITE | DAIRYLAND | Bank 1 | CB 1102 | PGE\BXYD | 2016-10-06 10:50:31.0637469 -07:00 | 2524201102 | 252421102 | 8 | 3 | 3 | 1 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {119E46EF-1F46-4E25-A8F4-DA55E9740E67}
1663 | 1287 | {58406B23-671D-11E5-80CA-005056A729E5} | YOSEMITE | DAIRYLAND | Bank 1 | CB 1105 | PGE\JWCp | 2017-05-16 13:18:47.4224532 -07:00 | 2524201105 | 252421105 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {2107E5CA-01BC-4D38-9B4C-7285B58890DE}
1665 | 1287 | {58406B2E-671D-11E5-80CA-005056A729E5} | YOSEMITE | DAIRYLAND | Bank 1 | CB 1109 | PGE\BXYD | 2016-10-06 11:10:47.6488325 -07:00 | 2524201109 | 252421109 | 8 | 3 | 3 | 1 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {C38AB1F7-0CA3-4D4B-8C27-FF1C26FECA11}
1666 | 1288 | {369B0373-275E-11E6-B38D-D4BED91EFF1A} | YOSEMITE | DAIRYLAND | Bank 2 | CB 1111 | PGE\BXYD | 2016-10-06 11:30:14.9930953 -07:00 | 252421111 | 252421111 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {C87FB491-77B0-459B-A2BE-86234B4D285D}
1668 | 1288 | {58406B3F-671D-11E5-80CA-005056A729E5} | YOSEMITE | DAIRYLAND | Bank 2 | CB 1112 | PGE\BXYD | 2016-10-06 11:33:38.5604339 -07:00 | 2524201112 | 252421112 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 | 617 | 13.47 | 13.34 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {1AA8FD88-8933-4FD0-9FA2-A85D2C1A2EB7}
1669 | 1288 | {58406B44-671D-11E5-80CA-005056A729E5} | YOSEMITE | DAIRYLAND | Bank 2 | CB 1113 | PGE\VXRO | 2017-03-02 11:06:27.5923420 -08:00 | 2524201113 | 252421113 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {592E6874-7221-4E94-82CA-4A01EE0C4AD6}
1108 | 1048 | {9AA85C90-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | FORESTHILL | Bank 1 | CB 1101 | PGE\SDK6 | 2016-09-28 14:07:03.4917092 -07:00 | 1521801101 | 152181101 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {474ABAEE-FDCE-4026-A612-96636C6F5AC2}
1110 | 1048 | {9AA85CA0-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | FORESTHILL | Bank 1 | CB 1102 | PGE\SDK6 | 2016-09-28 14:07:45.9089446 -07:00 | 1521801102 | 152181102 | 8 | 3 | 3 | 1 | 154 | 3.36 | 3.33 | 154 | 3.36 | 3.33 | 173 | 3.78 | 3.74 | 173 | 3.78 | 3.74 | 216 | 4.71 | 4.66 | 216 | 4.71 | 4.66 | 228 | 4.98 | 4.93 | 228 | 4.98 | 4.93 |  | Limited by bus conductor | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {2F1F8DD8-DF80-4E1C-9C6D-131468ADE90E}
1111 | 1049 | {A0BFD465-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | HORSESHOE | Bank 1 | CB 1101 | PGE\SDK6 | 2016-09-20 12:56:14.8569895 -07:00 | 1525701101 | 152571101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {0793626F-E24F-476D-9E19-C1BB8636A5E4}
1112 | 1049 | {A0BFD475-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | HORSESHOE | Bank 1 | CB 1102 | PGE\SDK6 | 2016-09-20 13:07:06.6913790 -07:00 | 1525701102 | 152571102 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {7ABEE9CF-5328-4B62-A3AB-57A885667F4A}
1113 | 1049 | {A0BFD493-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | HORSESHOE | Bank 1 | CB 1103 | PGE\SDK6 | 2016-09-20 13:16:13.4874851 -07:00 | 1525701103 | 152571103 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 689 | 15.04 | 14.89 | 689 | 15.04 | 14.89 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 732 | 15.98 | 15.82 | 732 | 15.98 | 15.82 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F20DA312-E9D7-4F69-A9C6-892F3610CEDB}
1114 | 1050 | {A0BFD49F-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | HORSESHOE | Bank 2 | CB 1104 | PGE\SDK6 | 2016-09-20 13:36:00.5058471 -07:00 | 1525701104 | 152571104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {8230715B-B8E0-4799-AFA3-E02F0CCB49BC}
1115 | 1050 | {A0BFD4AF-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | HORSESHOE | Bank 2 | CB 1105 | PGE\SDK6 | 2016-09-20 13:42:08.7270287 -07:00 | 1525701105 | 152571105 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {00C96877-EF85-4A36-BBAF-3E8E653DD34F}
1116 | 1050 | {A0BFD4B8-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | HORSESHOE | Bank 2 | CB 1106 | PGE\SDK6 | 2016-09-20 13:48:04.7758767 -07:00 | 1525701106 | 152571106 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 689 | 15.04 | 14.89 | 689 | 15.04 | 14.89 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {68DB76BA-4CC7-4C2A-AAFB-2E416E9D036B}
1117 | 1054 | {D40DD86C-0B3F-11E6-9D37-D4BED91EFF1A} | CENTRAL COAST | WATSONVILLE | BANK 3 (Non SCADA) | CB 2101 (Non-SCADA) | PGE\JLDe | 2016-09-23 09:37:13.9916186 -07:00 | 0833302101 | 083332101 | 12 | 3 | 3 | 2 | 346 | 13.08 | 12.95 | 346 | 13.08 | 12.95 | 346 | 13.08 | 12.95 | 346 | 13.08 | 12.95 | 346 | 13.08 | 12.95 | 346 | 13.08 | 12.95 | 346 | 13.08 | 12.95 | 346 | 13.08 | 12.95 |  |  | FALSE | FALSE | 346 | 346 | 346 | 346 | {00000000-0000-0000-0000-000000000000}
1120 | 1055 | {A0BFD4CE-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | LINCOLN | Bank 1 | CB 1101 | PGE\SDK6 | 2016-09-28 14:11:30.7744608 -07:00 | 1537001101 | 153701101 | 8 | 3 | 3 | 1 | 745 | 16.26 | 16.1 | 745 | 16.26 | 16.1 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 1937 | {9819E34A-2EE5-4284-87F2-45304AED6497}
1122 | 1055 | {A0BFD4E5-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | LINCOLN | Bank 1 | CB 1102 | PGE\SDK6 | 2016-09-28 14:11:21.5980596 -07:00 | 1537001102 | 153701102 | 8 | 3 | 3 | 1 | 745 | 16.26 | 16.1 | 745 | 16.26 | 16.1 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 1937 | {83DBB839-0C9F-4E08-8393-12F4C7BF6CF1}
1123 | 1056 | {A0BFD4FF-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | LINCOLN | Bank 2 | CB 2108 | PGE\SDK6 | 2017-01-17 14:43:32.3089844 -08:00 | 1537002108 | 153702108 | 12 | 3 | 3 | 1 | 400 | 15.12 | 14.97 | 290 | 10.96 | 10.85 | 400 | 15.12 | 14.97 | 290 | 10.96 | 10.85 | 400 | 15.12 | 14.97 | 290 | 10.96 | 10.85 | 400 | 15.12 | 14.97 | 290 | 10.96 | 10.85 | Need to have 12/21kV 7500 KVA auto-bank available in pick-list. |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1688 | {B09D9B06-A7DE-41D4-A087-539865E14DE7}
1124 | 1057 | {54FAE9C7-0B41-11E6-9D37-D4BED91EFF1A} | SIERRA | LINCOLN | Bank 3 | CB 1104 (Non-SCADA) | PGE\SDK6 | 2016-12-01 16:37:29.7428370 -08:00 | 1537001104 | 153701104 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 447 | 9.76 | 9.66 | 447 | 9.76 | 9.66 | 514 | 11.22 | 11.11 | 514 | 11.22 | 11.11 | 549 | 11.98 | 11.86 | 549 | 11.98 | 11.86 |  |  | FALSE | FALSE | 733 | 830 | 830 | 830 | {AD3DD978-FA0D-44DB-959F-B6F86062042A}
1125 | 1057 | {A0BFD512-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | LINCOLN | Bank 3 | CB 1105 | PGE\SDK6 | 2016-09-21 17:21:34.9203858 -07:00 | 1537001105 | 153701105 | 8 | 3 | 3 | 1 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 733 | 830 | 830 | 830 | {B1AE606C-DFB4-4D15-95CD-E5D15A5D1505}
1127 | 1058 | {46F10837-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | ARANA | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\ACT0 | 2016-11-23 09:50:59.0230785 -08:00 | 083010401 | 083010401 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {919641A3-5977-4867-A6A4-225300681202}
1128 | 1059 | {46F1083D-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | ARANA | Bank 2 (Non SCADA) | CB 402 (Non-SCADA) | PGE\ACT0 | 2016-11-23 09:53:22.3136595 -08:00 | 083010402 | 083010402 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 450 | 3.41 | 3.38 | 450 | 3.41 | 3.38 |  |  | FALSE | FALSE | 330 | 429 | 396 | 495 | {21522028-50E7-451E-8DFC-06DCFB8EEDE8}
1129 | 1061 | {46F10846-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | BEN LOMOND | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\MTDR | 2017-07-11 16:31:00.7722575 -07:00 | 083040401 | 083040401 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 455 | 3.44 | 3.41 | 455 | 3.44 | 3.41 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {00331E5F-2CD9-40AE-B955-D0E9B009C39B}
1130 | 1062 | {4D3DDA96-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | BEN LOMOND | Bank 2 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\ACT0 | 2016-09-22 16:15:29.3286050 -07:00 | 083041101 | 083041101 | 8 | 3 | 3 | 2 | 164 | 3.58 | 3.54 | 164 | 3.58 | 3.54 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 197 | 4.3 | 4.26 | 197 | 4.3 | 4.26 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 |  |  | FALSE | FALSE | 164 | 214 | 197 | 247 | {00000000-0000-0000-0000-000000000000}
1131 | 1063 | {1B45BE2C-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | SAN PABLO | Bank 1 | CB 1105 | PGE\C7CF | 2016-12-19 12:37:25.9005970 -08:00 | 0143701105 | 014371105 | 8 | 3 | 3 | 2 | 595 | 12.99 | 12.86 | 595 | 12.99 | 12.86 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 613 | 13.38 | 13.25 | 613 | 13.38 | 13.25 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {54C276B5-F5C8-4275-A1D4-51023FA69CD2}
1132 | 1063 | {1B45BE43-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | SAN PABLO | Bank 1 | CB 1106 | PGE\C7CF | 2016-12-19 12:37:11.2981546 -08:00 | 0143701106 | 014371106 | 8 | 3 | 3 | 2 | 595 | 12.99 | 12.86 | 595 | 12.99 | 12.86 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 613 | 13.38 | 13.25 | 613 | 13.38 | 13.25 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {DA34ECF2-AB4C-493E-A89E-6ADBD2A34908}
1133 | 1066 | {946B53AE-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | DEL MAR | Bank 1 | CB 1103 | PGE\SDK6 | 2016-09-28 14:28:08.2251299 -07:00 | 1525801103 | 152581103 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 666 | 14.53 | 14.38 | 666 | 14.53 | 14.38 | 711 | 15.52 | 15.36 | 711 | 15.52 | 15.36 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {B998F9B1-53A7-4A59-8A5F-3E61866CEAF1}
1134 | 1066 | {946B53BE-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | DEL MAR | Bank 1 | CB 1104 | PGE\SDK6 | 2016-12-01 15:04:40.5805591 -08:00 | 1525801104 | 152581104 | 8 | 3 | 3 | 1 | 573 | 12.51 | 12.38 | 573 | 12.51 | 12.38 | 720 | 15.71 | 15.55 | 720 | 15.71 | 15.55 | 634 | 13.84 | 13.7 | 634 | 13.84 | 13.7 | 720 | 15.71 | 15.55 | 720 | 15.71 | 15.55 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {79649E96-44CF-44A5-8848-BB187AAABEFB}
1135 | 1065 | {F4276553-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | POINT PINOLE | Bank 1 | CB 1101 | PGE\C7CF | 2016-12-19 11:43:17.1376305 -08:00 | 0142601101 | 014261101 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {354C93F9-0897-41D3-80F7-9473F4751E81}
1136 | 1065 | {F427656D-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | POINT PINOLE | Bank 1 | CB 1102 | PGE\C7CF | 2016-12-19 11:44:28.7123711 -08:00 | 0142601102 | 014261102 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {30DE6984-10F7-415A-8DC9-4D8FA582DD47}
1137 | 1065 | {FA7767AD-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | POINT PINOLE | Bank 1 | CB 1103 | PGE\C7CF | 2016-12-19 11:45:27.0635079 -08:00 | 0142601103 | 014261103 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {149F7324-1D9B-4E11-B401-7133084C1711}
1138 | 1067 | {946B53D1-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | DEL MAR | Bank 2 | CB 2105 | PGE\SDK6 | 2016-09-22 16:28:38.3334561 -07:00 | 1525802105 | 152582105 | 12 | 3 | 3 | 1 | 733 | 27.7 | 27.42 | 733 | 27.7 | 27.42 | 733 | 27.7 | 27.42 | 733 | 27.7 | 27.42 | 733 | 27.7 | 27.42 | 733 | 27.7 | 27.42 | 733 | 27.7 | 27.42 | 733 | 27.7 | 27.42 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1158 | {3FBFF3E9-AB6F-4913-A72E-CC5AD19BCE40}
1139 | 1067 | {946B53E8-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | DEL MAR | Bank 2 | CB 2106 | PGE\SDK6 | 2016-12-01 15:03:42.2187795 -08:00 | 1525802106 | 152582106 | 12 | 3 | 3 | 1 | 530 | 20.03 | 19.83 | 530 | 20.03 | 19.83 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1158 | {AB0DB495-7607-44F7-B0C4-A3F7FB84E872}
1140 | 1069 | {9EFE5B11-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | VALLEY VIEW | Bank 1 | CB 1103 | PGE\C7CF | 2016-12-19 12:44:40.7132900 -08:00 | 0143401103 | 014341103 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {092BF216-B03B-4CEF-B09E-A7E6B8EC8633}
1141 | 1070 | {A5932E6C-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | VALLEY VIEW | Bank 2 | CB 1105 | PGE\C7CF | 2016-12-19 12:45:19.9565955 -08:00 | 0143401105 | 014341105 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {AAC9E309-9EC0-48BF-A054-E6DFE134F5A1}
1142 | 1070 | {ABFB73AA-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | VALLEY VIEW | Bank 2 | CB 1106 | PGE\C7CF | 2016-12-19 12:45:41.4738028 -08:00 | 0143401106 | 014341106 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {4E3F3565-2556-4D07-BF3A-2A46D741F2FB}
1143 | 1071 | {946B53F4-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | DEL MAR | Bank 3 | CB 2109 | PGE\SDK6 | 2016-09-22 17:08:06.9488811 -07:00 | 1525802109 | 152582109 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 674 | 25.47 | 25.22 | 674 | 25.47 | 25.22 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1667 | {064DD2AC-0F41-48C8-9B9C-0535C62180F4}
1144 | 1072 | {D5CDDA6C-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | FRANKLIN | Bank 1 | CB 1101 | PGE\C7CF | 2016-12-12 15:02:17.8420675 -08:00 | 0139201101 | 013921101 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {C7674DA5-B466-42F0-B853-627B7E5B0152}
1145 | 1072 | {D5CDDA80-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | FRANKLIN | Bank 1 | CB 1102 | PGE\C7CF | 2016-12-12 15:02:55.9828645 -08:00 | 0139201102 | 013921102 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {279C03D5-687D-45A3-9125-48B794E50014}
1146 | 1073 | {D5CDDA8E-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | FRANKLIN | Bank 2 | CB 1103 | PGE\C7CF | 2016-12-12 15:08:06.3520335 -08:00 | 0139201103 | 013921103 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {85583B98-FC8E-41B6-BCFD-C39206A4079E}
1147 | 1073 | {DBC6BCCE-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | FRANKLIN | Bank 2 | CB 1104 | PGE\C7CF | 2016-12-12 15:08:37.2515270 -08:00 | 0139201104 | 013921104 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {824B01C7-1D83-41C5-96E3-265BCD1A2942}
1148 | 1071 | {946B5412-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | DEL MAR | Bank 3 | CB 2110 | PGE\SDK6 | 2016-09-22 17:12:20.0411385 -07:00 | 1525802110 | 152582110 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1667 | {B89222B8-14E5-4A91-ADC3-B6B33CDA143A}
1149 | 1074 | {41121FB7-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 1 | CB 1103 (Non-SCADA) | PGE\C7CF | 2016-12-12 13:31:42.7133434 -08:00 | 0125001103 | 012501103 | 8 | 3 | 3 | 2 | 445 | 9.71 | 9.61 | 445 | 9.71 | 9.61 | 494 | 10.78 | 10.67 | 494 | 10.78 | 10.67 | 458 | 10 | 9.9 | 458 | 10 | 9.9 | 509 | 11.11 | 11 | 509 | 11.11 | 11 |  |  | FALSE | FALSE | 1541 | 2004 | 1850 | 2312 | {0E9ED6BE-3275-4DDF-9FB2-6022D36ADFDD}
1150 | 1074 | {41121FBD-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 1 | CB 1108 (Non-SCADA) | PGE\C7CF | 2017-05-24 11:03:53.6761788 -07:00 | 0125001108 | 012501108 | 7 | 3 | 3 | 2 | 446 | 9.63 | 9.53 | 446 | 9.63 | 9.53 | 549 | 11.86 | 11.74 | 549 | 11.86 | 11.74 | 459 | 9.91 | 9.81 | 459 | 9.91 | 9.81 | 556 | 12.01 | 11.89 | 556 | 12.01 | 11.89 |  |  | FALSE | FALSE | 1541 | 2004 | 1850 | 2312 | {3EB15A8F-8B5E-4EAD-9EC1-97B56E4B20B6}
1151 | 1074 | {41121FC0-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 1 | CB 1109 (Non-SCADA) | PGE\C7CF | 2017-05-24 11:09:46.2006773 -07:00 | 0125001109 | 012501109 | 7 | 3 | 3 | 2 | 492 | 10.63 | 10.52 | 467 | 10.09 | 9.99 | 554 | 11.97 | 11.85 | 526 | 11.36 | 11.25 | 560 | 12.1 | 11.98 | 532 | 11.49 | 11.38 | 598 | 12.92 | 12.79 | 568 | 12.27 | 12.15 |  |  | FALSE | FALSE | 1541 | 2004 | 1850 | 2312 | {C316DF8C-7E90-45DC-88F5-7ECB1CF75B56}
1153 | 1074 | {41121FC6-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 1 | CB 1112 (Non-SCADA) | PGE\MUSF | 2017-04-06 15:37:16.1264263 -07:00 | 0125001112 | 012501112 | 7 | 3 | 3 | 2 | 427 | 9.22 | 9.13 | 427 | 9.22 | 9.13 | 474 | 10.24 | 10.14 | 474 | 10.24 | 10.14 | 440 | 9.5 | 9.41 | 440 | 9.5 | 9.41 | 488 | 10.54 | 10.43 | 488 | 10.54 | 10.43 |  |  | FALSE | FALSE | 1541 | 2004 | 1850 | 2312 | {8450F6A0-0101-4C28-8B99-4B17F538F04C}
1154 | 1068 | {4D3DDAA8-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | BIG BASIN | Bank 1 (Non SCADA) | CB 1101 | PGE\ACT0 | 2016-09-23 07:27:51.0018131 -07:00 | 0828401101 | 082841101 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 601 | 577 | 601 | {E2C19432-B401-43A8-BA2D-9DE4592266A6}
1155 | 1068 | {53724322-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | BIG BASIN | Bank 1 (Non SCADA) | CB 1102 | PGE\ACT0 | 2016-09-23 07:31:33.4301547 -07:00 | 0828401102 | 082841102 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 601 | 577 | 601 | {CD101492-6FA2-415E-A2D9-84881606EFD9}
1156 | 1077 | {5986A0B3-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | BIG TREES | Bank 2 (Non SCADA) | CB 402 (Non-SCADA) | PGE\ACT0 | 2016-09-26 09:46:00.4506741 -07:00 | 083050402 | 083050402 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 455 | 3.44 | 3.41 | 455 | 3.44 | 3.41 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {2B9E0421-8E91-4392-B133-DCEC46F4C45C}
1157 | 1078 | {5986A0BF-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | BORONDA | Bank 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\ACT0 | 2016-11-23 09:58:14.6285801 -08:00 | 1824601101 | 182461101 | 8 | 3 | 3 | 2 | 316 | 6.9 | 6.83 | 316 | 6.9 | 6.83 | 411 | 8.97 | 8.88 | 411 | 8.97 | 8.88 | 379 | 8.27 | 8.19 | 379 | 8.27 | 8.19 | 474 | 10.34 | 10.24 | 474 | 10.34 | 10.24 |  |  | FALSE | FALSE | 316 | 411 | 379 | 474 | {07C47F44-EDE4-48AE-8C67-7C2655DE5997}
1158 | 1078 | {5986A0C5-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | BORONDA | Bank 1 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\ACT0 | 2016-11-23 10:00:20.3537217 -08:00 | 1824601102 | 182461102 | 8 | 3 | 3 | 2 | 316 | 6.9 | 6.83 | 316 | 6.9 | 6.83 | 411 | 8.97 | 8.88 | 411 | 8.97 | 8.88 | 379 | 8.27 | 8.19 | 379 | 8.27 | 8.19 | 474 | 10.34 | 10.24 | 474 | 10.34 | 10.24 |  |  | FALSE | FALSE | 316 | 411 | 379 | 474 | {627109B7-66EC-4E8E-9F82-96A7CF4464C9}
1160 | 1079 | {5986A0CE-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | BUENA VISTA | Bank 1 | CB 1101 | PGE\MTDR | 2017-07-10 12:54:52.6257552 -07:00 | 1822601101 | 182261101 | 8 | 3 | 3 | 2 | 468 | 10.21 | 10.11 | 468 | 10.21 | 10.11 | 584 | 12.75 | 12.62 | 570 | 12.44 | 12.32 | 489 | 10.67 | 10.56 | 489 | 10.67 | 10.56 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {11A7D8AF-4CCD-4BEA-9A9D-1A59435D795C}
1162 | 1079 | {5986A0D3-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | BUENA VISTA | Bank 1 | CB 1102 | PGE\ACT0 | 2016-11-23 10:48:11.3402820 -08:00 | 1822601102 | 182261102 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {7ABAA536-29AB-4014-BFBB-C6A3AC89D62C}
1163 | 1079 | {5FB1E15C-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | BUENA VISTA | Bank 1 | CB 1106 | PGE\ACT0 | 2016-11-23 10:49:27.7850126 -08:00 | 1822601106 | 182261106 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {3BC6FA8E-15F7-47CB-8E20-E753A8AA6D2E}
1164 | 1080 | {5FB1E16A-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | BUENA VISTA | Bank 3 | CB 1103 | PGE\MTDR | 2017-07-10 13:01:14.8150550 -07:00 | 1822601103 | 182261103 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {ADD26351-9DE4-49A9-9EC9-27A757B9F344}
1165 | 1080 | {5FB1E16F-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | BUENA VISTA | Bank 3 | CB 1104 | PGE\ACT0 | 2016-11-23 10:55:57.9805642 -08:00 | 1822601104 | 182261104 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {9D2B3240-4EC0-4254-99C1-112F48841815}
1167 | 1081 | {6A93CA93-0B42-11E6-9D37-D4BED91EFF1A} | CENTRAL COAST | BURNS | BANK 1 (Non SCADA) | CB 2101 (Non-SCADA) | PGE\ACT0 | 2016-09-26 12:07:37.7372334 -07:00 | 1835802101 | 183582101 | 12 | 3 | 3 | 2 | 423 | 15.99 | 15.83 | 423 | 15.99 | 15.83 | 550 | 20.79 | 20.58 | 550 | 20.79 | 20.58 | 508 | 19.2 | 19.01 | 508 | 19.2 | 19.01 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 423 | 550 | 508 | 635 | {CF889828-6CC5-4DEC-A1A9-C38D91E464EB}
1170 | 1082 | {5FB1E180-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | CAMP EVERS | Bank 1 | CB 2103 | PGE\ACT0 | 2016-09-26 09:53:51.0207144 -07:00 | 0836202103 | 083622103 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 758 | 28.65 | 28.36 | 758 | 28.65 | 28.36 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 768 | 29.03 | 28.74 | 768 | 29.03 | 28.74 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {D1937979-0473-4C25-AE78-38F9FA2CA58E}
1171 | 1082 | {660B0FD2-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | CAMP EVERS | Bank 1 | CB 2104 | PGE\JLDe | 2017-03-13 14:48:01.2164777 -07:00 | 0836202104 | 083622104 | 12 | 3 | 3 | 2 | 1000 | 37.79 | 37.41 | 1000 | 37.79 | 37.41 | 1000 | 37.79 | 37.41 | 1000 | 37.79 | 37.41 | 1000 | 37.79 | 37.41 | 1000 | 37.79 | 37.41 | 1000 | 37.79 | 37.41 | 1000 | 37.79 | 37.41 | 1) If SW V0004 or V0012 are open, then the circuit is only good for SN: 628A, SE: 772A, WN: 647A, WE 821A. |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {43E5852F-C93A-4B05-B7F4-9DBB7FB22D39}
1172 | 1084 | {B31C2078-671D-11E5-80CA-005056A729E5} | FRESNO | CALIFORNIA AVE | Bank 1 | CB 1110 | PGE\BXYD | 2016-09-27 08:51:25.6983092 -07:00 | 2522801110 | 252281110 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {30D8EB2B-4C34-47EA-B2E0-82F6D5EFE3F6}
1173 | 1083 | {6C88B5FF-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | CAMP EVERS | Bank 2 | CB 2105 | PGE\MTDR | 2017-07-10 13:22:17.1364384 -07:00 | 0836202105 | 083622105 | 12 | 3 | 3 | 2 | 541 | 20.45 | 20.25 | 541 | 20.45 | 20.25 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {4EC3BF2F-5D0A-47B7-AEF7-51C48B5C6675}
1174 | 1084 | {B31C207D-671D-11E5-80CA-005056A729E5} | FRESNO | CALIFORNIA AVE | Bank 1 | CB 1113 | PGE\BXYD | 2016-09-27 08:51:12.0003678 -07:00 | 2522801113 | 252281113 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {253DBE7F-72AA-4A41-8DE6-92DB164FDDE9}
1175 | 1084 | {B31C2082-671D-11E5-80CA-005056A729E5} | FRESNO | CALIFORNIA AVE | Bank 1 | CB 1114 | PGE\BXYD | 2017-01-24 14:22:52.5805875 -08:00 | 2522801114 | 252281114 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {57FD7591-78CE-4D95-9CBA-DA2DE9CD5F13}
1176 | 1084 | {B31C2087-671D-11E5-80CA-005056A729E5} | FRESNO | CALIFORNIA AVE | Bank 1 | CB 1117 | PGE\BXYD | 2017-01-24 14:23:27.2600544 -08:00 | 2522801117 | 252281117 | 8 | 3 | 3 | 1 | 376 | 8.21 | 8.13 | 357 | 7.79 | 7.71 | 420 | 9.17 | 9.08 | 399 | 8.71 | 8.62 | 482 | 10.52 | 10.41 | 457 | 9.97 | 9.87 | 500 | 10.91 | 10.8 | 489 | 10.67 | 10.56 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {27327321-6F63-4D77-9381-5077D5397EE5}
1177 | 1085 | {B91B8C37-671D-11E5-80CA-005056A729E5} | FRESNO | CALIFORNIA AVE | Bank 2 | CB 1106 | PGE\BXYD | 2017-01-24 14:25:19.7382174 -08:00 | 2522801106 | 252281106 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3070 | {E4AA134B-6D4D-4B32-A31D-F80CB9200776}
1178 | 1085 | {B91B8C45-671D-11E5-80CA-005056A729E5} | FRESNO | CALIFORNIA AVE | Bank 2 | CB 1111 | PGE\BXYD | 2017-01-24 14:26:00.4237998 -08:00 | 2522801111 | 252281111 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. | Note 2 | FALSE | FALSE | 2061 | 2680 | 2474 | 3070 | {2FE386E9-3949-4A97-A617-EDD0AA5986B2}
1179 | 1085 | {B91B8C4A-671D-11E5-80CA-005056A729E5} | FRESNO | CALIFORNIA AVE | Bank 2 | CB 1112 | PGE\BXYD | 2017-01-24 14:26:49.5959454 -08:00 | 2522801112 | 252281112 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 456 | 9.95 | 9.85 | 539 | 11.76 | 11.64 | 512 | 11.17 | 11.06 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 666 | 14.53 | 14.38 | 632 | 13.79 | 13.65 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3070 | {116AD7AE-E0D8-4240-B7B1-EA7870CE0ED2}
1180 | 1085 | {B91B8C58-671D-11E5-80CA-005056A729E5} | FRESNO | CALIFORNIA AVE | Bank 2 | CB 1116 | PGE\BXYD | 2017-01-24 14:28:13.5567600 -08:00 | 2522801116 | 252281116 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3070 | {FED0F4C5-EAEE-4466-A5E0-12F62AE8B4DC}
1181 | 1086 | {B91B8C63-671D-11E5-80CA-005056A729E5} | FRESNO | CALIFORNIA AVE | Bank 3 | CB 1102 | PGE\BXYD | 2017-01-24 14:30:04.6152957 -08:00 | 2522801102 | 252281102 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {65D6A1DC-90F4-49E8-99E5-99695233EC42}
1182 | 1083 | {82E11DC6-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | CAMP EVERS | Bank 2 | CB 2106 | PGE\ACT0 | 2016-09-27 08:55:12.5445585 -07:00 | 0836202106 | 083622106 | 12 | 3 | 3 | 2 | 541 | 20.45 | 20.25 | 541 | 20.45 | 20.25 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {3D8927C3-EC62-4B9E-894E-1A542FE07829}
1183 | 1086 | {B91B8C6B-671D-11E5-80CA-005056A729E5} | FRESNO | CALIFORNIA AVE | Bank 3 | CB 1103 | PGE\BXYD | 2017-01-24 14:31:25.7680563 -08:00 | 2522801103 | 252281103 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {6DD0E6BB-1C67-497F-8455-500A39D53A0A}
1185 | 1086 | {B91B8C70-671D-11E5-80CA-005056A729E5} | FRESNO | CALIFORNIA AVE | Bank 3 | CB 1104 | PGE\BXYD | 2017-01-24 14:36:06.3394518 -08:00 | 2522801104 | 252281104 | 8 | 3 | 3 | 1 | 376 | 8.21 | 8.13 | 357 | 7.79 | 7.71 | 420 | 9.17 | 9.08 | 399 | 8.71 | 8.62 | 482 | 10.52 | 10.41 | 457 | 9.97 | 9.87 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {5938EA66-CDD6-4835-B8F8-42C77607859F}
1186 | 1086 | {B91B8C78-671D-11E5-80CA-005056A729E5} | FRESNO | CALIFORNIA AVE | Bank 3 | CB 1108 | PGE\BXYD | 2017-01-24 14:37:03.0153417 -08:00 | 2522801108 | 252281108 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {017A3D52-0025-41BD-8EC2-B6831CDB297F}
1187 | 1087 | {B91B8C86-671D-11E5-80CA-005056A729E5} | FRESNO | CAMDEN | Bank 1 | CB 1103 | PGE\BXYD | 2017-01-24 14:15:22.4495313 -08:00 | 2523001103 | 252301103 | 8 | 3 | 3 | 1 | 282 | 6.15 | 6.09 | 267 | 5.83 | 5.77 | 315 | 6.87 | 6.8 | 299 | 6.53 | 6.46 | 358 | 7.81 | 7.73 | 340 | 7.42 | 7.35 | 382 | 8.34 | 8.26 | 362 | 7.9 | 7.82 | TOTAL CAPABILITY SHOULD BE THE ADDITION OF 2-1/0CU CONDUCTOR BRANCHES Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19 Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F4B03376-6670-4ADF-9FAA-A050CBC1D701}
1188 | 1087 | {B91B8C97-671D-11E5-80CA-005056A729E5} | FRESNO | CAMDEN | Bank 1 | CB 1104 | PGE\BXYD | 2016-10-14 08:45:15.3842971 -07:00 | 2523001104 | 252301104 | 8 | 3 | 3 | 1 | 583 | 12.72 | 12.59 | 583 | 12.72 | 12.59 | 583 | 12.72 | 12.59 | 583 | 12.72 | 12.59 | 583 | 12.72 | 12.59 | 583 | 12.72 | 12.59 | 583 | 12.72 | 12.59 | 583 | 12.72 | 12.59 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19 Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {EDA84A68-5C2D-4651-A848-E5B572E4E3C9}
1189 | 1087 | {B91B8CA2-671D-11E5-80CA-005056A729E5} | FRESNO | CAMDEN | Bank 1 | CB 1105 | PGE\BXYD | 2016-09-27 09:47:38.8952279 -07:00 | 2523001105 | 252301105 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19 Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {D41C8B01-55DE-4D42-A78E-28956687E43E}
1190 | 1088 | {B91B8CAD-671D-11E5-80CA-005056A729E5} | FRESNO | CAMDEN | Bank 2 | CB 1102 | PGE\BXYD | 2017-01-24 14:17:38.2969437 -08:00 | 2523001102 | 252301102 | 7 | 3 | 3 | 1 | 486 | 10.5 | 10.4 | 486 | 10.5 | 10.4 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 486 | 583 | 583 | 583 | {0A1AE486-A4D6-41E8-84AB-2F092C80CCDC}
1194 | 1090 | {B91B8CF1-671D-11E5-80CA-005056A729E5} | FRESNO | CARUTHERS | Bank 1 | CB 1101 | PGE\BXYD | 2016-09-27 14:29:06.4701105 -07:00 | 2523701101 | 252371101 | 8 | 3 | 3 | 1 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | LF=90 for both Summer and Winter Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {86DFC75A-C7D0-422D-A4AF-C10918E56DFF}
1196 | 1090 | {B91B8CFC-671D-11E5-80CA-005056A729E5} | FRESNO | CARUTHERS | Bank 1 | CB 1102 | PGE\BXYD | 2016-09-27 11:32:39.6320763 -07:00 | 2523701102 | 252371102 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {86565219-795D-41F6-BCA9-0517193FCC70}
1197 | 1091 | {8FD03533-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | CAMPHORA | Bank 2 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\ACT0 | 2016-09-27 11:35:05.8931550 -07:00 | 1820701101 | 182071101 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 601 | 577 | 601 | {F311CFBA-D3AE-41C5-BB8E-0EC1E517EF6E}
1198 | 1092 | {B91B8D0D-671D-11E5-80CA-005056A729E5} | FRESNO | CARUTHERS | Bank 2 | CB 1104 | PGE\BXYD | 2016-09-27 14:28:50.5082415 -07:00 | 2523701104 | 252371104 | 8 | 3 | 3 | 1 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2060 | {53421A51-BAA4-4D37-939C-B285EBD55734}
1199 | 1092 | {B91B8D1E-671D-11E5-80CA-005056A729E5} | FRESNO | CARUTHERS | Bank 2 | CB 1105 | PGE\BXYD | 2016-09-27 14:28:35.6697885 -07:00 | 2523701105 | 252371105 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2060 | {6EBC0B35-3DC7-44DE-8154-0EB964C71636}
1201 | 1093 | {9633EAA7-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | CARMEL | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\MTDR | 2017-07-10 13:39:40.3530128 -07:00 | 182040401 | 182040401 | 4 | 3 | 3 | 2 | 521 | 3.94 | 3.9 | 494 | 3.74 | 3.7 | 587 | 4.44 | 4.4 | 557 | 4.22 | 4.18 | 593 | 4.49 | 4.45 | 563 | 4.26 | 4.22 | 633 | 4.79 | 4.74 | 601 | 4.55 | 4.5 | 1) 267 Al is the tie between Carmel 401 and Carmel 402. 2) 5% Derate for unbalance for capability study. |  | FALSE | FALSE | 570 | 741 | 684 | 856 | {2B8AF68E-6317-417C-82A4-7CA8CDA949ED}
1202 | 1093 | {9633EAAA-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | CARMEL | Bank 1 (Non SCADA) | CB 402 (Non-SCADA) | PGE\ACT0 | 2016-11-18 09:36:34.4219443 -08:00 | 182040402 | 182040402 | 4 | 3 | 3 | 1 | 440 | 3.33 | 3.3 | 440 | 3.33 | 3.3 | 578 | 4.37 | 4.33 | 578 | 4.37 | 4.33 | 528 | 4 | 3.96 | 528 | 4 | 3.96 | 600 | 4.54 | 4.49 | 600 | 4.54 | 4.49 | 1) OH conductor not derated for imbalance. Use highest phase for clearance loading. |  | FALSE | FALSE | 570 | 741 | 684 | 856 | {7277B23F-78DB-4CB3-9A8F-D225B4CBAEC4}
1203 | 1093 | {9633EAB0-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | CARMEL | Bank 1 (Non SCADA) | CB 403 (Non-SCADA) | PGE\ACT0 | 2016-11-23 10:58:11.9972405 -08:00 | 182040403 | 182040403 | 4 | 3 | 3 | 2 | 468 | 3.54 | 3.5 | 468 | 3.54 | 3.5 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 1) 397_AAC is the tie to the Carmel 402 circuit @ SW 8507. |  | FALSE | FALSE | 570 | 741 | 684 | 856 | {A4D5C591-F2E6-4B61-8925-849D4BC81A50}
1204 | 1094 | {B91B8D2F-671D-11E5-80CA-005056A729E5} | FRESNO | CLOVIS | Bank 1 | CB 1101 | PGE\BXYD | 2017-02-08 11:43:34.4120309 -08:00 | 2540801101 | 254081101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Note 1: Relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 2061 | 2500 | 2474 | 2500 | {E3B78484-2FA9-47EC-92FC-129D2A0D3156}
1205 | 1094 | {B91B8D37-671D-11E5-80CA-005056A729E5} | FRESNO | CLOVIS | Bank 1 | CB 1102 | PGE\BXYD | 2017-01-24 13:10:43.8717447 -08:00 | 2540801102 | 254081102 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Note 1: Relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {81D67F3C-C3B2-483D-B744-ECC710416929}
1206 | 1096 | {9633EAB6-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | CARMEL | Bank 2 (Non SCADA) | CB 405 (Non-SCADA) | PGE\ACT0 | 2016-11-18 09:46:33.2219271 -08:00 | 182040405 | 182040405 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {7D742DE6-1222-4265-A443-7CC4C26A0B78}
1207 | 1094 | {B91B8D45-671D-11E5-80CA-005056A729E5} | FRESNO | CLOVIS | Bank 1 | CB 1103 | PGE\BXYD | 2017-01-24 13:13:10.0309554 -08:00 | 2540801103 | 254081103 | 8 | 3 | 3 | 1 | 540 | 11.78 | 11.66 | 540 | 11.78 | 11.66 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 598 | 13.05 | 12.92 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Note 1: Relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {513B2BAE-8D22-40F4-B30A-ECD1CCAAA892}
1208 | 1094 | {B91B8D4A-671D-11E5-80CA-005056A729E5} | FRESNO | CLOVIS | Bank 1 | CB 1104 | PGE\BXYD | 2016-11-28 16:10:50.2350932 -08:00 | 2540801104 | 254081104 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {E233D185-C28C-4110-BB19-C205F84F3455}
1209 | 1098 | {9633EAC2-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | CASSERLY | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\ACT0 | 2016-09-27 14:32:27.4282208 -07:00 | 083110401 | 083110401 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {43743B51-9D23-4DAE-99D5-865C470778EA}
1210 | 1097 | {B91B8D55-671D-11E5-80CA-005056A729E5} | FRESNO | CLOVIS | Bank 2 | CB 1105 | PGE\BXYD | 2017-01-24 13:18:34.8292014 -08:00 | 2540801105 | 254081105 | 8 | 3 | 3 | 1 | 661 | 14.43 | 14.29 | 661 | 14.43 | 14.29 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1770 | 2235 | 2445 | 2805 | {DE3CE842-BEB2-461A-B7CF-4F87F3E66988}
1211 | 1099 | {9633EACB-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | CASTROVILLE | Bank 1 | CB 2103 | PGE\ACT0 | 2016-09-27 15:32:32.2310060 -07:00 | 1823502103 | 182352103 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 801 | 1042 | 962 | 1202 | {1964BF45-EA76-4C3D-B243-21E1A7B11140}
1212 | 1099 | {9C8D8E39-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | CASTROVILLE | Bank 1 | CB 2104 | PGE\ACT0 | 2016-09-27 15:39:19.5408331 -07:00 | 1823502104 | 182352104 | 11 | 4 | 4 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 801 | 1042 | 962 | 1202 | {4AB13447-76CC-40B9-9C67-DBB4FBBA9C53}
1213 | 1100 | {A2EED31B-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | CLIFF DRIVE | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\ACT0 | 2016-11-23 10:22:13.8609269 -08:00 | 083230401 | 083230401 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 450 | 3.41 | 3.38 | 450 | 3.41 | 3.38 |  |  | FALSE | FALSE | 330 | 429 | 396 | 495 | {D061E1A5-8736-48EB-82DC-B0CEB7B1F554}
1215 | 1097 | {B91B8D6D-671D-11E5-80CA-005056A729E5} | FRESNO | CLOVIS | Bank 2 | CB 1106 | PGE\BXYD | 2016-11-29 11:40:40.4928201 -08:00 | 2540801106 | 254081106 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {1C85DAE8-921D-4629-A7A6-4205569CAB5A}
1216 | 1102 | {A7233074-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PENRYN | Bank 1 | CB 1103 | PGE\SDK6 | 2016-09-27 17:20:54.7570294 -07:00 | 1525601103 | 152561103 | 8 | 4 | 4 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 962 | {29374C79-4BB4-4171-9490-EA5A75F349BE}
1218 | 1101 | {A2EED321-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | CLIFF DRIVE | Bank 2 (Non SCADA) | CB 402 (Non-SCADA) | PGE\ACT0 | 2016-11-23 11:05:16.8121614 -08:00 | 083230402 | 083230402 | 4 | 3 | 3 | 2 | 468 | 3.54 | 3.5 | 468 | 3.54 | 3.5 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 |  |  | FALSE | FALSE | 619 | 749 | 743 | 749 | {E17487E9-9CFE-4DD2-8B7D-053E35304064}
1219 | 1101 | {A2EED324-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | CLIFF DRIVE | Bank 2 (Non SCADA) | CB 403 (Non-SCADA) | PGE\ACT0 | 2016-11-23 11:07:47.3867952 -08:00 | 083230403 | 083230403 | 4 | 3 | 3 | 2 | 468 | 3.54 | 3.5 | 468 | 3.54 | 3.5 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 |  |  | FALSE | FALSE | 619 | 749 | 743 | 749 | {F0D920DE-80BD-4B99-B5E2-99A28DA7C570}
1220 | 1105 | {A2EED32D-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | COAST RD | Bank 2 (Non SCADA) | CB 401 (Non-SCADA) | PGE\J2T4 | 2017-03-02 14:13:39.1375291 -08:00 | 088820401 | 088820401 | 4 | 3 | 3 | 2 | 149 | 1.13 | 1.12 | 149 | 1.13 | 1.12 | 150 | 1.14 | 1.13 | 150 | 1.14 | 1.13 | 150 | 1.14 | 1.13 | 150 | 1.14 | 1.13 | 150 | 1.14 | 1.13 | 150 | 1.14 | 1.13 |  |  | FALSE | FALSE | 149 | 156 | 163 | 173 | {00000000-0000-0000-0000-000000000000}
1221 | 1097 | {B91B8D72-671D-11E5-80CA-005056A729E5} | FRESNO | CLOVIS | Bank 2 | CB 1107 | PGE\BXYD | 2017-01-24 13:21:33.9206454 -08:00 | 2540801107 | 254081107 | 8 | 3 | 3 | 1 | 661 | 14.43 | 14.29 | 661 | 14.43 | 14.29 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | LP=60 Note 1: 765/903Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1770 | 2235 | 2445 | 2805 | {EE323A05-6991-462E-9351-F81750DFD74D}
1224 | 1106 | {A2EED33C-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | DEL MONTE | Bank 1 | CB 2102 | PGE\ACT0 | 2016-11-23 11:12:36.3962094 -08:00 | 1822202102 | 182222102 | 12 | 3 | 3 | 2 | 492 | 18.59 | 18.4 | 492 | 18.59 | 18.4 | 554 | 20.94 | 20.73 | 554 | 20.94 | 20.73 | 560 | 21.16 | 20.95 | 560 | 21.16 | 20.95 | 598 | 22.6 | 22.37 | 598 | 22.6 | 22.37 |  |  | FALSE | FALSE | 1190 | 1331 | 1331 | 1331 | {37CEE527-5208-4A86-9A66-E1FAC36D64A0}
1225 | 1064 | {5A8ACA00-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | ANNAPOLIS | Bank 1 | CB 1101 (Non-SCADA) | PGE\C8M4 | 2017-05-08 18:04:36.2982495 -07:00 | 0428601101 | 042861101 | 8 | 3 | 3 | 2 | 115 | 2.51 | 2.48 | 91 | 1.99 | 1.97 | 149 | 3.25 | 3.22 | 119 | 2.6 | 2.57 | 137 | 2.99 | 2.96 | 110 | 2.4 | 2.38 | 172 | 3.75 | 3.71 | 137 | 2.99 | 2.96 | QA COMPLETED BY C8M4 ON 05/08/2017 |  | FALSE | TRUE | 91 | 119 | 110 | 137 | {9F4B71C0-F44E-4F69-A6EC-C510612CCC85}
1226 | 1106 | {A985082C-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | DEL MONTE | Bank 1 | CB 2103 | PGE\ACT0 | 2016-11-23 11:13:35.8945031 -08:00 | 1822202103 | 182222103 | 12 | 3 | 3 | 2 | 582 | 22 | 21.78 | 582 | 22 | 21.78 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1331 | 1331 | 1331 | {27DF12C2-6025-451F-84EA-5E3C436FBB84}
1227 | 1097 | {B91B8D7A-671D-11E5-80CA-005056A729E5} | FRESNO | CLOVIS | Bank 2 | CB 1108 | PGE\BXYD | 2017-01-24 13:22:32.3125683 -08:00 | 2540801108 | 254081108 | 8 | 3 | 3 | 1 | 584 | 12.75 | 12.62 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Note 1: 765/903Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1770 | 2235 | 2445 | 2805 | {8E14D6E1-37F1-4BA4-9750-ED6D3809741E}
1228 | 1108 | {B91B8D88-671D-11E5-80CA-005056A729E5} | FRESNO | CLOVIS | Bank 3 | CB 2109 | PGE\BXYD | 2016-12-28 08:39:38.2065247 -08:00 | 2540802109 | 254082109 | 11 | 3 | 3 | 1 | 584 | 21.85 | 21.63 | 584 | 21.85 | 21.63 | 667 | 24.95 | 24.7 | 667 | 24.95 | 24.7 | 647 | 24.21 | 23.97 | 647 | 24.21 | 23.97 | 667 | 24.95 | 24.7 | 667 | 24.95 | 24.7 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {25F31ADE-1558-4033-838A-877DA2CC56C7}
1229 | 1109 | {B59B6BEE-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | DEL MONTE | Bank 2 | CB 2104 | PGE\ACT0 | 2016-11-23 11:15:57.9806224 -08:00 | 1822202104 | 182222104 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {9AA18822-EDD3-43E6-AB7C-7613B2515AA3}
1231 | 1109 | {BC1600A3-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | DEL MONTE | Bank 2 | CB 2105 | PGE\ACT0 | 2016-11-23 11:41:23.4826525 -08:00 | 1822202105 | 182222105 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {C4A4B92D-D135-4BEF-935B-918713253EA2}
1232 | 1108 | {B91B8DA2-671D-11E5-80CA-005056A729E5} | FRESNO | CLOVIS | Bank 3 | CB 2110 | PGE\BXYD | 2017-01-24 13:31:48.6816675 -08:00 | 2540802110 | 254082110 | 11 | 3 | 3 | 1 | 540 | 20.2 | 20 | 540 | 20.2 | 20 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 598 | 22.37 | 22.15 | 598 | 22.37 | 22.15 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {7400F0A9-8475-4621-939A-86AB833B08FF}
1234 | 1110 | {C245F84F-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | DEL MONTE | Bank 9 | CB 1101 (Non-SCADA) | PGE\ACT0 | 2016-11-23 11:34:01.5434036 -08:00 | 182221101 | 182221101 | 8 | 3 | 3 | 2 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 429 | 558 | 515 | 644 | {00000000-0000-0000-0000-000000000000}
1235 | 1108 | {B91B8DB9-671D-11E5-80CA-005056A729E5} | FRESNO | CLOVIS | Bank 3 | CB 2111 | PGE\BXYD | 2016-12-28 08:41:33.0254687 -08:00 | 2540802111 | 254082111 | 11 | 3 | 3 | 1 | 540 | 20.2 | 20 | 540 | 20.2 | 20 | 686 | 25.66 | 25.4 | 686 | 25.66 | 25.4 | 598 | 22.37 | 22.15 | 598 | 22.37 | 22.15 | 700 | 26.19 | 25.93 | 700 | 26.19 | 25.93 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {2D6C7B91-7A6A-415E-9E1A-D384CA83B48B}
1238 | 1047 | {CEEBC99E-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | DOLAN ROAD | Bank 1 | CB 1104 | PGE\MTDR | 2017-07-17 09:03:04.3853577 -07:00 | 1823801104 | 182381104 | 8 | 3 | 3 | 2 | 458 | 10 | 9.9 | 458 | 10 | 9.9 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 458 | 596 | 550 | 687 | {5E750021-6EDD-4751-8F9C-F01940E2615F}
1239 | 1111 | {B91B8DD6-671D-11E5-80CA-005056A729E5} | FRESNO | COALINGA NO 1 | Bank 1 | CB 1108 | PGE\BXYD | 2017-01-24 10:52:25.7401107 -08:00 | 2521601108 | 252161108 | 8 | 3 | 3 | 1 | 435 | 9.49 | 9.4 | 413 | 9.01 | 8.92 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 733 | 842 | 842 | 842 | {70FC6827-C2F7-462C-AE2A-126916587EA6}
1244 | 1111 | {B91B8DDB-671D-11E5-80CA-005056A729E5} | FRESNO | COALINGA NO 1 | Bank 1 | CB 1109 | PGE\BXYD | 2017-01-24 10:52:57.9387171 -08:00 | 2521601109 | 252161109 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 733 | 842 | 842 | 842 | {1213B1F3-9DF9-422A-B730-F8EB84A64621}
1246 | 1112 | {CEEBC9B2-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | ERTA | Bank 2 (Non SCADA) | CB 403 (Non-SCADA) | PGE\ACT0 | 2016-09-28 10:26:26.2809049 -07:00 | 083510403 | 083510403 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 825 | 938 | 938 | 938 | {49AAF624-D468-4BAC-9F88-0C3F3AE29496}
1247 | 1112 | {CEEBC9B5-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | ERTA | Bank 2 (Non SCADA) | CB 404 (Non-SCADA) | PGE\ACT0 | 2016-09-28 10:30:13.3801798 -07:00 | 083510404 | 083510404 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 825 | 938 | 938 | 938 | {A9865F95-BDCC-4C31-BD8D-7A11189F37CD}
1248 | 1116 | {CEEBC9C1-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | FELTON | Bank 2 (Non SCADA) | CB 401 (Non-SCADA) | PGE\ACT0 | 2016-09-28 13:47:23.0538818 -07:00 | 083140401 | 083140401 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {F8EB0047-0BD5-4E00-84A3-6377972B4A74}
1249 | 1051 | {5A8ACA16-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | ARCATA | Bank 1 | CB 1105 | PGE\C8M4 | 2017-07-19 10:04:51.7064390 -07:00 | 192020122 | 192020122 | 8 | 3 | 3 | 2 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | TRUE | 1374 | 1787 | 1649 | 2000 | {E956BB9D-6A81-46E7-95D6-8F5FD67D4117}
1270 | 1060 | {C70A69CD-0E4A-11E6-95F2-D4BED91EFF1A} | HUMBOLDT | ARCATA | BANK 2 | CB 1121 | PGE\C8M4 | 2017-08-02 14:40:44.3482215 -07:00 | 1920201121 | 192021121 | 8 | 3 | 3 | 2 | 492 | 10.74 | 10.63 | 467 | 10.19 | 10.09 | 554 | 12.09 | 11.97 | 526 | 11.48 | 11.37 | 528 | 11.52 | 11.4 | 501 | 10.93 | 10.82 | 598 | 13.05 | 12.92 | 568 | 12.4 | 12.28 |  |  | FALSE | TRUE | 1374 | 1787 | 1649 | 2000 | {12B87862-C686-420D-B35B-05FB31B0A94D}
1271 | 1124 | {AD80BEF4-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PLEASANT GROVE | Bank 2 | CB 2107 | PGE\SDK6 | 2016-09-28 15:56:09.9689575 -07:00 | 1524402107 | 152442107 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {4561ED47-4550-442E-BD2B-C8C8C3A3DA38}
1272 | 1124 | {AD80BF3C-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PLEASANT GROVE | Bank 2 | CB 2108 | PGE\SDK6 | 2016-09-28 16:02:30.5786928 -07:00 | 1524402108 | 152442108 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {83C5DE95-E5DF-4778-8920-99D6AA8FB434}
1273 | 1060 | {5A8ACA77-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | ARCATA | BANK 2 | CB 1122 | PGE\C8M4 | 2017-08-02 14:41:07.6393201 -07:00 | 1920201122 | 192021122 | 8 | 3 | 3 | 2 | 492 | 10.74 | 10.63 | 467 | 10.19 | 10.09 | 554 | 12.09 | 11.97 | 526 | 11.48 | 11.37 | 560 | 12.22 | 12.1 | 532 | 11.61 | 11.49 | 598 | 13.05 | 12.92 | 568 | 12.4 | 12.28 |  |  | FALSE | TRUE | 1374 | 1787 | 1649 | 2000 | {65A6788A-F9AE-44CF-9786-73742483FEA8}
1274 | 1119 | {B91B8CE3-671D-11E5-80CA-005056A729E5} | FRESNO | CANTUA | Bank 1 | CB 1106 | PGE\BXYD | 2016-09-28 16:18:39.6104664 -07:00 | 2535901106 | 253591106 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1099 | 1429 | 1319 | 1649 | {49E7DD30-5319-4599-8EF1-C84532BF1460}
1275 | 1125 | {AD80BF5D-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PLEASANT GROVE | Bank 3 | CB 2109 | PGE\SDK6 | 2016-09-28 16:16:26.7616514 -07:00 | 1524402109 | 152442109 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {5B58946D-D9F7-47BC-A93F-EB63ABBD0A0D}
1276 | 1125 | {AD80BF97-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PLEASANT GROVE | Bank 3 | CB 2110 | PGE\SDK6 | 2016-09-28 16:19:51.0991544 -07:00 | 1524402110 | 152442110 | 12 | 3 | 3 | 1 | 978 | 36.96 | 36.59 | 978 | 36.96 | 36.59 | 1000 | 37.79 | 37.41 | 1000 | 37.79 | 37.41 | 1000 | 37.79 | 37.41 | 1000 | 37.79 | 37.41 | 1000 | 37.79 | 37.41 | 1000 | 37.79 | 37.41 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {4B707C12-2EDB-44FD-9E67-D1598C7A882D}
1278 | 1127 | {AD80BFD7-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | ROCKLIN | Bank 1 | CB 1101 | PGE\SDK6 | 2016-09-28 16:48:20.8519836 -07:00 | 1520601101 | 152061101 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 962 | {5489FA49-3952-43A3-9A65-1F5CB0DE2CD0}
1279 | 1127 | {AD80BFE0-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | ROCKLIN | Bank 1 | CB 1102 | PGE\SDK6 | 2016-12-01 15:07:00.5694960 -08:00 | 1520601102 | 152061102 | 8 | 3 | 3 | 1 | 566 | 12.35 | 12.23 | 566 | 12.35 | 12.23 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 962 | {E247EBBF-8B5D-49E6-B3DE-54825EF4E09C}
1280 | 1113 | {B91B8DE6-671D-11E5-80CA-005056A729E5} | FRESNO | COALINGA NO 1 | Bank 2 | CB 1106 | PGE\BXYD | 2017-01-24 10:54:45.4390062 -08:00 | 2521601106 | 252161106 | 8 | 3 | 3 | 1 | 435 | 9.49 | 9.4 | 413 | 9.01 | 8.92 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 481 | 625 | 577 | 702 | {DAD77F83-9BB0-476C-A6BB-3EACB4F4309E}
1281 | 1113 | {B91B8DEB-671D-11E5-80CA-005056A729E5} | FRESNO | COALINGA NO 1 | Bank 2 | CB 1107 | PGE\BXYD | 2017-01-24 10:57:11.7991444 -08:00 | 2521601107 | 252161107 | 8 | 3 | 3 | 1 | 435 | 9.49 | 9.4 | 413 | 9.01 | 8.92 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 481 | 625 | 577 | 702 | {6962C93C-8CE1-4944-84B6-74551DB6D32C}
1283 | 1129 | {AD80C001-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | ROCKLIN | Bank 2 | CB 1103 | PGE\SDK6 | 2016-09-28 17:08:13.0616242 -07:00 | 1520601103 | 152061103 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 456 | 9.95 | 9.85 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 529 | 11.54 | 11.42 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | TRUE | FALSE | 481 | 625 | 577 | 721 | {C3700541-079D-4D6B-BC07-6F6187C5FB2A}
1284 | 1129 | {AD80C00A-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | ROCKLIN | Bank 2 | CB 1104 | PGE\SDK6 | 2016-09-28 17:14:09.8217362 -07:00 | 1520601104 | 152061104 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 456 | 9.95 | 9.85 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 557 | 12.16 | 12.04 | 529 | 11.54 | 11.42 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | TRUE | FALSE | 481 | 625 | 577 | 721 | {69C998D3-2DD3-49FC-BF03-B0638DACF390}
1285 | 1128 | {5A011827-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | 18TH STREET | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\DMAL | 2017-03-17 13:37:23.0398113 -07:00 | 022390401 | 022390401 | 3 | 3 | 3 | 2 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 |  |  | FALSE | FALSE | 300 | 300 | 300 | 300 | {992498FC-AEC8-4DEE-9F22-5035043532CB}
1286 | 1128 | {5A01182A-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | 18TH STREET | Bank 1 (Non SCADA) | CB 402 (Non-SCADA) | PGE\DMAL | 2017-03-14 17:33:37.8542061 -07:00 | 022390402 | 022390402 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 |  |  | FALSE | FALSE | 528 | 687 | 634 | 792 | {C17F0349-604C-4376-B8A5-011EFE939D53}
1288 | 1138 | {9402A8FB-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SILVER | Bank 401 (Non SCADA) | CB 401 (Non-SCADA) | PGE\DMAL | 2017-05-12 14:39:42.8948796 -07:00 | 022670401 | 022670401 | 3 | 3 | 3 | 2 | 319 | 2.3 | 2.28 | 319 | 2.3 | 2.28 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 383 | 2.76 | 2.73 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 319 | 400 | 383 | 400 | {9968D0BE-9BFC-4CCF-A0D0-BAF84CC12B7A}
1291 | 1140 | {B91B8E55-671D-11E5-80CA-005056A729E5} | FRESNO | CORCORAN | Bank 3 | CB 1112 (Non-SCADA) | PGE\BXYD | 2017-01-24 10:31:51.5069990 -08:00 | 2521701112 | 252171112 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {2A1E295E-FD99-4DBA-B528-18C0DF5BC465}
1292 | 1140 | {B91B8E5B-671D-11E5-80CA-005056A729E5} | FRESNO | CORCORAN | Bank 3 | CB 1116 (Non-SCADA) | PGE\BXYD | 2016-09-29 08:30:17.0944166 -07:00 | 2521701116 | 252171116 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {6098229F-0B61-4FD1-B3AA-B32BEABC3AB4}
1293 | 1140 | {B91B8E61-671D-11E5-80CA-005056A729E5} | FRESNO | CORCORAN | Bank 3 | CB 1118 | PGE\BXYD | 2016-09-29 08:33:03.5331202 -07:00 | 2521701118 | 252171118 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {B9EBD04A-1C6C-49DB-B336-B06C76EEDDB7}
1294 | 1141 | {B91B8E6C-671D-11E5-80CA-005056A729E5} | FRESNO | CORCORAN | Bank 4 | CB 1104 | PGE\BXYD | 2016-09-29 08:53:00.6791433 -07:00 | 2521701104 | 252171104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F8A5A676-58D5-43B2-B1FC-A1F19B936B16}
1295 | 1141 | {BF18FD6A-671D-11E5-80CA-005056A729E5} | FRESNO | CORCORAN | Bank 4 | CB 1106 (Non-SCADA) | PGE\BXYD | 2017-01-24 10:37:35.1928021 -08:00 | 2521701106 | 252171106 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {FD6C41A7-6E7E-4DD8-98B4-FB1FA7A52B85}
1296 | 1141 | {BF18FD76-671D-11E5-80CA-005056A729E5} | FRESNO | CORCORAN | Bank 4 | CB 1108 (Non-SCADA) | PGE\BXYD | 2016-09-29 09:19:28.7714514 -07:00 | 2521701108 | 252171108 | 8 | 3 | 3 | 1 | 440 | 9.6 | 9.5 | 440 | 9.6 | 9.5 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 528 | 11.52 | 11.4 | 528 | 11.52 | 11.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note 1: Phase relay / 1.2 or phase relay - 50 amps, whichever is less. See Protection Bulletin 6-3, p.19. Note 2: Capability x .95 to account for phase unbalance if limiting factor is OH conductor, switches, disconnects, CT's, or VCB'S. See Engr. Std. Drw. 050864. Note 3: UG cable ratings were calculated with the actual daily load factor. See Engr, Std. Drw. 050166. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {C11D7BA9-5E29-4E6F-A585-31FFDF7A3316}
1297 | 1142 | {BF18FD88-671D-11E5-80CA-005056A729E5} | FRESNO | DEVILS DEN | Bank 1 | CB 1101 (Non-SCADA) | PGE\JCS9 | 2016-12-15 15:28:58.2280532 -08:00 | 2534501101 | 253451101 | 8 | 3 | 3 | 1 | 183 | 3.99 | 3.95 | 183 | 3.99 | 3.95 | 211 | 4.6 | 4.55 | 211 | 4.6 | 4.55 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | SEL 251 Phase: MTT 300a, Tap 5, TD 2.0, IT 2400a. Ground: MTT 180a, Tap 3.0, IT 2400a. |  | FALSE | FALSE | 240 | 312 | 288 | 360 | {C9FB5C49-EDD9-4AE1-B4DF-9248C96A5480}
1298 | 1142 | {BF18FD8E-671D-11E5-80CA-005056A729E5} | FRESNO | DEVILS DEN | Bank 1 | CB 1102 (Non-SCADA) | PGE\JCS9 | 2016-11-30 14:55:10.7819667 -08:00 | 2534501102 | 253451102 | 8 | 3 | 3 | 1 | 210 | 4.58 | 4.53 | 210 | 4.58 | 4.53 | 210 | 4.58 | 4.53 | 210 | 4.58 | 4.53 | 210 | 4.58 | 4.53 | 210 | 4.58 | 4.53 | 210 | 4.58 | 4.53 | 210 | 4.58 | 4.53 | SEL 251 Phase: MTT 252a, Tap 4.2, TD 2.0, IT 2400a. Ground: MTT 180a, Tap 3.0, TD 3.0, IT 2502a. |  | FALSE | FALSE | 240 | 312 | 288 | 360 | {63D58FF1-6566-4E62-A7BC-FC8A0F4FDD74}
1299 | 1144 | {BF18FD97-671D-11E5-80CA-005056A729E5} | FRESNO | DINUBA | Bank 1 | CB 1102 | PGE\KRBk | 2016-12-13 10:16:00.1700226 -08:00 | 2540901102 | 254091102 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {0214654E-CFE3-4A6A-9ECA-45C1A554D20D}
1300 | 1144 | {BF18FD9C-671D-11E5-80CA-005056A729E5} | FRESNO | DINUBA | Bank 1 | CB 1104 | PGE\BXYD | 2016-09-29 10:02:27.0115549 -07:00 | 2540901104 | 254091104 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {50A0DB5E-8BFC-4146-AEFB-2B2A7ED673F7}
1301 | 1145 | {BF18FDBE-671D-11E5-80CA-005056A729E5} | FRESNO | DINUBA | Bank 2 | CB 1105 | PGE\BXYD | 2016-09-29 10:41:39.2531013 -07:00 | 2540901105 | 254091105 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {FD3367D3-3077-4612-A2F5-370002A69003}
1302 | 1145 | {BF18FDD5-671D-11E5-80CA-005056A729E5} | FRESNO | DINUBA | Bank 2 | CB 1106 | PGE\BXYD | 2016-09-29 10:42:49.0219659 -07:00 | 2540901106 | 254091106 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {06E012D4-10E6-43BE-A60E-B4432475C7B0}
1303 | 1146 | {BF18FDE3-671D-11E5-80CA-005056A729E5} | FRESNO | DUNLAP | Bank 1 | CB 1102 (Non-SCADA) | PGE\BXYD | 2016-09-29 10:59:11.3946940 -07:00 | 2540601102 | 254061102 | 8 | 3 | 3 | 1 | 154 | 3.36 | 3.33 | 154 | 3.36 | 3.33 | 173 | 3.78 | 3.74 | 173 | 3.78 | 3.74 | 206 | 4.5 | 4.46 | 206 | 4.5 | 4.46 | 228 | 4.98 | 4.93 | 228 | 4.98 | 4.93 |  |  | FALSE | FALSE | 171 | 223 | 206 | 257 | {65DBFC84-B1BE-4394-BA4A-429EED361CD1}
1304 | 1146 | {BF18FDEF-671D-11E5-80CA-005056A729E5} | FRESNO | DUNLAP | Bank 1 | CB 1103 (Non-SCADA) | PGE\BXYD | 2016-11-29 08:57:35.6009911 -08:00 | 2540601103 | 254061103 | 8 | 3 | 3 | 1 | 171 | 3.73 | 3.69 | 171 | 3.73 | 3.69 | 223 | 4.87 | 4.82 | 223 | 4.87 | 4.82 | 206 | 4.5 | 4.46 | 206 | 4.5 | 4.46 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 |  |  | FALSE | FALSE | 171 | 223 | 206 | 257 | {3ACA4F6D-CDFC-4F25-BD4E-2FC9F8145B68}
1306 | 1147 | {BF18FE01-671D-11E5-80CA-005056A729E5} | FRESNO | FIGARDEN | Bank 1 | CB 2102 | PGE\BXYD | 2017-01-24 10:02:44.6858015 -08:00 | 2545502102 | 254552102 | 12 | 3 | 3 | 1 | 573 | 21.66 | 21.44 | 573 | 21.66 | 21.44 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 634 | 23.96 | 23.72 | 634 | 23.96 | 23.72 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1984 | 2579 | 2200 | 2640 | {6983F9A2-BAAD-4660-9F30-457493CEDA3A}
1307 | 1147 | {BF18FE2D-671D-11E5-80CA-005056A729E5} | FRESNO | FIGARDEN | Bank 1 | CB 2103 | PGE\BXYD | 2016-09-29 11:36:43.0901389 -07:00 | 2545502103 | 254552103 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {16D0111C-FCA8-4C56-9595-6F441D695E0D}
1308 | 1147 | {BF18FE44-671D-11E5-80CA-005056A729E5} | FRESNO | FIGARDEN | Bank 1 | CB 2104 | PGE\BXYD | 2016-11-29 11:41:25.1476053 -08:00 | 2545502104 | 254552104 | 12 | 3 | 3 | 1 | 530 | 20.03 | 19.83 | 530 | 20.03 | 19.83 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {C013277D-2DA5-458D-871D-EB4FA91BBF4B}
1309 | 1147 | {BF18FE4F-671D-11E5-80CA-005056A729E5} | FRESNO | FIGARDEN | Bank 1 | CB 2105 | PGE\BXYD | 2017-01-24 10:05:29.1108555 -08:00 | 2545502105 | 254552105 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 |  |  | FALSE | FALSE | 1984 | 2579 | 2200 | 2640 | {546B7CCA-A526-41B8-802D-1360789D3BDA}
1310 | 1122 | {3D6E31A8-FDD1-11E5-9D37-D4BED91EFF1A} | SAN JOSE | MILPITAS | Bank 1 | CB 1104 (Non-SCADA) | PGE\INM2 | 2017-01-25 07:38:21.0333660 -08:00 | 0828301104 | 082831104 | 8 | 3 | 3 | 2 | 916 | 19.99 | 19.79 | 916 | 19.99 | 19.79 | 1000 | 21.82 | 21.6 | 1000 | 21.82 | 21.6 | 1000 | 21.82 | 21.6 | 1000 | 21.82 | 21.6 | 1000 | 21.82 | 21.6 | 1000 | 21.82 | 21.6 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {81063479-3D94-4154-BEB6-7B7905A50A93}
1312 | 1149 | {BF18FE72-671D-11E5-80CA-005056A729E5} | FRESNO | FIGARDEN | Bank 2 | CB 2107 | PGE\BXYD | 2016-09-29 13:29:45.4482384 -07:00 | 2545502107 | 254552107 | 11 | 3 | 3 | 1 | 503 | 18.82 | 18.63 | 503 | 18.82 | 18.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 2004 | 2606 | 2405 | 3007 | {3A597E7F-E3F1-4A38-BF54-7D1C5A924FD6}
1313 | 1149 | {BF18FE86-671D-11E5-80CA-005056A729E5} | FRESNO | FIGARDEN | Bank 2 | CB 2108 | PGE\BXYD | 2016-09-29 13:35:29.4621823 -07:00 | 2545502108 | 254552108 | 11 | 3 | 3 | 1 | 503 | 18.82 | 18.63 | 503 | 18.82 | 18.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 2004 | 2606 | 2405 | 3007 | {C3366CA5-78AC-455B-8D3C-97F1643465B0}
1315 | 1149 | {BF18FE9D-671D-11E5-80CA-005056A729E5} | FRESNO | FIGARDEN | Bank 2 | CB 2109 | PGE\BXYD | 2017-01-24 10:10:06.5586340 -08:00 | 2545502109 | 254552109 | 11 | 3 | 3 | 1 | 530 | 19.83 | 19.63 | 530 | 19.83 | 19.63 | 600 | 22.45 | 22.23 | 570 | 21.33 | 21.12 | 600 | 22.45 | 22.23 | 570 | 21.33 | 21.12 | 600 | 22.45 | 22.23 | 570 | 21.33 | 21.12 |  |  | FALSE | FALSE | 2004 | 2606 | 2200 | 2640 | {2D9C6139-C906-4354-A570-875A292FA94D}
1318 | 1149 | {BF18FEAB-671D-11E5-80CA-005056A729E5} | FRESNO | FIGARDEN | Bank 2 | CB 2110 | PGE\BXYD | 2016-09-29 13:45:53.8700727 -07:00 | 2545502110 | 254552110 | 11 | 3 | 3 | 1 | 477 | 17.85 | 17.67 | 477 | 17.85 | 17.67 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 528 | 19.75 | 19.55 | 528 | 19.75 | 19.55 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 2004 | 2606 | 2405 | 3007 | {97A99F76-9169-48DC-B30A-B880E6DF6380}
1319 | 1158 | {BF18FED1-671D-11E5-80CA-005056A729E5} | FRESNO | FIGARDEN | Bank 3 | CB 2111 | PGE\BXYD | 2016-11-28 16:20:32.5913557 -08:00 | 2545502111 | 254552111 | 11 | 3 | 3 | 1 | 573 | 21.44 | 21.23 | 573 | 21.44 | 21.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 2004 | 2606 | 2405 | 3007 | {41FEAF38-CC06-4A13-BFAA-E55062CA3A63}
1320 | 1158 | {BF18FEE8-671D-11E5-80CA-005056A729E5} | FRESNO | FIGARDEN | Bank 3 | CB 2112 | PGE\BXYD | 2017-01-24 10:12:48.4564718 -08:00 | 2545502112 | 254552112 | 11 | 3 | 3 | 1 | 573 | 21.44 | 21.23 | 573 | 21.44 | 21.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 2004 | 2606 | 2405 | 3007 | {95630AAF-BD54-4551-AEE4-ACE415A21564}
1322 | 1158 | {BF18FF0F-671D-11E5-80CA-005056A729E5} | FRESNO | FIGARDEN | Bank 3 | CB 2113 | PGE\BXYD | 2017-01-24 10:14:59.2321101 -08:00 | 2545502113 | 254552113 | 11 | 3 | 3 | 1 | 440 | 16.46 | 16.3 | 440 | 16.46 | 16.3 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 528 | 19.75 | 19.55 | 528 | 19.75 | 19.55 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 2004 | 2606 | 2405 | 3007 | {CDF5C705-FD09-43A2-AF30-7A4038E6E78A}
1324 | 1160 | {C5114033-671D-11E5-80CA-005056A729E5} | FRESNO | GUERNSEY | Bank 1 | CB 1102 | PGE\BXYD | 2016-09-29 14:32:33.2659586 -07:00 | 2526601102 | 252661102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {BAC08179-4011-4B3F-BCB3-56633C6055DB}
1325 | 1160 | {C5114038-671D-11E5-80CA-005056A729E5} | FRESNO | GUERNSEY | Bank 1 | CB 1104 | PGE\BXYD | 2016-09-29 14:36:01.8876662 -07:00 | 2526601104 | 252661104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {D21172D2-E683-4EDE-8A4B-183A0EC7E8AE}
1326 | 1160 | {C511403D-671D-11E5-80CA-005056A729E5} | FRESNO | GUERNSEY | Bank 1 | CB 1106 | PGE\BXYD | 2017-01-24 09:22:32.9727419 -08:00 | 2526601106 | 252661106 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {9AD592AC-D603-494E-8DC4-891CF07DF6E9}
1327 | 1160 | {C511404B-671D-11E5-80CA-005056A729E5} | FRESNO | GUERNSEY | Bank 1 | CB 1108 | PGE\BXYD | 2017-01-24 09:23:23.2518642 -08:00 | 2526601108 | 252661108 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {61878932-CAAA-479C-B34E-6943570F1C9E}
1330 | 1159 | {E81C7D8C-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MILPITAS | Bank 2 | CB 1106 | PGE\JLDe | 2016-09-29 14:56:22.9804137 -07:00 | 0828301106 | 082831106 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {71A5ADBB-14BE-45A0-9703-851FC0D3F5DA}
1331 | 1162 | {C5114056-671D-11E5-80CA-005056A729E5} | FRESNO | GUERNSEY | Bank 2 | CB 1101 | PGE\BXYD | 2017-01-24 09:25:23.2166332 -08:00 | 2526601101 | 252661101 | 8 | 4 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {20A9EE8E-3AC7-45DA-B3A2-AD9891A2BE5C}
1332 | 1162 | {C5114061-671D-11E5-80CA-005056A729E5} | FRESNO | GUERNSEY | Bank 2 | CB 1103 | PGE\BXYD | 2016-09-29 14:58:50.2355177 -07:00 | 2526601103 | 252661103 | 8 | 3 | 3 | 1 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {8DF0A326-9C13-44A2-B126-A7156B18D67F}
1333 | 1164 | {C511406F-671D-11E5-80CA-005056A729E5} | FRESNO | HARDWICK | Bank 1 | CB 1101 (Non-SCADA) | PGE\BXYD | 2016-09-29 16:34:20.2536888 -07:00 | 2537101101 | 253711101 | 8 | 3 | 3 | 1 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 |  |  | FALSE | FALSE | 702 | 702 | 702 | 702 | {BB4ECC2D-57E8-4321-B6D2-88A287F5DE18}
1334 | 1164 | {C5114075-671D-11E5-80CA-005056A729E5} | FRESNO | HARDWICK | Bank 1 | CB 1102 (Non-SCADA) | PGE\BXYD | 2017-01-24 09:16:41.9392917 -08:00 | 2537101102 | 253711102 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 701 | 701 | 701 | 701 | {502719DF-9C58-4409-A0B5-E584528C2D24}
1342 | 1165 | {473E9CE9-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | ARBUCKLE | Bank 1 | CB 1101 | PGE\SDK6 | 2016-09-29 16:22:46.6946754 -07:00 | 0620801101 | 062081101 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 |  |  | TRUE | FALSE | 641 | 722 | 722 | 722 | {BDBA0B0C-2D88-4DE2-9D7F-7883CCBD8AC9}
1343 | 1165 | {473E9CF9-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | ARBUCKLE | Bank 1 | CB 1102 | PGE\SDK6 | 2016-09-29 16:22:37.0414674 -07:00 | 0620801102 | 062081102 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 |  |  | TRUE | FALSE | 641 | 722 | 722 | 722 | {A0C53289-CDF0-45BA-BF76-97A92A43F04C}
1344 | 1165 | {473E9D17-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | ARBUCKLE | Bank 1 | CB 1103 | PGE\SDK6 | 2016-09-29 16:25:31.5985512 -07:00 | 0620801103 | 062081103 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | Breaker is presently idle - no outlet attached in field. |  | TRUE | FALSE | 641 | 722 | 722 | 722 | {1D531C11-4BDD-4C49-8176-7C1F3C597DF5}
1345 | 1166 | {473E9D2A-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | ARBUCKLE | Bank 2 | CB 1104 | PGE\SDK6 | 2016-09-29 16:38:50.2119633 -07:00 | 0620801104 | 062081104 | 8 | 3 | 3 | 1 | 572 | 12.48 | 12.36 | 572 | 12.48 | 12.36 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 | Noe: Use Group 2 settings (480A Phase MTT) for recloser bypass scenarios, if loading permits. |  | FALSE | FALSE | 572 | 722 | 687 | 722 | {BB7D5D0F-1F6E-4063-AAEF-601D1BE63FBE}
1346 | 1167 | {C511409A-671D-11E5-80CA-005056A729E5} | FRESNO | HENRIETTA | Bank 5 | CB 1106 | PGE\BXYD | 2017-01-24 09:11:27.0356731 -08:00 | 2526801106 | 252681106 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 489 | 10.67 | 10.56 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {6B1EA48B-4C8C-4B1F-B3CA-4067EBC00D85}
1347 | 1167 | {C511409F-671D-11E5-80CA-005056A729E5} | FRESNO | HENRIETTA | Bank 5 | CB 1110 | PGE\BXYD | 2017-01-24 09:11:58.9066774 -08:00 | 2526801110 | 252681110 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 489 | 10.67 | 10.56 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {BD05CF76-216E-4289-A6E0-C0A6A2B192A9}
1349 | 1170 | {4D8916BB-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | CORTINA | Bank 3 | CB 1101 | PGE\SDK6 | 2016-09-29 16:53:08.8133189 -07:00 | 0631201101 | 063121101 | 8 | 3 | 3 | 1 | 320 | 6.98 | 6.91 | 320 | 6.98 | 6.91 | 416 | 9.08 | 8.99 | 416 | 9.08 | 8.99 | 384 | 8.38 | 8.3 | 384 | 8.38 | 8.3 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 |  |  | FALSE | FALSE | 320 | 416 | 384 | 481 | {38B5395E-3137-4F5F-BE34-3CED5D649057}
1350 | 1171 | {C51140E3-671D-11E5-80CA-005056A729E5} | FRESNO | JACOBS CORNER | Bank 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\BXYD | 2016-09-30 08:03:51.0885197 -07:00 | 2547701101 | 254771101 | 8 | 3 | 3 | 1 | 572 | 12.48 | 12.36 | 572 | 12.48 | 12.36 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 687 | 14.99 | 14.84 | 687 | 14.99 | 14.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 |  |  | FALSE | FALSE | 572 | 744 | 687 | 842 | {7D15AB38-C674-4F81-A991-CE107B060EFA}
1351 | 1172 | {C51140E9-671D-11E5-80CA-005056A729E5} | FRESNO | JACOBS CORNER | Bank 2 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\BXYD | 2017-01-24 08:23:17.0391476 -08:00 | 2547701102 | 254771102 | 8 | 3 | 3 | 1 | 650 | 14.19 | 14.05 | 617 | 13.47 | 13.34 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 |  |  | FALSE | FALSE | 733 | 842 | 842 | 842 | {B7C8C4D3-ED28-4169-BFDC-F34399A0973C}
1352 | 1175 | {C511411F-671D-11E5-80CA-005056A729E5} | FRESNO | KEARNEY | Bank 3 | CB 1113 | PGE\BXYD | 2016-09-30 08:44:33.2338091 -07:00 | 2527001113 | 252701113 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {BA815BC1-8E52-45B9-9689-ADA32AE0C66E}
1353 | 1175 | {C5114124-671D-11E5-80CA-005056A729E5} | FRESNO | KEARNEY | Bank 3 | CB 1114 | PGE\BXYD | 2016-09-30 08:47:12.2826677 -07:00 | 2527001114 | 252701114 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {25F31282-47D5-4470-9561-0B76983F6E1B}
1355 | 1176 | {C511413E-671D-11E5-80CA-005056A729E5} | FRESNO | KERMAN | Bank 1 | CB 1104 (Non-SCADA) | PGE\BXYD | 2016-09-30 09:13:52.0435510 -07:00 | 2527101104 | 252711104 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {DE1052BD-4B1D-4B79-9C06-E328DB4F0262}
1356 | 1176 | {C5114144-671D-11E5-80CA-005056A729E5} | FRESNO | KERMAN | Bank 1 | CB 1106 | PGE\BXYD | 2017-01-23 17:09:38.0615713 -08:00 | 2527101106 | 252711106 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {B6B0F604-D8F8-4B67-BA69-55C047CD8E7B}
1358 | 1176 | {C5114152-671D-11E5-80CA-005056A729E5} | FRESNO | KERMAN | Bank 1 | CB 1108 (Non-SCADA) | PGE\BXYD | 2016-09-30 09:34:02.8378087 -07:00 | 2527101108 | 252711108 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F0026115-BFBD-472C-8E9A-AAEB5514E745}
1360 | 1177 | {C511415E-671D-11E5-80CA-005056A729E5} | FRESNO | KERMAN | Bank 2 | CB 1101 | PGE\BXYD | 2016-11-29 09:08:42.2400660 -08:00 | 2527101101 | 252711101 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {1080557A-441B-44F2-B861-40D8443AFB47}
1361 | 1177 | {C5114172-671D-11E5-80CA-005056A729E5} | FRESNO | KERMAN | Bank 2 | CB 1102 | PGE\BXYD | 2017-01-20 11:52:58.5154545 -08:00 | 2527101102 | 252711102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {428F4F50-D83B-4220-BD5F-226203CE8C0F}
1362 | 1177 | {C511417A-671D-11E5-80CA-005056A729E5} | FRESNO | KERMAN | Bank 2 | CB 1103 | PGE\BXYD | 2016-09-30 09:52:44.9420934 -07:00 | 2527101103 | 252711103 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {70954E73-C5B6-41D9-9758-929E01256205}
1363 | 1179 | {C5114197-671D-11E5-80CA-005056A729E5} | FRESNO | KETTLEMAN HILLS | Bank 1 | CB 1101 (Non-SCADA) | PGE\BXYD | 2016-09-30 10:00:16.3129619 -07:00 | 2527301101 | 252731101 | 8 | 3 | 3 | 1 | 171 | 3.73 | 3.69 | 171 | 3.73 | 3.69 | 223 | 4.87 | 4.82 | 223 | 4.87 | 4.82 | 206 | 4.5 | 4.46 | 206 | 4.5 | 4.46 | 257 | 5.61 | 5.55 | 257 | 5.61 | 5.55 |  |  | FALSE | FALSE | 171 | 223 | 206 | 257 | {41DD9F38-554A-4366-A185-0A0A5165AC9C}
1364 | 1179 | {C51141A0-671D-11E5-80CA-005056A729E5} | FRESNO | KETTLEMAN HILLS | Bank 1 | CB 2104 (Non-SCADA) | PGE\BXYD | 2017-01-23 17:07:38.2980682 -08:00 | 2527302104 | 252732104 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 |  |  | FALSE | FALSE | 512 | 600 | 600 | 600 | {A15C2A1E-4361-461A-927C-FA9561D1D819}
1365 | 1180 | {C51141B5-671D-11E5-80CA-005056A729E5} | FRESNO | KINGSBURG | Bank 1 | CB 1102 | PGE\BXYD | 2017-01-23 16:49:44.7946243 -08:00 | 2522401102 | 252241102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F4ADD099-DEAE-46BA-9A28-310C132D9AF0}
1367 | 1180 | {C51141C0-671D-11E5-80CA-005056A729E5} | FRESNO | KINGSBURG | Bank 1 | CB 1108 | PGE\BXYD | 2017-01-23 16:50:30.6751066 -08:00 | 2522401108 | 252241108 | 8 | 3 | 3 | 1 | 540 | 11.78 | 11.66 | 540 | 11.78 | 11.66 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 598 | 13.05 | 12.92 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {E3002A0E-A95F-4EEF-AAAC-1ED71BA2A90E}
1370 | 1180 | {C51141CE-671D-11E5-80CA-005056A729E5} | FRESNO | KINGSBURG | Bank 1 | CB 1110 | PGE\BXYD | 2016-09-30 10:50:33.1363976 -07:00 | 2522401110 | 252241110 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {BBCB5475-2A52-4FDD-99F2-4479EADA4E75}
1373 | 1180 | {C51141D6-671D-11E5-80CA-005056A729E5} | FRESNO | KINGSBURG | Bank 1 | CB 1116 | PGE\BXYD | 2016-09-30 10:59:10.4721596 -07:00 | 2522401116 | 252241116 | 8 | 3 | 3 | 1 | 540 | 11.78 | 11.66 | 540 | 11.78 | 11.66 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {64ACA5B2-B61E-4741-9A3E-63C2F9EAAC67}
1376 | 1181 | {8EC75DE8-2762-11E6-B38D-D4BED91EFF1A} | FRESNO | KINGSBURG | Bank 3 | CB 1111 | PGE\BXYD | 2017-01-23 16:59:12.7859470 -08:00 | 2522401111 | 252241111 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {26D6BC4F-E0B7-4AFF-8417-1028707DD4C6}
1377 | 1181 | {CB10858F-671D-11E5-80CA-005056A729E5} | FRESNO | KINGSBURG | Bank 3 | CB 1112 | PGE\BXYD | 2016-09-30 11:32:39.3028220 -07:00 | 2522401112 | 252241112 | 8 | 3 | 3 | 1 | 636 | 13.88 | 13.74 | 636 | 13.88 | 13.74 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {266060A6-E1EF-4DEE-96AB-FF91901C693E}
1380 | 1181 | {CB108597-671D-11E5-80CA-005056A729E5} | FRESNO | KINGSBURG | Bank 3 | CB 1113 | PGE\BXYD | 2016-09-30 11:35:50.6195370 -07:00 | 2522401113 | 252241113 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {51B858B2-93CC-47F0-98BE-BE174CC5EE1A}
1381 | 1181 | {CB10859C-671D-11E5-80CA-005056A729E5} | FRESNO | KINGSBURG | Bank 3 | CB 1114 | PGE\BXYD | 2016-09-30 11:51:40.7780169 -07:00 | 2522401114 | 252241114 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F748F6F6-4A8B-4C48-B6A3-FCC00DFDC704}
1384 | 1182 | {CB1085C5-671D-11E5-80CA-005056A729E5} | FRESNO | LEMOORE | Bank 1 | CB 1101 | PGE\BXYD | 2016-09-30 11:48:55.4671035 -07:00 | 2536001101 | 253601101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9B1A826D-82E2-4C6A-AD62-3059238EF905}
1385 | 1182 | {CB1085D6-671D-11E5-80CA-005056A729E5} | FRESNO | LEMOORE | Bank 1 | CB 1103 | PGE\BXYD | 2016-09-30 11:50:50.6806893 -07:00 | 2536001103 | 253601103 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {C65B79F3-5015-4652-955F-E8975628DAAC}
1386 | 1184 | {CB1085E4-671D-11E5-80CA-005056A729E5} | FRESNO | LEMOORE | Bank 2 | CB 1102 | PGE\BXYD | 2016-09-30 12:00:12.7287713 -07:00 | 2536001102 | 253601102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {22C219B3-1684-4C02-A668-94B3D0839A67}
1388 | 1184 | {CB1085E9-671D-11E5-80CA-005056A729E5} | FRESNO | LEMOORE | Bank 2 | CB 1104 | PGE\BXYD | 2016-09-30 12:06:24.3834638 -07:00 | 2536001104 | 253601104 | 8 | 3 | 3 | 1 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {79ECFCB6-0DA4-4BFC-BF90-9EE9C2E0D63A}
1389 | 1184 | {CB1085F1-671D-11E5-80CA-005056A729E5} | FRESNO | LEMOORE | Bank 2 | CB 1105 | PGE\BXYD | 2017-01-23 16:26:22.3744552 -08:00 | 2536001105 | 253601105 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {0ADD6EEE-79A2-4152-8704-48F64584D0F7}
1392 | 1186 | {CB1085FF-671D-11E5-80CA-005056A729E5} | FRESNO | MALAGA | Bank 1 | CB 1109 | PGE\BXYD | 2017-01-23 15:18:44.8456273 -08:00 | 2542501109 | 254251109 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {DCE4E4EE-6627-4761-A766-76D423C2D859}
1393 | 1186 | {CB108610-671D-11E5-80CA-005056A729E5} | FRESNO | MALAGA | Bank 1 | CB 1110 | PGE\BXYD | 2017-01-23 15:21:17.4321616 -08:00 | 2542501110 | 254251110 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F0740AC1-666C-4B5E-BD51-BB0A6732913B}
1394 | 1186 | {CB10861B-671D-11E5-80CA-005056A729E5} | FRESNO | MALAGA | Bank 1 | CB 1111 | PGE\BXYD | 2017-01-23 15:22:48.5223133 -08:00 | 2542501111 | 254251111 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {5E0324B5-AC81-4700-9947-6FB1094A82B8}
1396 | 1187 | {CB108626-671D-11E5-80CA-005056A729E5} | FRESNO | MALAGA | Bank 2 | CB 1105 | PGE\ATO3 | 2017-04-12 10:15:06.7251168 -07:00 | 2542501105 | 254251105 | 8 | 3 | 3 | 1 | 140 | 3.06 | 3.03 | 140 | 3.06 | 3.03 | 140 | 3.06 | 3.03 | 140 | 3.06 | 3.03 | 140 | 3.06 | 3.03 | 140 | 3.06 | 3.03 | 140 | 3.06 | 3.03 | 140 | 3.06 | 3.03 | Malaga 1105 is PPG Special Facility Alternate Feed. (115KV cust sub is the normal feed). 271A Reserved Capacity on this feeder for PPG Industries. |  | FALSE | FALSE | 1200 | 1200 | 1200 | 1200 | {64C70DD0-8818-41D0-BB38-6AB6ED8F1140}
1397 | 1187 | {CB10862B-671D-11E5-80CA-005056A729E5} | FRESNO | MALAGA | Bank 2 | CB 1106 | PGE\BXYD | 2017-01-23 15:37:43.1995183 -08:00 | 2542501106 | 254251106 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 633 | 13.81 | 13.67 | 633 | 13.81 | 13.67 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 633 | 13.81 | 13.67 | 633 | 13.81 | 13.67 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {6056472E-87FE-4857-9B68-93C0FE834F2B}
1398 | 1187 | {CB108633-671D-11E5-80CA-005056A729E5} | FRESNO | MALAGA | Bank 2 | CB 1107 | PGE\BXYD | 2017-01-23 15:43:29.3701753 -08:00 | 2542501107 | 254251107 | 8 | 3 | 3 | 1 | 495 | 10.8 | 10.69 | 470 | 10.26 | 10.16 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 598 | 13.05 | 12.92 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {3312E751-F4F6-4FD0-9E44-CCB6F6F42826}
1399 | 1187 | {CB108638-671D-11E5-80CA-005056A729E5} | FRESNO | MALAGA | Bank 2 | CB 1108 | PGE\BXYD | 2017-01-23 15:48:05.4330841 -08:00 | 2542501108 | 254251108 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 598 | 13.05 | 12.92 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {065F1273-50F3-40E5-A01A-B05BC699EB68}
1402 | 1188 | {CB108646-671D-11E5-80CA-005056A729E5} | FRESNO | MALAGA | Bank 3 | CB 1101 | PGE\BXYD | 2017-01-23 16:03:26.2095910 -08:00 | 2542501101 | 254251101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2640 | 2200 | 2640 | {A8A9E164-4423-4AE0-A967-97E78AA78F7A}
1403 | 1188 | {CB108654-671D-11E5-80CA-005056A729E5} | FRESNO | MALAGA | Bank 3 | CB 1102 | PGE\BXYD | 2017-01-23 16:05:15.1776865 -08:00 | 2542501102 | 254251102 | 8 | 3 | 3 | 1 | 540 | 11.78 | 11.66 | 540 | 11.78 | 11.66 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 598 | 13.05 | 12.92 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2640 | 2200 | 2640 | {CE1CCFD1-2DCF-4F22-A39D-F671724ACED8}
1404 | 1188 | {CB10865C-671D-11E5-80CA-005056A729E5} | FRESNO | MALAGA | Bank 3 | CB 1103 | PGE\BXYD | 2017-01-23 16:07:33.4899463 -08:00 | 2542501103 | 254251103 | 8 | 3 | 3 | 1 | 573 | 12.51 | 12.38 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2640 | 2200 | 2640 | {0933C854-74D4-479C-85AE-284EBB26B0DF}
1405 | 1188 | {CB108667-671D-11E5-80CA-005056A729E5} | FRESNO | MALAGA | Bank 3 | CB 1104 | PGE\BXYD | 2017-01-23 16:08:42.7084774 -08:00 | 2542501104 | 254251104 | 8 | 3 | 3 | 1 | 566 | 12.35 | 12.23 | 566 | 12.35 | 12.23 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2640 | 2200 | 2640 | {71A3861E-8087-4EC7-A2CC-0902188DFE71}
1406 | 1189 | {CB108681-671D-11E5-80CA-005056A729E5} | FRESNO | MANCHESTER | Bank 1 | CB 1101 | PGE\BXYD | 2017-01-23 14:15:57.3279732 -08:00 | 2539201101 | 253921101 | 8 | 3 | 3 | 1 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B846C296-4DAF-4528-BDE1-794EFAD7CBBA}
1410 | 1189 | {CB108689-671D-11E5-80CA-005056A729E5} | FRESNO | MANCHESTER | Bank 1 | CB 1103 | PGE\BXYD | 2016-10-03 08:31:22.1282297 -07:00 | 2539201103 | 253921103 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {EA8D5432-86FE-4911-BFA6-3ACF4D8B33E1}
1411 | 1189 | {CB10868E-671D-11E5-80CA-005056A729E5} | FRESNO | MANCHESTER | Bank 1 | CB 1104 | PGE\BXYD | 2017-01-23 14:18:34.1899587 -08:00 | 2539201104 | 253921104 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {E4D7E5BD-9D16-4C1B-8864-B5658D6070ED}
1413 | 1189 | {CB108693-671D-11E5-80CA-005056A729E5} | FRESNO | MANCHESTER | Bank 1 | CB 1107 | PGE\BXYD | 2017-01-23 14:21:35.4233958 -08:00 | 2539201107 | 253921107 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {5D5B62F4-C7E8-463D-9C29-2A3A6A2B757A}
1416 | 1192 | {CB10869E-671D-11E5-80CA-005056A729E5} | FRESNO | MANCHESTER | Bank 2 | CB 1102 (Non-SCADA) | PGE\BXYD | 2017-01-23 14:56:49.5999346 -08:00 | 2539201102 | 253921102 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2640 | 2200 | 2640 | {7A5F9DB9-B881-46D3-A609-0F1C219CC3C7}
1418 | 1192 | {CB1086A1-671D-11E5-80CA-005056A729E5} | FRESNO | MANCHESTER | Bank 2 | CB 1105 | PGE\BXYD | 2016-11-29 09:20:50.4438292 -08:00 | 2539201105 | 253921105 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {346172FB-6A90-4A13-802D-3489A52374A3}
1420 | 1192 | {CB1086A6-671D-11E5-80CA-005056A729E5} | FRESNO | MANCHESTER | Bank 2 | CB 1106 (Non-SCADA) | PGE\BXYD | 2016-10-03 09:07:02.5056181 -07:00 | 2539201106 | 253921106 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {769C6EE6-FD83-4D6C-90AC-2614BBC02EB4}
1422 | 1192 | {CB1086AC-671D-11E5-80CA-005056A729E5} | FRESNO | MANCHESTER | Bank 2 | CB 1108 (Non-SCADA) | PGE\BXYD | 2017-01-23 15:03:41.1982498 -08:00 | 2539201108 | 253921108 | 8 | 3 | 3 | 1 | 540 | 11.78 | 11.66 | 540 | 11.78 | 11.66 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 598 | 13.05 | 12.92 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2640 | 2200 | 2640 | {D2128E06-1E4C-4396-AD22-5D8172E132E4}
1423 | 1194 | {BD2D2688-2764-11E6-B38D-D4BED91EFF1A} | FRESNO | MANCHESTER | Bank 3 | CB 1109 | PGE\BXYD | 2016-10-03 09:29:29.0694961 -07:00 | 2539201109 | 253921109 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {27573762-7B90-4785-A598-0CB5106E1BE4}
1425 | 1194 | {C51F36D8-2764-11E6-B38D-D4BED91EFF1A} | FRESNO | MANCHESTER | Bank 3 | CB 1110 | PGE\BXYD | 2016-10-03 09:37:43.6481765 -07:00 | 2539201110 | 253921110 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {E84BC8FC-B4B3-46FB-A388-7C2586C08BB6}
1426 | 1194 | {CB8E3A6A-2764-11E6-B38D-D4BED91EFF1A} | FRESNO | MANCHESTER | Bank 3 | CB 1111 | PGE\BXYD | 2016-11-28 16:26:40.5576507 -08:00 | 2539201111 | 253921111 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {C43A8CB1-34DC-46A2-AEE5-A2A88C8F5874}
1427 | 1194 | {CB8E3A6D-2764-11E6-B38D-D4BED91EFF1A} | FRESNO | MANCHESTER | Bank 3 | CB 1112 | PGE\BXYD | 2016-10-03 09:54:20.6240554 -07:00 | 2539201112 | 253921112 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {1C0FED25-EC78-4370-88C3-E88F9EE3F090}
1429 | 1195 | {CB1086D3-671D-11E5-80CA-005056A729E5} | FRESNO | MC CALL | Bank 4 | CB 1101 | PGE\BXYD | 2016-10-03 10:05:33.2681156 -07:00 | 2541201101 | 254121101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9697325B-665B-4FEC-98E7-77416EC9A544}
1430 | 1195 | {CB1086DB-671D-11E5-80CA-005056A729E5} | FRESNO | MC CALL | Bank 4 | CB 1103 | PGE\BXYD | 2017-01-23 13:52:14.1420253 -08:00 | 2541201103 | 254121103 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {912A0856-1D09-49E9-9D6B-A5ED92169C3C}
1432 | 1195 | {CB1086EC-671D-11E5-80CA-005056A729E5} | FRESNO | MC CALL | Bank 4 | CB 1105 | PGE\BXYD | 2017-01-23 13:54:28.4918089 -08:00 | 2541201105 | 254121105 | 8 | 3 | 3 | 1 | 573 | 12.51 | 12.38 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {CE241F3C-9543-4129-ADB0-2A1B02A945C0}
1434 | 1195 | {CB1086FA-671D-11E5-80CA-005056A729E5} | FRESNO | MC CALL | Bank 4 | CB 1107 | PGE\BXYD | 2017-01-23 13:55:53.5602448 -08:00 | 2541201107 | 254121107 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {6B74F5FB-A408-4565-A33F-9E3E97B4FBA1}
1440 | 1197 | {CB108717-671D-11E5-80CA-005056A729E5} | FRESNO | MC CALL | Bank 5 | CB 1102 | PGE\BXYD | 2016-10-03 11:38:43.6562912 -07:00 | 2541201102 | 254121102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Emergency capability is 564 if going NORTH (limited by OH Conductor) |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {98FC862F-92D2-458C-A402-02AA34EA0924}
1441 | 1197 | {CB10871C-671D-11E5-80CA-005056A729E5} | FRESNO | MC CALL | Bank 5 | CB 1104 | PGE\BXYD | 2016-10-03 11:40:39.0254817 -07:00 | 2541201104 | 254121104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {29EC3CB6-88EF-4E1E-B061-99ECA454A9EF}
1442 | 1197 | {CB108721-671D-11E5-80CA-005056A729E5} | FRESNO | MC CALL | Bank 5 | CB 1106 | PGE\BXYD | 2016-10-03 11:42:58.5998144 -07:00 | 2541201106 | 254121106 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9A736B3D-6005-49E0-B898-CAA872DA212D}
1443 | 1201 | {CB108735-671D-11E5-80CA-005056A729E5} | FRESNO | MC MULLIN | Bank 1 (Non SCADA) | CB 1104 (Non-SCADA) | PGE\BXYD | 2017-01-23 13:41:33.9993151 -08:00 | 2544101104 | 254411104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {AF316AFB-992D-4A60-847C-8B7A37340E34}
1445 | 1201 | {CB10873B-671D-11E5-80CA-005056A729E5} | FRESNO | MC MULLIN | Bank 1 (Non SCADA) | CB 1105 (Non-SCADA) | PGE\BXYD | 2017-01-23 13:43:27.5850994 -08:00 | 2544101105 | 254411105 | 8 | 3 | 3 | 1 | 650 | 14.19 | 14.05 | 617 | 13.47 | 13.34 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {0DAD9520-FEEE-4E47-AE7B-878D015357D0}
1447 | 1201 | {CB10874A-671D-11E5-80CA-005056A729E5} | FRESNO | MC MULLIN | Bank 1 (Non SCADA) | CB 1106 (Non-SCADA) | PGE\BXYD | 2017-01-23 13:45:54.7739299 -08:00 | 2544101106 | 254411106 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {4C08E3FF-C2CA-4663-915A-1AE46E079B5C}
1448 | 1202 | {CB108759-671D-11E5-80CA-005056A729E5} | FRESNO | OROSI | Bank 1 | CB 1101 | PGE\BXYD | 2016-10-03 12:17:51.5054511 -07:00 | 2528401101 | 252841101 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {C05C606B-E70B-4445-A29A-1F1A006C5F03}
1449 | 1202 | {CB108761-671D-11E5-80CA-005056A729E5} | FRESNO | OROSI | Bank 1 | CB 1103 | PGE\BXYD | 2017-01-23 13:34:15.7712878 -08:00 | 2528401103 | 252841103 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {2DA5D026-EC07-4FE0-A1F8-A2B668595CD5}
1450 | 1204 | {CB10876C-671D-11E5-80CA-005056A729E5} | FRESNO | OROSI | Bank 2 | CB 1102 | PGE\BXYD | 2016-10-03 13:21:54.1791942 -07:00 | 2528401102 | 252841102 | 8 | 3 | 3 | 1 | 231 | 5.04 | 4.99 | 231 | 5.04 | 4.99 | 252 | 5.5 | 5.44 | 252 | 5.5 | 5.44 | 287 | 6.26 | 6.2 | 287 | 6.26 | 6.2 | 303 | 6.61 | 6.54 | 303 | 6.61 | 6.54 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {04A53FEE-E664-418D-AA62-D55891403C6B}
1451 | 1204 | {CB108771-671D-11E5-80CA-005056A729E5} | FRESNO | OROSI | Bank 2 | CB 1104 | PGE\BXYD | 2016-10-03 13:21:43.1167381 -07:00 | 2528401104 | 252841104 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {EB59F6AB-E464-4178-A188-334B5D290240}
1452 | 1206 | {CB10878B-671D-11E5-80CA-005056A729E5} | FRESNO | PARLIER | Bank 2 | CB 1102 | PGE\BXYD | 2017-01-23 13:10:23.9757538 -08:00 | 2522901102 | 252291102 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 489 | 10.67 | 10.56 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {CBF4E9DA-29BD-477D-A4BC-947898A972B1}
1455 | 1206 | {CB108796-671D-11E5-80CA-005056A729E5} | FRESNO | PARLIER | Bank 2 | CB 1103 | PGE\BXYD | 2016-10-03 13:32:24.1474946 -07:00 | 2522901103 | 252291103 | 8 | 3 | 3 | 1 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {EF659EB9-58F8-40D9-B82B-CB665B532EB1}
1457 | 1206 | {CB1087A4-671D-11E5-80CA-005056A729E5} | FRESNO | PARLIER | Bank 2 | CB 1104 | PGE\BXYD | 2017-01-23 13:14:03.4407742 -08:00 | 2522901104 | 252291104 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 489 | 10.67 | 10.56 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {D5401B99-B3DB-45E2-86CA-B5F6CFC31FA9}
1459 | 1208 | {CB1087B8-671D-11E5-80CA-005056A729E5} | FRESNO | PINEDALE | Bank 1 | CB 2101 | PGE\BXYD | 2017-01-23 12:02:58.9583665 -08:00 | 2528502101 | 252852101 | 12 | 3 | 3 | 1 | 512 | 19.35 | 19.16 | 512 | 19.35 | 19.16 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 556 | 21.01 | 20.8 | 556 | 21.01 | 20.8 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1773 | {8A298AAC-3B6B-4B59-9DBB-93ADFFF7451C}
1462 | 1208 | {CB1087DE-671D-11E5-80CA-005056A729E5} | FRESNO | PINEDALE | Bank 1 | CB 2102 | PGE\BXYD | 2017-01-23 12:04:07.8648916 -08:00 | 2528502102 | 252852102 | 12 | 3 | 3 | 1 | 476 | 17.99 | 17.81 | 476 | 17.99 | 17.81 | 578 | 21.84 | 21.62 | 549 | 20.75 | 20.54 | 528 | 19.95 | 19.75 | 528 | 19.95 | 19.75 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1773 | {91611222-02D0-406E-8859-AA0E831BE996}
1464 | 1208 | {D10E1E54-671D-11E5-80CA-005056A729E5} | FRESNO | PINEDALE | Bank 1 | CB 2103 | PGE\BXYD | 2017-01-23 12:04:56.4754264 -08:00 | 2528502103 | 252852103 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1773 | {CE552D31-9FCA-4752-85ED-4C4236C46CA9}
1466 | 1211 | {D10E1E63-671D-11E5-80CA-005056A729E5} | FRESNO | PINEDALE | Bank 2 | CB 2105 | PGE\BXYD | 2016-11-28 16:34:39.7457020 -08:00 | 2528502105 | 252852105 | 12 | 3 | 3 | 1 | 512 | 19.35 | 19.16 | 512 | 19.35 | 19.16 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 556 | 21.01 | 20.8 | 556 | 21.01 | 20.8 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {8E08E35E-6B4F-41DB-904D-81C8358EBC7F}
1469 | 1211 | {D10E1E71-671D-11E5-80CA-005056A729E5} | FRESNO | PINEDALE | Bank 2 | CB 2106 | PGE\JWCp | 2017-08-01 11:37:37.6177452 -07:00 | 2528502106 | 252852106 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {DE96AAE8-5E2A-413E-8043-BD1F7F3B1DE9}
1472 | 1211 | {D10E1E9A-671D-11E5-80CA-005056A729E5} | FRESNO | PINEDALE | Bank 2 | CB 2107 | PGE\BXYD | 2017-01-23 12:09:38.7628549 -08:00 | 2528502107 | 252852107 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {4D9CBCC2-5D9E-4A70-A2D0-9F4D63927021}
1473 | 1213 | {D10E1EAE-671D-11E5-80CA-005056A729E5} | FRESNO | PINEDALE | Bank 3 | CB 2109 | PGE\BXYD | 2017-01-23 13:02:32.0510785 -08:00 | 2528502109 | 252852109 | 12 | 3 | 3 | 1 | 477 | 18.03 | 17.85 | 477 | 18.03 | 17.85 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 528 | 19.95 | 19.75 | 528 | 19.95 | 19.75 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {55AB0942-60F1-4795-988E-8DB420C7ED05}
1477 | 1213 | {D10E1EBC-671D-11E5-80CA-005056A729E5} | FRESNO | PINEDALE | Bank 3 | CB 2110 | PGE\BXYD | 2016-11-28 16:39:16.9578724 -08:00 | 2528502110 | 252852110 | 12 | 3 | 3 | 1 | 477 | 18.03 | 17.85 | 477 | 18.03 | 17.85 | 581 | 21.96 | 21.74 | 581 | 21.96 | 21.74 | 526 | 19.88 | 19.68 | 526 | 19.88 | 19.68 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {EA8B25DE-EB69-42B8-B95C-9BB90AAB1323}
1481 | 1213 | {D10E1ECA-671D-11E5-80CA-005056A729E5} | FRESNO | PINEDALE | Bank 3 | CB 2111 | PGE\BXYD | 2016-11-28 16:40:31.4701663 -08:00 | 2528502111 | 252852111 | 12 | 3 | 3 | 1 | 477 | 18.03 | 17.85 | 477 | 18.03 | 17.85 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 528 | 19.95 | 19.75 | 528 | 19.95 | 19.75 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {F67C5D5C-C6CC-4240-844F-0D4E73A0D064}
1484 | 1214 | {D10E1ED8-671D-11E5-80CA-005056A729E5} | FRESNO | RAINBOW | Bank 1 (Non SCADA) | CB 1105 (Non-SCADA) | PGE\BXYD | 2016-12-09 08:38:57.5742172 -08:00 | 2544401105 | 254441105 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {3229CAEA-C926-41CF-8F1A-95199D08140F}
1487 | 1214 | {D10E1EDE-671D-11E5-80CA-005056A729E5} | FRESNO | RAINBOW | Bank 1 (Non SCADA) | CB 1106 (Non-SCADA) | PGE\BXYD | 2016-10-03 14:39:32.5859037 -07:00 | 2544401106 | 254441106 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {5D0E8FBF-3254-4406-A9EF-5148D80BBAF4}
1489 | 1215 | {D10E1F02-671D-11E5-80CA-005056A729E5} | FRESNO | REEDLEY | Bank 1 | CB 1106 | PGE\BXYD | 2016-10-03 14:59:37.4203193 -07:00 | 2523401106 | 252341106 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {86BFB430-42EE-4C63-B707-20013967A53F}
1491 | 1215 | {D10E1F0D-671D-11E5-80CA-005056A729E5} | FRESNO | REEDLEY | Bank 1 | CB 1112 | PGE\BXYD | 2016-10-03 15:02:10.3246025 -07:00 | 2523401112 | 252341112 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {766D4FF7-847F-408B-BD00-4106C6CFBC36}
1492 | 1216 | {D10E1F24-671D-11E5-80CA-005056A729E5} | FRESNO | REEDLEY | Bank 3 | CB 1101 | PGE\BXYD | 2017-01-23 11:47:02.9251816 -08:00 | 2523401101 | 252341101 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {04F45A0D-15A0-4339-BCC9-A72A4B84575B}
1495 | 1216 | {D10E1F32-671D-11E5-80CA-005056A729E5} | FRESNO | REEDLEY | Bank 3 | CB 1104 | PGE\BXYD | 2016-10-03 15:09:40.8569049 -07:00 | 2523401104 | 252341104 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {98EE472D-82D9-410F-A4A8-D937C262D344}
1496 | 1216 | {D10E1F3A-671D-11E5-80CA-005056A729E5} | FRESNO | REEDLEY | Bank 3 | CB 1110 | PGE\BXYD | 2016-10-03 15:11:29.8848129 -07:00 | 2523401110 | 252341110 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {8B314E24-1612-4C99-A4C2-B07B5E00BEAA}
1499 | 1217 | {D10E1F4E-671D-11E5-80CA-005056A729E5} | FRESNO | RESERVE OIL | Bank 2 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\BXYD | 2016-12-09 09:36:13.8048355 -08:00 | 254181101 | 254181101 | 8 | 3 | 3 | 1 | 160 | 3.49 | 3.46 | 160 | 3.49 | 3.46 | 208 | 4.54 | 4.49 | 208 | 4.54 | 4.49 | 192 | 4.19 | 4.15 | 192 | 4.19 | 4.15 | 240 | 5.24 | 5.19 | 240 | 5.24 | 5.19 |  |  | FALSE | FALSE | 160 | 208 | 192 | 240 | {A70BA924-AAE6-461A-AD62-955E220DC1DA}
1501 | 1221 | {D10E1F57-671D-11E5-80CA-005056A729E5} | FRESNO | RIVER ROCK | Bank 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\BXYD | 2017-01-23 10:28:13.9282411 -08:00 | 255251101 | 255251101 | 8 | 3 | 3 | 1 | 280 | 6.11 | 6.05 | 280 | 6.11 | 6.05 | 280 | 6.11 | 6.05 | 280 | 6.11 | 6.05 | 280 | 6.11 | 6.05 | 280 | 6.11 | 6.05 | 280 | 6.11 | 6.05 | 280 | 6.11 | 6.05 |  |  | FALSE | FALSE | 320 | 416 | 384 | 481 | {00000000-0000-0000-0000-000000000000}
1508 | 1224 | {D10E1F60-671D-11E5-80CA-005056A729E5} | FRESNO | SAN JOAQUIN | Bank 1 | CB 1106 | PGE\BXYD | 2016-10-03 15:49:05.3457861 -07:00 | 2523601106 | 252361106 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {9AC28C28-0387-47A0-82C0-E2104748698F}
1510 | 1224 | {D10E1F6B-671D-11E5-80CA-005056A729E5} | FRESNO | SAN JOAQUIN | Bank 1 | CB 1108 | PGE\BXYD | 2016-10-03 16:16:57.6540522 -07:00 | 2523601108 | 252361108 | 8 | 3 | 3 | 1 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {B59506C8-9D2D-4F35-B5DC-993E40EC3C8D}
1511 | 1225 | {D10E1F79-671D-11E5-80CA-005056A729E5} | FRESNO | SAN JOAQUIN | Bank 2 | CB 1112 | PGE\BXYD | 2016-10-03 16:23:09.1317156 -07:00 | 2523601112 | 252361112 | 8 | 3 | 3 | 1 | 320 | 6.98 | 6.91 | 320 | 6.98 | 6.91 | 386 | 8.42 | 8.34 | 386 | 8.42 | 8.34 | 384 | 8.38 | 8.3 | 384 | 8.38 | 8.3 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 320 | 416 | 384 | 481 | {292A45F8-2E2E-4BB7-8395-1738369BE5A5}
1514 | 1226 | {D10E1F9E-671D-11E5-80CA-005056A729E5} | FRESNO | SANGER | Bank 1 | CB 1108 | PGE\BXYD | 2016-10-03 16:42:46.4447918 -07:00 | 2523501108 | 252351108 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {D364BEFF-AC4A-48FD-AA7C-D8A2E9D0440A}
1517 | 1226 | {D10E1FA7-671D-11E5-80CA-005056A729E5} | FRESNO | SANGER | Bank 1 | CB 1112 | PGE\BXYD | 2016-10-03 16:47:58.8747388 -07:00 | 2523501112 | 252351112 | 8 | 3 | 3 | 1 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {6B329A41-B43B-4CEB-A136-963ECC89EC4C}
1518 | 1226 | {D10E1FAC-671D-11E5-80CA-005056A729E5} | FRESNO | SANGER | Bank 1 | CB 1114 | PGE\BXYD | 2016-10-03 16:49:59.2004940 -07:00 | 2523501114 | 252351114 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {32F6F5C7-E055-4013-BC21-F58041D71D90}
1519 | 1226 | {D10E1FBA-671D-11E5-80CA-005056A729E5} | FRESNO | SANGER | Bank 1 | CB 1116 | PGE\BXYD | 2017-01-23 10:00:25.9441651 -08:00 | 2523501116 | 252351116 | 8 | 3 | 3 | 1 | 425 | 9.28 | 9.19 | 413 | 9.01 | 8.92 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {A42BDF54-CD08-4FFE-93A8-E175E5B2596A}
1520 | 1226 | {D10E1FBF-671D-11E5-80CA-005056A729E5} | FRESNO | SANGER | Bank 1 | CB 1118 | PGE\BXYD | 2016-10-03 16:56:24.6543731 -07:00 | 2523501118 | 252351118 | 8 | 3 | 3 | 1 | 435 | 9.49 | 9.4 | 435 | 9.49 | 9.4 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {EB9738B5-332B-4AE5-8561-3FCAAE905FFB}
1521 | 1227 | {D10E1FCA-671D-11E5-80CA-005056A729E5} | FRESNO | SANGER | Bank 3 | CB 1104 | PGE\BXYD | 2017-01-23 10:07:10.7719501 -08:00 | 2523501104 | 252351104 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 489 | 10.67 | 10.56 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {5D4E3E69-97EB-4847-BEE7-F6FBDAE54AA6}
1522 | 1227 | {D10E1FCF-671D-11E5-80CA-005056A729E5} | FRESNO | SANGER | Bank 3 | CB 1106 | PGE\BXYD | 2016-11-28 16:58:48.3940704 -08:00 | 2523501106 | 252351106 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {30D57098-4541-48A5-976F-951B4115EE75}
1523 | 1227 | {D10E1FD4-671D-11E5-80CA-005056A729E5} | FRESNO | SANGER | Bank 3 | CB 1110 | PGE\BXYD | 2016-10-04 08:12:40.0128762 -07:00 | 2523501110 | 252351110 | 8 | 3 | 3 | 1 | 433 | 9.45 | 9.36 | 433 | 9.45 | 9.36 | 433 | 9.45 | 9.36 | 433 | 9.45 | 9.36 | 433 | 9.45 | 9.36 | 433 | 9.45 | 9.36 | 433 | 9.45 | 9.36 | 433 | 9.45 | 9.36 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {82D055FE-2505-4523-AE22-ECCCF2C6D6D3}
1524 | 1228 | {D10E1FE2-671D-11E5-80CA-005056A729E5} | FRESNO | SCHINDLER | Bank 2 | CB 1104 | PGE\BXYD | 2017-01-23 09:32:56.8052515 -08:00 | 2528901104 | 252891104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {10D388F4-C017-4B04-89EB-B807AD2FB2DB}
1525 | 1228 | {D10E1FE7-671D-11E5-80CA-005056A729E5} | FRESNO | SCHINDLER | Bank 2 | CB 1105 | PGE\BXYD | 2017-01-23 09:33:45.7277923 -08:00 | 2528901105 | 252891105 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {A25135CA-6F77-4AEE-9528-1C72105D0E3A}
1526 | 1228 | {D10E1FF5-671D-11E5-80CA-005056A729E5} | FRESNO | SCHINDLER | Bank 2 | CB 1107 | PGE\BXYD | 2017-01-23 09:34:19.6584448 -08:00 | 2528901107 | 252891107 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {3C68C230-C576-4E2A-BD15-E7E0CDF2FF49}
1527 | 1228 | {D10E1FFA-671D-11E5-80CA-005056A729E5} | FRESNO | SCHINDLER | Bank 2 | CB 1108 | PGE\BXYD | 2017-01-23 09:34:41.4052630 -08:00 | 2528901108 | 252891108 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F0244D35-217A-4BB3-B984-7E1E44C1E1C6}
1530 | 1228 | {D10E1FFF-671D-11E5-80CA-005056A729E5} | FRESNO | SCHINDLER | Bank 2 | CB 1109 | PGE\BXYD | 2017-01-23 09:35:58.7983513 -08:00 | 2528901109 | 252891109 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {9F22E792-820B-400C-835C-A5E483DA3936}
1531 | 1228 | {D10E2004-671D-11E5-80CA-005056A729E5} | FRESNO | SCHINDLER | Bank 2 | CB 1114 | PGE\BXYD | 2016-10-04 08:43:58.7254022 -07:00 | 2528901114 | 252891114 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {CF7914E8-9344-409A-9C3E-01A0232CAB45}
1533 | 1228 | {D10E2018-671D-11E5-80CA-005056A729E5} | FRESNO | SCHINDLER | Bank 2 | CB 1116 | PGE\BXYD | 2016-10-04 08:46:30.8743567 -07:00 | 2528901116 | 252891116 | 8 | 3 | 3 | 1 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F95F612F-8BA8-49A3-992F-D3383DA8F4B1}
1535 | 1230 | {2717D5B2-A5BE-11E5-A1F0-D4BED91EFF1A} | FRESNO | SCHINDLER | Bank 3 | CB 1110 | PGE\KRBk | 2016-12-08 14:16:46.2456926 -08:00 | 2528901110 | 252891110 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {01EA1437-A71F-4138-990D-668C2BFC2127}
1536 | 1232 | {B134AF90-2758-11E6-B38D-D4BED91EFF1A} | FRESNO | SHEPHERD | Bank 3 | CB 2110 | PGE\BXYD | 2016-10-04 09:51:15.7725335 -07:00 | 2520602110 | 252062110 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {DB4257F4-E81B-4A3A-905A-EB7BFA0FF932}
1537 | 1232 | {B134AF93-2758-11E6-B38D-D4BED91EFF1A} | FRESNO | SHEPHERD | Bank 3 | CB 2111 | PGE\BXYD | 2016-11-29 10:06:36.6438960 -08:00 | 2520602111 | 252062111 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {0090D235-4406-4F0B-968F-7B42C3544DA3}
1541 | 1232 | {B134AF96-2758-11E6-B38D-D4BED91EFF1A} | FRESNO | SHEPHERD | Bank 3 | CB 2112 | PGE\BXYD | 2017-01-23 09:28:55.0318021 -08:00 | 2520602112 | 252062112 | 12 | 3 | 3 | 1 | 198 | 7.48 | 7.41 | 198 | 7.48 | 7.41 | 257 | 9.71 | 9.61 | 257 | 9.71 | 9.61 | 238 | 8.99 | 8.9 | 238 | 8.99 | 8.9 | 297 | 11.22 | 11.11 | 297 | 11.22 | 11.11 | Summer Capability (norm/emerg): 241/253 Winter Capability (norm/emerg): 281/295 |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {EFB0992F-1D5E-4BCE-9DFC-81CD1D0140B9}
1544 | 1234 | {D10E202F-671D-11E5-80CA-005056A729E5} | FRESNO | STONE CORRAL | Bank 2 | CB 1108 (Non-SCADA) | PGE\BXYD | 2016-11-29 09:27:14.1058579 -08:00 | 2529201108 | 252921108 | 8 | 3 | 3 | 1 | 229 | 5 | 4.95 | 229 | 5 | 4.95 | 297 | 6.48 | 6.42 | 297 | 6.48 | 6.42 | 274 | 5.98 | 5.92 | 274 | 5.98 | 5.92 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 |  |  | FALSE | FALSE | 229 | 297 | 274 | 343 | {117D9510-6180-4DFC-8743-20DE88CAC6F4}
1546 | 1236 | {D10E203B-671D-11E5-80CA-005056A729E5} | FRESNO | STONE CORRAL | Bank 3 | CB 1109 (Non-SCADA) | PGE\BXYD | 2016-10-04 10:16:39.2329328 -07:00 | 2529201109 | 252921109 | 8 | 3 | 3 | 1 | 345 | 7.53 | 7.45 | 345 | 7.53 | 7.45 | 386 | 8.42 | 8.34 | 386 | 8.42 | 8.34 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 702 | 702 | 702 | 702 | {C75331F6-6ECE-4782-A2E0-FB7BAA004475}
1547 | 1236 | {D10E2041-671D-11E5-80CA-005056A729E5} | FRESNO | STONE CORRAL | Bank 3 | CB 1110 (Non-SCADA) | PGE\BXYD | 2017-01-23 09:18:47.6029210 -08:00 | 2529201110 | 252921110 | 8 | 3 | 3 | 1 | 183 | 3.99 | 3.95 | 173 | 3.78 | 3.74 | 211 | 4.6 | 4.55 | 200 | 4.36 | 4.32 | 266 | 5.81 | 5.75 | 252 | 5.5 | 5.45 | 284 | 6.2 | 6.14 | 269 | 5.87 | 5.81 |  |  | FALSE | FALSE | 701 | 701 | 701 | 701 | {E513E8D2-EB92-4CFD-B22C-ACC3B40C93E5}
1549 | 1241 | {D10E207B-671D-11E5-80CA-005056A729E5} | FRESNO | TULARE LAKE | Bank 1 | CB 1104 (Non-SCADA) | PGE\BXYD | 2016-10-04 10:42:25.4322011 -07:00 | 2529501104 | 252951104 | 8 | 3 | 3 | 1 | 171 | 3.73 | 3.69 | 171 | 3.73 | 3.69 | 223 | 4.87 | 4.82 | 223 | 4.87 | 4.82 | 206 | 4.5 | 4.46 | 206 | 4.5 | 4.46 | 257 | 5.61 | 5.55 | 257 | 5.61 | 5.55 |  |  | FALSE | FALSE | 171 | 223 | 206 | 257 | {8841CCD1-F25D-414E-B5D8-64CE2BD6A62B}
1550 | 1241 | {D10E2081-671D-11E5-80CA-005056A729E5} | FRESNO | TULARE LAKE | Bank 1 | CB 1106 | PGE\BXYD | 2016-10-04 10:43:25.3801315 -07:00 | 2529501106 | 252951106 | 8 | 3 | 3 | 1 | 171 | 3.73 | 3.69 | 171 | 3.73 | 3.69 | 223 | 4.87 | 4.82 | 223 | 4.87 | 4.82 | 206 | 4.5 | 4.46 | 206 | 4.5 | 4.46 | 257 | 5.61 | 5.55 | 257 | 5.61 | 5.55 |  |  | FALSE | FALSE | 171 | 223 | 206 | 257 | {4C8139CD-6D47-453F-8567-5F2CC624531F}
1551 | 1244 | {D7085BD9-671D-11E5-80CA-005056A729E5} | FRESNO | WAHTOKE | Bank 3 | CB 1109 | PGE\BXYD | 2016-10-04 11:24:37.9065570 -07:00 | 2545301109 | 254531109 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {5C034BC1-8F67-43D9-93B5-0FA13CE5B533}
1553 | 1244 | {D7085BDE-671D-11E5-80CA-005056A729E5} | FRESNO | WAHTOKE | Bank 3 | CB 1110 | PGE\BXYD | 2017-01-23 08:11:51.3680872 -08:00 | 2545301110 | 254531110 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 570 | 12.44 | 12.32 | 683 | 14.91 | 14.76 | 683 | 14.91 | 14.76 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 683 | 14.91 | 14.76 | 683 | 14.91 | 14.76 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {2798A027-8483-4679-B18C-CAFD67084764}
1555 | 1244 | {D7085BEC-671D-11E5-80CA-005056A729E5} | FRESNO | WAHTOKE | Bank 3 | CB 1111 | PGE\BXYD | 2017-01-23 08:12:41.3358481 -08:00 | 2545301111 | 254531111 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {6EFB2E2B-3B26-4B0B-8F3A-D8AB8C277A8A}
1556 | 1240 | {B2D17508-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | BELLEVUE | Bank 2 | CB 1102 | PGE\DCGa | 2017-03-16 06:42:39.4145312 -07:00 | 0431801102 | 043181102 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Capability Sheet done by GER5 6/4/11 |  | FALSE | TRUE | 733 | 953 | 879 | 1099 | {F72EE35A-5193-497F-8FF4-82FD69ECC55A}
1557 | 1240 | {B2D1756C-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | BELLEVUE | Bank 2 | CB 1104 | PGE\C8M4 | 2016-11-03 11:25:42.6039456 -07:00 | 0431801104 | 043181104 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Capability Sheet done by: ZJC1 7/1/2008 |  | FALSE | TRUE | 733 | 953 | 879 | 1099 | {A22AFFE4-3374-48F8-8183-FF2A06D0BA17}
1558 | 1249 | {D7085BFD-671D-11E5-80CA-005056A729E5} | FRESNO | WEST FRESNO | Bank 1 | CB 1101 | PGE\BXYD | 2017-01-20 14:25:28.9961891 -08:00 | 2537301101 | 253731101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {D57994AE-1155-493A-BACE-3D17CBD95ABB}
1559 | 1249 | {D7085C0B-671D-11E5-80CA-005056A729E5} | FRESNO | WEST FRESNO | Bank 1 | CB 1102 | PGE\BXYD | 2017-01-26 10:48:51.3998144 -08:00 | 2537301102 | 253731102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F6B9865E-1210-46F2-BAAB-A0DDD13C1BFE}
1560 | 1249 | {D7085C10-671D-11E5-80CA-005056A729E5} | FRESNO | WEST FRESNO | Bank 1 | CB 1103 | PGE\J2T4 | 2017-01-08 17:16:49.9594193 -08:00 | 2537301103 | 253731103 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | J2T4 - 210A reserved capacity for Danish Creamery. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {15B66C52-1396-440F-8145-1A10EB98578D}
1562 | 1249 | {D7085C15-671D-11E5-80CA-005056A729E5} | FRESNO | WEST FRESNO | Bank 1 | CB 1104 | PGE\BXYD | 2016-10-04 13:05:00.7842335 -07:00 | 2537301104 | 253731104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {12753577-240B-4171-BEFD-F658584C3183}
1564 | 1249 | {D7085C26-671D-11E5-80CA-005056A729E5} | FRESNO | WEST FRESNO | Bank 1 | CB 1109 | PGE\BXYD | 2016-10-04 13:10:45.3133883 -07:00 | 2537301109 | 253731109 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {ACC419EA-A120-4EA4-A1F0-D7CAB0ABC6FF}
1565 | 1252 | {D7085C3A-671D-11E5-80CA-005056A729E5} | FRESNO | WEST FRESNO | Bank 2 | CB 1105 | PGE\BXYD | 2016-10-04 13:21:06.1354811 -07:00 | 2537301105 | 253731105 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {6B67ADD4-52B2-49D1-B28A-90686FC3D067}
1566 | 1252 | {D7085C42-671D-11E5-80CA-005056A729E5} | FRESNO | WEST FRESNO | Bank 2 | CB 1106 | PGE\BXYD | 2016-10-04 13:23:04.9325676 -07:00 | 2537301106 | 253731106 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {8E29C457-0D1B-4408-9ED4-A130AAEECDCB}
1567 | 1252 | {D7085C4A-671D-11E5-80CA-005056A729E5} | FRESNO | WEST FRESNO | Bank 2 | CB 1107 | PGE\BXYD | 2016-10-04 16:36:29.3818286 -07:00 | 2537301107 | 253731107 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {89984C32-8EDB-4A5D-BCCB-0E10CE9B5148}
1569 | 1252 | {D7085C52-671D-11E5-80CA-005056A729E5} | FRESNO | WEST FRESNO | Bank 2 | CB 1108 | PGE\BXYD | 2016-11-29 09:36:47.7791679 -08:00 | 2537301108 | 253731108 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {5B07A939-3703-4A20-896C-41EA03CC1AC9}
1573 | 1252 | {D7085C5A-671D-11E5-80CA-005056A729E5} | FRESNO | WEST FRESNO | Bank 2 | CB 1110 | PGE\BXYD | 2016-10-04 16:30:33.1753425 -07:00 | 2537301110 | 253731110 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9E4729E8-66AB-414F-9C0F-F2718814E4FB}
1578 | 1251 | {B2D17587-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | BELLEVUE | Bank 4 | CB 2101 | PGE\DCGa | 2017-07-19 07:42:05.6054186 -07:00 | 0431802101 | 043182101 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | Capability Sheet done by: JDLM 1/27/2016 |  | FALSE | TRUE | 793 | 984 | 952 | 1190 | {EC7F2769-7FF2-4301-9D71-BD4C40A07B0C}
1579 | 1253 | {D7085C65-671D-11E5-80CA-005056A729E5} | FRESNO | WEST FRESNO | Bank 3 | CB 1111 | PGE\BXYD | 2016-10-04 13:56:28.3406649 -07:00 | 2537301111 | 253731111 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {5BC09781-10B2-4BEF-A13F-3CD53F35E8D3}
1580 | 1253 | {D7085C76-671D-11E5-80CA-005056A729E5} | FRESNO | WEST FRESNO | Bank 3 | CB 1112 | PGE\BXYD | 2016-10-04 14:00:01.6755574 -07:00 | 2537301112 | 253731112 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F591E429-0F3F-4AB1-8B2A-6EE73FC9A063}
1582 | 1251 | {B2D175F9-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | BELLEVUE | Bank 4 | CB 2105 | PGE\DCGa | 2017-03-16 06:46:22.0605856 -07:00 | 0431802105 | 043182105 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 675 | 25.51 | 25.25 | 675 | 25.51 | 25.25 | 675 | 25.51 | 25.25 | 675 | 25.51 | 25.25 | 675 | 25.51 | 25.25 | 675 | 25.51 | 25.25 |  |  | FALSE | TRUE | 793 | 984 | 952 | 1190 | {871AC6F9-F62F-43A9-AFC0-7382E4361A40}
1583 | 1254 | {B91E84F2-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | CORONA | Bank 1 | CB 1101 | PGE\C8M4 | 2017-04-10 15:29:14.7721698 -07:00 | 0434901101 | 043491101 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | TRUE | 1374 | 1787 | 1649 | 2061 | {FEEA1A10-B7F5-4EDC-943A-633AF94E1AB1}
1584 | 1254 | {B91E8509-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | CORONA | Bank 1 | CB 1102 | PGE\C8M4 | 2016-11-03 18:27:45.1995186 -07:00 | 0434901102 | 043491102 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | TRUE | 1374 | 1787 | 1649 | 2061 | {E3B3D5A8-4580-47DC-9A2A-1E715D8349C2}
1585 | 1254 | {B91E8512-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | CORONA | Bank 1 | CB 1103 | PGE\C8M4 | 2016-11-03 18:32:01.8571831 -07:00 | 0434901103 | 043491103 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | TRUE | 1374 | 1787 | 1649 | 2061 | {A35CAE45-FFBD-42E7-8719-C4B78C449ECE}
1586 | 1256 | {D10E1EED-671D-11E5-80CA-005056A729E5} | FRESNO | RANCHERS COTTON | Bank 1 (Non SCADA) | CB 1101 | PGE\BXYD | 2016-12-09 08:42:34.7478384 -08:00 | 254801101 | 254801101 | 8 | 3 | 3 | 1 | 560 | 12.22 | 12.1 | 560 | 12.22 | 12.1 | 560 | 12.22 | 12.1 | 560 | 12.22 | 12.1 | 560 | 12.22 | 12.1 | 560 | 12.22 | 12.1 | 560 | 12.22 | 12.1 | 560 | 12.22 | 12.1 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {BF295D23-C895-479C-A878-5742DC70A6C7}
1588 | 1257 | {D7085C87-671D-11E5-80CA-005056A729E5} | FRESNO | WOODCHUCK | Bank 1 (Non SCADA) | CB 2101 (Non-SCADA) | PGE\BXYD | 2017-01-09 08:50:30.8532022 -08:00 | 254912101 | 254912101 | 11 | 3 | 3 | 1 | 150 | 5.61 | 5.55 | 150 | 5.61 | 5.55 | 150 | 5.61 | 5.55 | 150 | 5.61 | 5.55 | 150 | 5.61 | 5.55 | 150 | 5.61 | 5.55 | 150 | 5.61 | 5.55 | 150 | 5.61 | 5.55 |  |  | FALSE | FALSE | 270 | 270 | 270 | 270 | {6C6BBC67-03BA-4837-92C5-EE7B4BC36408}
1592 | 1258 | {D7085C90-671D-11E5-80CA-005056A729E5} | FRESNO | WOODWARD | Bank 1 | CB 2101 | PGE\KRBk | 2016-10-14 11:48:56.8782092 -07:00 | 2552902101 | 255292101 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {E73CA33A-D2F7-4C60-AA60-BBB5094DFA86}
1593 | 1126 | {5A8ACAC3-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | BIG LAGOON | Bank 1 | CB 1101 | PGE\D5LZ | 2017-07-20 14:48:27.5400186 -07:00 | 192361101 | 192361101 | 8 | 3 | 3 | 2 | 110 | 2.4 | 2.38 | 68 | 1.48 | 1.47 | 124 | 2.71 | 2.68 | 89 | 1.94 | 1.92 | 144 | 3.14 | 3.11 | 82 | 1.79 | 1.77 | 153 | 3.34 | 3.31 | 103 | 2.25 | 2.23 |  |  | FALSE | TRUE | 68 | 89 | 82 | 103 | {3E849770-8916-4FB9-8044-5E5EE7E463E1}
1594 | 1258 | {D7085CA7-671D-11E5-80CA-005056A729E5} | FRESNO | WOODWARD | Bank 1 | CB 2102 | PGE\KRBk | 2016-10-14 12:28:56.5649111 -07:00 | 2552902102 | 255292102 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {B81ED366-432C-426A-BF8C-1490D479BA89}
1597 | 1258 | {D7085CB8-671D-11E5-80CA-005056A729E5} | FRESNO | WOODWARD | Bank 1 | CB 2103 | PGE\KRBk | 2016-10-14 12:47:36.4618602 -07:00 | 2552902103 | 255292103 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {16176905-9468-4728-BF65-165DA733FEC8}
1598 | 1262 | {D7085CCF-671D-11E5-80CA-005056A729E5} | FRESNO | WOODWARD | Bank 2 | CB 2104 | PGE\KRBk | 2016-11-10 09:58:31.6348158 -08:00 | 2552902104 | 255292104 | 11 | 3 | 3 | 1 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 700 | 26.19 | 25.93 | 700 | 26.19 | 25.93 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 700 | 26.19 | 25.93 | 700 | 26.19 | 25.93 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {250F8BF5-7491-4E77-8ED8-FCA1F2E20AFC}
1599 | 1196 | {1849F849-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | ATASCADERO | Bank 1 | CB 1101 | PGE\A9S5 | 2016-11-09 11:55:14.0108595 -08:00 | 1825401101 | 182541101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F78C9BC5-0FF6-42E6-8D99-6AC7BDAD4D5B}
1600 | 1196 | {1EB17AE7-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | ATASCADERO | Bank 1 | CB 1102 | PGE\A9S5 | 2016-11-09 11:55:44.9936511 -08:00 | 1825401102 | 182541102 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Good For 600A Summer Emerg when load picked up through tie SW 30499 |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {FA9F0207-7BA2-49F5-A875-5A1EA46B6FAB}
1601 | 1264 | {4C486F6A-671D-11E5-80CA-005056A729E5} | YOSEMITE | ATWATER | Bank 1 | CB 1105 | PGE\BXYD | 2016-10-13 13:40:33.1438014 -07:00 | 2536101105 | 253611105 | 8 | 3 | 3 | 1 | 573 | 12.51 | 12.38 | 573 | 12.51 | 12.38 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 634 | 13.84 | 13.7 | 634 | 13.84 | 13.7 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {0E4B80CE-9FEF-4EDB-B630-F63D867B43C3}
1603 | 1264 | {4C486F72-671D-11E5-80CA-005056A729E5} | YOSEMITE | ATWATER | Bank 1 | CB 1106 | PGE\BXYD | 2016-10-05 09:51:37.4161463 -07:00 | 2536101106 | 253611106 | 8 | 3 | 3 | 1 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F4264C9C-5E14-40C9-BFB1-336D25AE392A}
1606 | 1196 | {1EB17AF2-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | ATASCADERO | Bank 1 | CB 1103 | PGE\A9S5 | 2016-11-09 11:56:12.9968685 -08:00 | 1825401103 | 182541103 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {6147B175-262F-4277-B2F8-0ECD612357DD}
1607 | 1264 | {4C486F7A-671D-11E5-80CA-005056A729E5} | YOSEMITE | ATWATER | Bank 1 | CB 1107 | PGE\BXYD | 2016-10-13 13:42:02.3576922 -07:00 | 2536101107 | 253611107 | 8 | 3 | 3 | 1 | 512 | 11.17 | 11.06 | 512 | 11.17 | 11.06 | 608 | 13.27 | 13.14 | 608 | 13.27 | 13.14 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 646 | 14.1 | 13.96 | 646 | 14.1 | 13.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F3AFA0DF-F312-463A-9434-B4D7D85A8BEA}
1608 | 1264 | {4C486F85-671D-11E5-80CA-005056A729E5} | YOSEMITE | ATWATER | Bank 1 | CB 1108 | PGE\BXYD | 2016-10-13 13:42:16.2423918 -07:00 | 2536101108 | 253611108 | 8 | 3 | 3 | 1 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {E5202B98-E4EF-4527-AD0C-EBED8FECCD6D}
1609 | 1267 | {280E30D0-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | BAYWOOD | Bank 1 | CB 1101 | PGE\A9S5 | 2016-11-09 11:59:19.7640339 -08:00 | 182801101 | 182801101 | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 582 | 12.7 | 12.57 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | East: Paralle 397 AL Conductor - Limiting Factor of 402 A |  | FALSE | FALSE | 733 | 842 | 842 | 842 | {590AE6C8-2870-40A5-9C8B-2961AC7B01A4}
1610 | 1268 | {280E30DF-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | BUELLTON | Bank 1 | CB 1101 | PGE\A9S5 | 2016-11-11 08:37:32.7235149 -08:00 | 1830401101 | 183041101 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {F17703A6-F4AC-45C3-A62A-17F47480F190}
1612 | 1269 | {280E30F6-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | BUELLTON | Bank 2 | CB 1102 | PGE\A9S5 | 2016-11-11 08:38:55.5035408 -08:00 | 1830401102 | 183041102 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {797D582C-2C58-4998-B58E-2A0683CB8625}
1613 | 1270 | {4C486F90-671D-11E5-80CA-005056A729E5} | YOSEMITE | ATWATER | Bank 2 | CB 1102 | PGE\BXYD | 2016-10-05 14:32:18.3810777 -07:00 | 2536101102 | 253611102 | 8 | 3 | 3 | 1 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F878E505-B299-489C-AAE0-26906AE947F2}
1615 | 1270 | {4C486FA1-671D-11E5-80CA-005056A729E5} | YOSEMITE | ATWATER | Bank 2 | CB 1103 | PGE\JCD5 | 2017-01-18 13:35:03.1388672 -08:00 | 2536101103 | 253611103 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 634 | 13.84 | 13.7 | 632 | 13.79 | 13.65 | 700 | 15.28 | 15.13 | 675 | 14.73 | 14.58 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {77264F8F-44C0-465E-A06D-B00FE7F8CF5F}
1616 | 1270 | {4C486FA9-671D-11E5-80CA-005056A729E5} | YOSEMITE | ATWATER | Bank 2 | CB 1104 | PGE\BXYD | 2016-10-05 14:37:23.3237791 -07:00 | 2536101104 | 253611104 | 8 | 3 | 3 | 1 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {BCD9A91D-D290-47AB-86A0-01B925125CC0}
1670 | 1290 | {58406B52-671D-11E5-80CA-005056A729E5} | YOSEMITE | DOS PALOS | Bank 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\VxLa | 2017-07-31 15:10:28.6134965 -07:00 | 2540401101 | 254041101 | 8 | 3 | 3 | 1 | 572 | 12.48 | 12.36 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {51EE17B9-3BF8-4DCF-9595-84A080DDB94F}
1671 | 1290 | {58406B5B-671D-11E5-80CA-005056A729E5} | YOSEMITE | DOS PALOS | Bank 1 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\BXYD | 2016-12-27 08:51:51.4889704 -08:00 | 2540401102 | 254041102 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {07D81684-1925-4C36-BA59-D6C1FA2CE185}
2624 | 1292 | {58406B64-671D-11E5-80CA-005056A729E5} | YOSEMITE | EL CAPITAN | Bank 1 | CB 1103 | PGE\BXYD | 2016-10-06 13:05:54.0255271 -07:00 | 2538801103 | 253881103 | 8 | 3 | 3 | 1 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {80DA6B82-F247-440F-9683-AB8FAA9ADBBA}
2625 | 1292 | {58406B79-671D-11E5-80CA-005056A729E5} | YOSEMITE | EL CAPITAN | Bank 1 | CB 1104 (Non-SCADA) | PGE\BXYD | 2016-10-06 13:10:25.4562599 -07:00 | 2538801104 | 253881104 | 8 | 3 | 3 | 1 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {680D3E78-BDFF-4927-8FCA-2423F818B7B3}
2627 | 2274 | {58406B8B-671D-11E5-80CA-005056A729E5} | YOSEMITE | EL CAPITAN | Bank 2 | CB 1102 | PGE\BXYD | 2016-10-06 13:19:49.6479849 -07:00 | 2538801102 | 253881102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {0AADC527-6ED0-4AFC-B621-213E3A620B46}
2628 | 2274 | {58406B96-671D-11E5-80CA-005056A729E5} | YOSEMITE | EL CAPITAN | Bank 2 | CB 1105 | PGE\BXYD | 2016-10-06 13:24:40.9440989 -07:00 | 2538801105 | 253881105 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F797BC0D-C77F-468F-A25B-E5B9AB21EFC3}
2629 | 2274 | {58406B9B-671D-11E5-80CA-005056A729E5} | YOSEMITE | EL CAPITAN | Bank 2 | CB 1106 (Non-SCADA) | PGE\BXYD | 2016-10-06 13:28:59.3402658 -07:00 | 2538801106 | 253881106 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {54AFAF56-F5AF-45D3-8AC2-A298CEC2E7E3}
2630 | 2275 | {58406BB0-671D-11E5-80CA-005056A729E5} | YOSEMITE | EL CAPITAN | Bank 3 | CB 2109 | PGE\BXYD | 2016-11-08 15:53:29.6354692 -08:00 | 2538802109 | 253882109 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {1FCAB617-4728-4F64-83B5-CE00D67C6879}
2631 | 2275 | {58406BBE-671D-11E5-80CA-005056A729E5} | YOSEMITE | EL CAPITAN | Bank 3 | CB 2110 | PGE\BXYD | 2016-11-08 15:53:46.0632262 -08:00 | 2538802110 | 253882110 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {38220715-572C-49B9-8BA9-069EB6F3B40C}
2632 | 2277 | {58406BCF-671D-11E5-80CA-005056A729E5} | YOSEMITE | EL NIDO | Bank 1 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\BXYD | 2016-10-06 14:51:44.9957803 -07:00 | 2524501102 | 252451102 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {18A94069-D144-4249-92DA-4F086C12E9BA}
2634 | 2277 | {58406BD2-671D-11E5-80CA-005056A729E5} | YOSEMITE | EL NIDO | Bank 1 (Non SCADA) | CB 1104 (Non-SCADA) | PGE\BXYD | 2016-12-27 09:31:51.4701068 -08:00 | 2524501104 | 252451104 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {0808F825-4768-483A-8EDF-92C97E7FB7B6}
2635 | 2279 | {58406BD8-671D-11E5-80CA-005056A729E5} | YOSEMITE | EL NIDO | Bank 2 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\BXYD | 2016-10-06 15:29:05.0079408 -07:00 | 2524501101 | 252451101 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {1C5BD8F4-D1F0-41EC-B1CA-495AEE2A0355}
2636 | 2278 | {5A8ACB16-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | BRIDGEVILLE | Bank 2 | CB 1101 | PGE\C8M4 | 2017-04-27 12:41:51.8500629 -07:00 | 1924601101 | 192461101 | 8 | 3 | 3 | 2 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | QA CHECKED BY C8M4 ON 4/27/2017 |  | FALSE | TRUE | 274 | 357 | 329 | 412 | {6CB02827-48C7-44B6-A72F-E0001A04DF04}
2637 | 2279 | {58406BE4-671D-11E5-80CA-005056A729E5} | YOSEMITE | EL NIDO | Bank 2 (Non SCADA) | CB 1103 (Non-SCADA) | PGE\BXYD | 2016-10-06 15:45:35.7101555 -07:00 | 2524501103 | 252451103 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {86514801-0AAD-4D10-BBF1-8228BCEA10F0}
2638 | 2278 | {5A8ACB2D-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | BRIDGEVILLE | Bank 2 | CB 1102 | PGE\C8M4 | 2017-04-27 12:54:29.3309805 -07:00 | 1924601102 | 192461102 | 8 | 3 | 3 | 2 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | QA CHECKED BY C8M4 ON 4/27/2017 |  | FALSE | TRUE | 274 | 357 | 329 | 412 | {49A2283C-CAA3-4D3D-8C7E-5ABE9ED15E79}
2644 | 1261 | {5A8ACAEF-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | BLUE LAKE | Bank 1 | CB 1101 | PGE\D5LZ | 2017-07-24 11:45:42.5780604 -07:00 | 1921801101 | 192181101 | 8 | 3 | 3 | 2 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | TRUE | 577 | 721 | 692 | 721 | {799B54F8-0F73-4F88-A46A-4C855955F2DD}
2645 | 1261 | {5A8ACAFF-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | BLUE LAKE | Bank 1 | CB 1102 | PGE\D5LZ | 2017-07-24 11:44:18.5865836 -07:00 | 1921801102 | 192181102 | 8 | 3 | 3 | 2 | 492 | 10.74 | 10.63 | 467 | 10.19 | 10.09 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | TRUE | 577 | 721 | 692 | 721 | {E478AF4F-B711-489C-B1DA-FA549F613586}
2646 | 2280 | {58406BF0-671D-11E5-80CA-005056A729E5} | YOSEMITE | EL PECO | Bank 1 | CB 1102 (Non-SCADA) | PGE\BXYD | 2016-10-06 16:47:28.1599208 -07:00 | 2539801102 | 253981102 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 625 | 577 | 702 | {37B73FD4-03D0-409A-918A-A22F193A5271}
2648 | 2282 | {58406BFC-671D-11E5-80CA-005056A729E5} | YOSEMITE | EL PECO | Bank 2 | CB 1105 | PGE\KRBk | 2016-12-12 08:37:52.5771049 -08:00 | 2539801105 | 253981105 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {3CE8BB33-C545-469B-8567-135F2A3D5BE1}
2650 | 2282 | {58406C01-671D-11E5-80CA-005056A729E5} | YOSEMITE | EL PECO | Bank 2 | CB 1106 | PGE\BXYD | 2016-10-06 16:45:58.6738581 -07:00 | 2539801106 | 253981106 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {7C141E6C-9B7B-43A1-8226-E8EF48FCC98C}
2652 | 2284 | {58406C15-671D-11E5-80CA-005056A729E5} | YOSEMITE | FIREBAUGH | Bank 1 | CB 1101 | PGE\BXYD | 2016-10-06 17:12:41.6900959 -07:00 | 2534701101 | 253471101 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {14241AFF-2C5E-42BE-A1B9-767D9EFC61C1}
2655 | 2284 | {58406C1D-671D-11E5-80CA-005056A729E5} | YOSEMITE | FIREBAUGH | Bank 1 | CB 1102 | PGE\BXYD | 2016-10-10 08:16:12.7907323 -07:00 | 2534701102 | 253471102 | 8 | 3 | 3 | 1 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F00DAFD9-C647-41C0-8791-B4ADD18E7503}
2656 | 2286 | {280E3113-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | CABRILLO | Bank 1 | CB 1103 | PGE\A9S5 | 2016-11-11 08:40:08.8457279 -08:00 | 1831001103 | 183101103 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {F3412F9E-EA64-4871-837D-4D9BC92B35FB}
2657 | 2286 | {2EA06DB1-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | CABRILLO | Bank 1 | CB 1104 | PGE\A9S5 | 2016-11-11 08:40:26.6526853 -08:00 | 1831001104 | 183101104 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {44CDD289-6FEE-4829-A205-E24BEAE8E4AC}
2658 | 2287 | {2EA06DC8-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | CAMBRIA | Bank 1 | CB 1101 | PGE\J2T4 | 2017-07-06 08:28:02.8789350 -07:00 | 1827701101 | 182771101 | 8 | 3 | 3 | 2 | 150 | 3.27 | 3.24 | 142 | 3.1 | 3.07 | 169 | 3.69 | 3.65 | 160 | 3.49 | 3.46 | 190 | 4.15 | 4.11 | 188 | 4.1 | 4.06 | 190 | 4.15 | 4.11 | 190 | 4.15 | 4.11 |  |  | FALSE | FALSE | 206 | 268 | 247 | 309 | {086F4912-4CAA-477C-8C44-6D426DB8CE1A}
2659 | 2287 | {2EA06DD0-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | CAMBRIA | Bank 1 | CB 1102 | PGE\J2T4 | 2017-07-06 08:28:07.8241984 -07:00 | 1827701102 | 182771102 | 8 | 3 | 3 | 2 | 206 | 4.5 | 4.46 | 206 | 4.5 | 4.46 | 268 | 5.85 | 5.79 | 268 | 5.85 | 5.79 | 247 | 5.39 | 5.34 | 247 | 5.39 | 5.34 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 |  |  | FALSE | FALSE | 206 | 268 | 247 | 309 | {7519E5D7-AC11-4FB0-A70F-3E54185561C4}
2660 | 2288 | {2EA06DE4-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | CAYUCOS | Bank 1 | CB 1101 | PGE\A9S5 | 2016-11-11 08:44:14.8386420 -08:00 | 1825501101 | 182551101 | 8 | 3 | 3 | 2 | 321 | 7.01 | 6.94 | 321 | 7.01 | 6.94 | 360 | 7.86 | 7.78 | 360 | 7.86 | 7.78 | 358 | 7.81 | 7.73 | 358 | 7.81 | 7.73 | 382 | 8.34 | 8.26 | 382 | 8.34 | 8.26 |  |  | FALSE | FALSE | 572 | 744 | 687 | 842 | {1177E3F8-155B-4381-AFCF-B4BDB4A19A55}
2661 | 2289 | {2EA06DF2-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | CAYUCOS | Bank 2 | CB 1102 | PGE\A9S5 | 2016-11-11 08:44:55.4272113 -08:00 | 1825501102 | 182551102 | 8 | 3 | 3 | 2 | 369 | 8.05 | 7.97 | 369 | 8.05 | 7.97 | 414 | 9.04 | 8.95 | 414 | 9.04 | 8.95 | 415 | 9.06 | 8.97 | 415 | 9.06 | 8.97 | 443 | 9.67 | 9.57 | 443 | 9.67 | 9.57 |  |  | FALSE | FALSE | 572 | 744 | 687 | 842 | {C8B9D84F-F6E6-4659-8F3E-E63B49809E3D}
2662 | 2284 | {58406C22-671D-11E5-80CA-005056A729E5} | YOSEMITE | FIREBAUGH | Bank 1 | CB 1103 | PGE\BXYD | 2016-10-10 08:20:38.4465761 -07:00 | 2534701103 | 253471103 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F990C16F-153F-43D6-8345-294A11CEC57C}
2664 | 2290 | {58406C40-671D-11E5-80CA-005056A729E5} | YOSEMITE | GUSTINE | Bank 1 | CB 1101 | PGE\BXYD | 2017-01-10 14:31:03.8863556 -08:00 | 1631101101 | 163111101 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 577 | 12.59 | 12.46 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {9302BD02-A115-471D-9C23-F4140883B6AB}
2665 | 2291 | {58406C4B-671D-11E5-80CA-005056A729E5} | YOSEMITE | GUSTINE | Bank 2 | CB 1102 | PGE\BXYD | 2017-01-10 14:38:09.7121444 -08:00 | 1631101102 | 163111102 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 515 | 578 | 600 | 711 | {AC4EDC70-CD0A-44E9-BBC7-1DECF833F167}
2666 | 2292 | {58406C59-671D-11E5-80CA-005056A729E5} | YOSEMITE | HAMMONDS | Bank 1 | CB 1101 | PGE\BXYD | 2017-01-10 14:23:54.8781056 -08:00 | 2534001101 | 253401101 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {17B5852B-97FF-4D6D-93A2-9311682EBB54}
2668 | 2292 | {58406C64-671D-11E5-80CA-005056A729E5} | YOSEMITE | HAMMONDS | Bank 1 | CB 1102 | PGE\BXYD | 2016-10-10 09:23:38.6092360 -07:00 | 2534001102 | 253401102 | 8 | 3 | 3 | 1 | 376 | 8.21 | 8.13 | 376 | 8.21 | 8.13 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {DDFB878B-4AAC-4B0D-87C3-D11BE05F23E0}
2669 | 2292 | {58406C6C-671D-11E5-80CA-005056A729E5} | YOSEMITE | HAMMONDS | Bank 1 | CB 1104 | PGE\BXYD | 2017-01-10 14:25:26.9354759 -08:00 | 2534001104 | 253401104 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {BB1073EE-41B6-484D-94B1-F62C12B76143}
2671 | 2294 | {58406C8C-671D-11E5-80CA-005056A729E5} | YOSEMITE | LE GRAND | Bank 1 | CB 1104 | PGE\SJJ8 | 2017-08-07 14:49:30.3803437 -07:00 | 2553601104 | 255361104 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 440 | 9.6 | 9.5 | 500 | 10.91 | 10.8 | 440 | 9.6 | 9.5 | 500 | 10.91 | 10.8 | 440 | 9.6 | 9.5 | 500 | 10.91 | 10.8 | 440 | 9.6 | 9.5 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {1056FF55-598A-48E6-8C34-A272A50485B2}
2672 | 2294 | {58406C91-671D-11E5-80CA-005056A729E5} | YOSEMITE | LE GRAND | Bank 1 | CB 1106 | PGE\SJJ8 | 2017-08-07 12:51:16.9889987 -07:00 | 2553601106 | 255361106 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {B8BCD59B-CCBF-4F1C-A086-4B2B45D3C06D}
2673 | 2294 | {58406C99-671D-11E5-80CA-005056A729E5} | YOSEMITE | LE GRAND | Bank 1 | CB 1110 | PGE\SJJ8 | 2017-08-07 14:56:38.9104782 -07:00 | 2553601110 | 255361110 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {02993D27-1CEE-41E3-BBD0-08890AA9BD7F}
2675 | 2293 | {B124890B-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | VASONA | Bank 1 | CB 1101 | PGE\IRB2 | 2016-10-10 10:47:52.4152610 -07:00 | 0837701101 | 083771101 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B7D081A8-B583-4969-8F4A-5B0583DDB521}
2676 | 2296 | {58406CC2-671D-11E5-80CA-005056A729E5} | YOSEMITE | LIVINGSTON | Bank 1 | CB 1106 | PGE\BXYD | 2016-10-10 10:26:37.0499653 -07:00 | 2522601106 | 252261106 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {251F394F-45CE-4C37-9B91-C32289369EF9}
2677 | 2297 | {58406CD0-671D-11E5-80CA-005056A729E5} | YOSEMITE | LIVINGSTON | Bank 2 | CB 1101 | PGE\BXYD | 2016-10-10 10:36:37.3401271 -07:00 | 2522601101 | 252261101 | 8 | 3 | 3 | 1 | 512 | 11.17 | 11.06 | 512 | 11.17 | 11.06 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 512 | 666 | 615 | 702 | {199A0917-5D7F-4045-8D17-E8BD60B6DF2F}
2678 | 2293 | {B124893F-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | VASONA | Bank 1 | CB 1102 | PGE\IRB2 | 2016-10-10 10:48:15.7068075 -07:00 | 0837701102 | 083771102 | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 582 | 12.7 | 12.57 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {C808C3CD-6C3F-48DD-B9C7-4C625DC70F84}
2679 | 2293 | {B1248956-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | VASONA | Bank 1 | CB 1103 | PGE\IRB2 | 2016-10-10 10:48:35.2860090 -07:00 | 0837701103 | 083771103 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9A174275-2395-46A9-86F1-B938D72D740F}
2680 | 2297 | {58406CE1-671D-11E5-80CA-005056A729E5} | YOSEMITE | LIVINGSTON | Bank 2 | CB 1102 | PGE\BXYD | 2016-10-10 10:43:27.5689466 -07:00 | 2522601102 | 252261102 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 512 | 666 | 615 | 702 | {44C3D07A-19C9-4B75-93F0-26E99EC3B25D}
2681 | 2293 | {B124896D-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | VASONA | Bank 1 | CB 1104 | PGE\IRB2 | 2016-10-10 10:49:04.6314900 -07:00 | 0837701104 | 083771104 | 8 | 4 | 4 | 2 | 534 | 11.65 | 11.53 | 534 | 11.65 | 11.53 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {4DBF9E15-D4F5-4084-9436-45CFA2223B96}
2683 | 2298 | {58406CF5-671D-11E5-80CA-005056A729E5} | YOSEMITE | MADERA | Bank 1 | CB 1112 | PGE\BXYD | 2016-10-10 10:52:30.1809636 -07:00 | 2527601112 | 252761112 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 916 | 1191 | 1100 | 1375 | {E83DF02F-764D-4A72-A497-D64ACBBED707}
2684 | 2298 | {58406CFD-671D-11E5-80CA-005056A729E5} | YOSEMITE | MADERA | Bank 1 | CB 1114 | PGE\BXYD | 2016-10-10 10:54:31.6934702 -07:00 | 2527601114 | 252761114 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 916 | 1191 | 1100 | 1375 | {1C78F96D-AA43-43CD-B768-68BF3A7901CD}
2685 | 2299 | {58406D0B-671D-11E5-80CA-005056A729E5} | YOSEMITE | MADERA | Bank 2 | CB 1102 | PGE\BXYD | 2016-10-10 11:00:52.2807765 -07:00 | 2527601102 | 252761102 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {1DD3BB7B-CF4F-4B57-9292-E9B2C1A949E2}
2686 | 2295 | {B738287C-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | VASONA | Bank 2 | CB 1105 | PGE\IRB2 | 2016-10-10 11:05:51.7946058 -07:00 | 0837701105 | 083771105 | 8 | 4 | 4 | 2 | 534 | 11.65 | 11.53 | 534 | 11.65 | 11.53 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {75666BA6-4A28-4112-B141-81575FFFA61A}
2687 | 2299 | {58406D10-671D-11E5-80CA-005056A729E5} | YOSEMITE | MADERA | Bank 2 | CB 1104 | PGE\BXYD | 2016-10-10 11:12:13.2536806 -07:00 | 2527601104 | 252761104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {1498A4B1-404A-460D-9915-2B12A0A6D3C6}
2688 | 2299 | {58406D15-671D-11E5-80CA-005056A729E5} | YOSEMITE | MADERA | Bank 2 | CB 1106 | PGE\BXYD | 2016-10-10 11:23:39.0003848 -07:00 | 2527601106 | 252761106 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {A347D4A7-3FE3-4279-93A9-DB8536562C07}
2689 | 2300 | {58406D23-671D-11E5-80CA-005056A729E5} | YOSEMITE | MADERA | Bank 3 | CB 1118 | PGE\BXYD | 2016-10-10 11:30:48.3049959 -07:00 | 2527601118 | 252761118 | 8 | 3 | 3 | 1 | 636 | 13.88 | 13.74 | 636 | 13.88 | 13.74 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F79C3A93-F447-4CB1-902C-6E73DE5B9083}
2690 | 2300 | {58406D2B-671D-11E5-80CA-005056A729E5} | YOSEMITE | MADERA | Bank 3 | CB 1119 | PGE\BXYD | 2016-10-10 11:48:19.0768774 -07:00 | 2527601119 | 252761119 | 8 | 3 | 3 | 1 | 636 | 13.88 | 13.74 | 636 | 13.88 | 13.74 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F914FC6F-5D5D-4B48-B65F-3995712D1BEA}
2692 | 2301 | {58406D42-671D-11E5-80CA-005056A729E5} | YOSEMITE | MARIPOSA | Bank 1 | CB 2101 | PGE\BXYD | 2016-11-08 15:58:35.5440494 -08:00 | 2544502101 | 254452101 | 12 | 3 | 3 | 1 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 |  |  | FALSE | FALSE | 423 | 486 | 486 | 486 | {1232A08F-F560-45C7-89BA-C4A2522343F9}
2693 | 2302 | {58406D5F-671D-11E5-80CA-005056A729E5} | YOSEMITE | MARIPOSA | Bank 2 | CB 2102 | PGE\BXYD | 2016-11-08 16:00:12.7207454 -08:00 | 2544502102 | 254452102 | 12 | 3 | 3 | 1 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 |  |  | FALSE | FALSE | 423 | 486 | 486 | 486 | {2A11AF18-C1D2-4080-AEF9-EAC70CE8390D}
2694 | 2295 | {B7382893-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | VASONA | Bank 2 | CB 1108 | PGE\IRB2 | 2016-10-10 12:58:22.3640452 -07:00 | 0837701108 | 083771108 | 8 | 4 | 4 | 2 | 534 | 11.65 | 11.53 | 534 | 11.65 | 11.53 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {FD526C08-1492-4A53-872E-80F27C601281}
2695 | 2303 | {5E3AA887-671D-11E5-80CA-005056A729E5} | YOSEMITE | MENDOTA | Bank 2 | CB 1101 | PGE\BXYD | 2016-10-10 13:01:22.0526145 -07:00 | 2523101101 | 252311101 | 8 | 3 | 3 | 1 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {E41F94B1-D825-4390-AE47-F99FBC84AC50}
2696 | 2303 | {5E3AA88C-671D-11E5-80CA-005056A729E5} | YOSEMITE | MENDOTA | Bank 2 | CB 1102 | PGE\BXYD | 2016-10-10 13:04:10.5869028 -07:00 | 2523101102 | 252311102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {95BA848E-669F-41F9-9AE0-4BB08F257526}
2697 | 2303 | {5E3AA897-671D-11E5-80CA-005056A729E5} | YOSEMITE | MENDOTA | Bank 2 | CB 1103 | PGE\BXYD | 2016-10-10 13:11:48.7057909 -07:00 | 2523101103 | 252311103 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {110E7CF7-7539-421F-A20B-40D355F5189C}
2698 | 2303 | {5E3AA89F-671D-11E5-80CA-005056A729E5} | YOSEMITE | MENDOTA | Bank 2 | CB 1104 | PGE\BXYD | 2016-10-10 13:15:24.5085756 -07:00 | 2523101104 | 252311104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {A6A4DFB2-1B58-4C95-9C38-54FA74A1FE71}
2699 | 2304 | {5E3AA8AD-671D-11E5-80CA-005056A729E5} | YOSEMITE | MERCED | Bank 1 | CB 2101 | PGE\BXYD | 2016-11-08 16:00:53.6098457 -08:00 | 2528002101 | 252802101 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {04CC6FBB-9424-4B75-9203-00DB98B6E931}
2700 | 2304 | {5E3AA8BB-671D-11E5-80CA-005056A729E5} | YOSEMITE | MERCED | Bank 1 | CB 2102 | PGE\BXYD | 2016-11-08 16:01:09.5223557 -08:00 | 2528002102 | 252802102 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {0C00E4F9-CBA2-44FF-8E2D-9CDC9089DC22}
2701 | 2305 | {5E3AA8D2-671D-11E5-80CA-005056A729E5} | YOSEMITE | MERCED | Bank 3 | CB 1108 | PGE\BXYD | 2016-10-10 13:37:06.7189049 -07:00 | 2528001108 | 252801108 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {53EC0812-F339-4351-B4AA-016E2D4370C8}
2702 | 2305 | {5E3AA8E3-671D-11E5-80CA-005056A729E5} | YOSEMITE | MERCED | Bank 3 | CB 1114 | PGE\BXYD | 2016-10-10 13:40:17.1227920 -07:00 | 2528001114 | 252801114 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {BD16DA41-C005-42F7-BF60-E24C2F7A9B41}
2703 | 2305 | {5E3AA8F7-671D-11E5-80CA-005056A729E5} | YOSEMITE | MERCED | Bank 3 | CB 1116 | PGE\BXYD | 2016-10-10 13:47:32.4673290 -07:00 | 2528001116 | 252801116 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {BAF928B8-222C-417F-B036-6E4E026D8EBA}
2704 | 2307 | {BF48EF6E-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | 8TH AVENUE | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-12 12:04:09.8689883 -08:00 | 012670401 | 012670401 | 4 | 3 | 3 | 2 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 396 | 3 | 2.97 | 396 | 3 | 2.97 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {9A8FE19B-85D1-47A7-8CF9-46837269ED3F}
2705 | 2306 | {5E3AA934-671D-11E5-80CA-005056A729E5} | YOSEMITE | MIWUK | Bank 1 | CB 1701 | PGE\BXYD | 2017-01-09 16:20:04.2246417 -08:00 | 1636601701 | 163661701 | 10 | 3 | 3 | 1 | 422 | 13.05 | 12.92 | 422 | 13.05 | 12.92 | 500 | 15.46 | 15.31 | 475 | 14.69 | 14.54 | 468 | 14.47 | 14.33 | 468 | 14.47 | 14.33 | 500 | 15.46 | 15.31 | 475 | 14.69 | 14.54 |  |  | FALSE | FALSE | 453 | 589 | 543 | 679 | {9C50661A-90C8-401B-89D6-9E3637D1D5A4}
2706 | 2306 | {5E3AA939-671D-11E5-80CA-005056A729E5} | YOSEMITE | MIWUK | Bank 1 | CB 1702 | PGE\BXYD | 2017-01-09 16:21:04.7538057 -08:00 | 1636601702 | 163661702 | 10 | 3 | 3 | 1 | 422 | 13.05 | 12.92 | 422 | 13.05 | 12.92 | 500 | 15.46 | 15.31 | 500 | 15.46 | 15.31 | 468 | 14.47 | 14.33 | 468 | 14.47 | 14.33 | 500 | 15.46 | 15.31 | 500 | 15.46 | 15.31 |  |  | FALSE | FALSE | 453 | 589 | 543 | 679 | {7F485796-0AFD-425E-9403-0B4714855351}
2707 | 2310 | {5E3AA947-671D-11E5-80CA-005056A729E5} | YOSEMITE | NEWHALL | Bank 2 | CB 1111 (Non-SCADA) | PGE\JWCp | 2017-02-24 11:23:28.0714208 -08:00 | 2544601111 | 254461111 | 8 | 3 | 3 | 1 | 650 | 14.19 | 14.05 | 617 | 13.47 | 13.34 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {CBE2092F-CA9C-4897-9042-6149EE0119FC}
2708 | 2311 | {892ACD4D-2F56-11E6-B38D-D4BED91EFF1A} | EAST BAY | BANCROFT | UNIT SUB 401 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-12 12:54:28.2091153 -08:00 | 013030401 | 013030401 | 4 | 3 | 3 | 2 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 396 | 3 | 2.97 | 396 | 3 | 2.97 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {1E74E580-1C49-4922-9048-E191224A66A8}
2709 | 2312 | {5E3AA953-671D-11E5-80CA-005056A729E5} | YOSEMITE | NEWHALL | Bank 3 | CB 1109 (Non-SCADA) | PGE\BXYD | 2016-11-28 16:53:58.8554513 -08:00 | 2544601109 | 254461109 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 549 | 714 | 659 | 824 | {245FD1E0-E5F3-4BA4-BF56-650B95C72FC3}
2710 | 2313 | {892ACD4A-2F56-11E6-B38D-D4BED91EFF1A} | EAST BAY | BANCROFT | UNIT SUB 402 (Non SCADA) | CB 402 (Non-SCADA) | PGE\C7CF | 2016-12-12 12:55:14.3715866 -08:00 | 013030402 | 013030402 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 455 | 3.44 | 3.41 | 455 | 3.44 | 3.41 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {FCC319EB-5AB6-4F4E-8CF2-83CE6FB1EA7A}
2711 | 2315 | {5E3AA974-671D-11E5-80CA-005056A729E5} | YOSEMITE | NEWMAN | Bank 2 | CB 1105 | PGE\BXYD | 2017-01-09 15:51:19.1278674 -08:00 | 1627401105 | 162741105 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {1EE0FB16-EE79-490B-A30C-FEC0FE4B15D3}
2712 | 2315 | {5E3AA985-671D-11E5-80CA-005056A729E5} | YOSEMITE | NEWMAN | Bank 2 | CB 1106 | PGE\BXYD | 2016-10-10 14:40:13.5954992 -07:00 | 1627401106 | 162741106 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F2E77A46-1525-4942-BC04-ECAA76E2FA8B}
2713 | 2316 | {806482BC-2F56-11E6-B38D-D4BED91EFF1A} | EAST BAY | BARRETT | UNIT SUB 401 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-12 12:58:55.4864668 -08:00 | 013020401 | 013020401 | 4 | 3 | 3 | 2 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 429 | 3.25 | 3.22 | 429 | 3.25 | 3.22 | 396 | 3 | 2.97 | 396 | 3 | 2.97 | 495 | 3.75 | 3.71 | 495 | 3.75 | 3.71 |  |  | FALSE | FALSE | 330 | 429 | 396 | 495 | {94A8C148-0BAE-4FA3-BC75-4CEB2D9C720F}
2714 | 2317 | {5E3AA999-671D-11E5-80CA-005056A729E5} | YOSEMITE | OAKHURST | Bank 1a | CB 1101 | PGE\BXYD | 2016-10-10 14:49:48.6552902 -07:00 | 2544201101 | 254421101 | 8 | 3 | 3 | 1 | 229 | 5 | 4.95 | 229 | 5 | 4.95 | 297 | 6.48 | 6.42 | 297 | 6.48 | 6.42 | 274 | 5.98 | 5.92 | 274 | 5.98 | 5.92 | 343 | 7.49 | 7.42 | 343 | 7.49 | 7.42 |  |  | FALSE | FALSE | 229 | 297 | 274 | 343 | {B9936AEF-5578-4BCF-9D5C-C83C2ECC43AE}
2715 | 2318 | {806482BF-2F56-11E6-B38D-D4BED91EFF1A} | EAST BAY | BARRETT | UNIT SUB 402 (Non SCADA) | CB 402 (Non-SCADA) | PGE\C7CF | 2016-12-12 13:01:29.2296143 -08:00 | 013020402 | 013020402 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 443 | 3.35 | 3.32 | 443 | 3.35 | 3.32 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {4ADCB7CA-B0A5-48DA-A535-1320B0EF47EF}
2716 | 2317 | {5E3AA99E-671D-11E5-80CA-005056A729E5} | YOSEMITE | OAKHURST | Bank 1a | CB 1102 | PGE\BXYD | 2016-10-10 14:51:35.5653261 -07:00 | 2544201102 | 254421102 | 8 | 3 | 3 | 1 | 229 | 5 | 4.95 | 229 | 5 | 4.95 | 297 | 6.48 | 6.42 | 297 | 6.48 | 6.42 | 274 | 5.98 | 5.92 | 274 | 5.98 | 5.92 | 343 | 7.49 | 7.42 | 343 | 7.49 | 7.42 |  |  | FALSE | FALSE | 229 | 297 | 274 | 343 | {04203737-CDA7-40CB-B0BF-2B8B7F174F85}
2717 | 2309 | {34A203B9-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | CHOLAME | Bank 1 | CB 1101 | PGE\MTDR | 2017-07-06 11:17:11.8595124 -07:00 | 1825601101 | 182561101 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 |  |  | FALSE | FALSE | 572 | 600 | 600 | 600 | {24E068B0-CAE5-4702-9016-6855C272CB67}
2718 | 2320 | {5E3AA9A9-671D-11E5-80CA-005056A729E5} | YOSEMITE | OAKHURST | Bank 2 | CB 1103 | PGE\BXYD | 2016-10-10 14:55:56.9302037 -07:00 | 2544201103 | 254421103 | 8 | 3 | 3 | 1 | 633 | 13.81 | 13.67 | 633 | 13.81 | 13.67 | 633 | 13.81 | 13.67 | 633 | 13.81 | 13.67 | 633 | 13.81 | 13.67 | 633 | 13.81 | 13.67 | 633 | 13.81 | 13.67 | 633 | 13.81 | 13.67 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {123B4BB7-BE1C-432D-90CE-82B239F2A9C2}
2719 | 2322 | {5E3AA9B7-671D-11E5-80CA-005056A729E5} | YOSEMITE | ORO LOMA | Bank 1 | CB 1106 | PGE\VxLa | 2017-02-14 08:19:23.7559300 -08:00 | 255371106 | 255371106 | 8 | 3 | 3 | 1 | 416 | 9.08 | 8.99 | 395 | 8.62 | 8.53 | 484 | 10.56 | 10.45 | 459 | 10.02 | 9.92 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {1E8233AE-95F3-4C11-9569-517E0A0AD2C6}
2720 | 2322 | {5E3AA9BF-671D-11E5-80CA-005056A729E5} | YOSEMITE | ORO LOMA | Bank 1 | CB 1108 | PGE\BXYD | 2016-10-10 15:02:27.6151047 -07:00 | 255371108 | 255371108 | 8 | 3 | 3 | 1 | 416 | 9.08 | 8.99 | 416 | 9.08 | 8.99 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {050DD672-EC7B-42DA-B3D3-07C0FD2EB8E3}
2721 | 2321 | {BF48EFA0-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | BECK STREET | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-12 13:04:12.0108319 -08:00 | 012640401 | 012640401 | 4 | 3 | 3 | 2 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 396 | 3 | 2.97 | 396 | 3 | 2.97 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 330 | 429 | 396 | 495 | {0686CC55-F901-47D9-BACC-AA4333C1CE08}
2722 | 2322 | {2717D644-A5BE-11E5-A1F0-D4BED91EFF1A} | YOSEMITE | ORO LOMA | Bank 1 | CB 1110 | PGE\BXYD | 2016-10-10 15:05:40.7475145 -07:00 | 255371110 | 255371110 | 8 | 3 | 3 | 1 | 435 | 9.49 | 9.4 | 435 | 9.49 | 9.4 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {59E1938A-1DCB-4F41-9853-D5CC460C9A7D}
2723 | 2322 | {5E3AA9CA-671D-11E5-80CA-005056A729E5} | YOSEMITE | ORO LOMA | Bank 1 | CB 1112 | PGE\BXYD | 2016-10-10 15:07:54.5062895 -07:00 | 255371112 | 255371112 | 8 | 3 | 3 | 1 | 435 | 9.49 | 9.4 | 435 | 9.49 | 9.4 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {4117893C-0A0A-427B-8A5A-59CA859B32BC}
2724 | 2324 | {34A203D3-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | CHOLAME | Bank 2 | CB 2102 | PGE\MTDR | 2017-07-06 13:47:23.5992292 -07:00 | 1825602102 | 182562102 | 12 | 3 | 3 | 2 | 330 | 12.47 | 12.35 | 330 | 12.47 | 12.35 | 400 | 15.12 | 14.97 | 380 | 14.36 | 14.22 | 396 | 14.97 | 14.82 | 380 | 14.36 | 14.22 | 400 | 15.12 | 14.97 | 380 | 14.36 | 14.22 |  |  | FALSE | FALSE | 330 | 429 | 396 | 486 | {30B8C7E2-9995-4238-B5C4-F89C7E53FB9D}
2725 | 2308 | {369796E3-671D-11E5-80CA-005056A729E5} | STOCKTON | EAST STOCKTON | Bank 3 | CB 1101 | PGE\BXYD | 2017-01-12 15:38:10.3441956 -08:00 | 1631301101 | 163131101 | 8 | 3 | 3 | 1 | 550 | 12 | 11.88 | 522 | 11.39 | 11.28 | 550 | 12 | 11.88 | 522 | 11.39 | 11.28 | 550 | 12 | 11.88 | 522 | 11.39 | 11.28 | 550 | 12 | 11.88 | 522 | 11.39 | 11.28 | 1. 2CU//1/0CU S/O SW 1013 sum nor = 373A, sum emer=428A; win nor=542A, win emer=577A. 4/29/13 SZC1 2. Update OH conductor new rating. 4/29/13 SZC1 |  | FALSE | FALSE | 733 | 818 | 818 | 818 | {D2AE6A3C-C002-4995-83D5-64319523E1E2}
2726 | 2308 | {369796F5-671D-11E5-80CA-005056A729E5} | STOCKTON | EAST STOCKTON | Bank 3 | CB 1102 | PGE\SZC1 | 2016-10-10 16:09:32.9725579 -07:00 | 1631301102 | 163131102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 1. Remove 14083 57HSB and update Trayer subsruface switch rating. 7/16/08 SZC1 2. Update OH conductor new rating. 4/29/13 SZC1 |  | FALSE | FALSE | 733 | 818 | 818 | 818 | {E9BA96FB-1ABF-4D20-B9F7-D4E2EBD5891E}
2727 | 2325 | {5E3AA9D5-671D-11E5-80CA-005056A729E5} | YOSEMITE | ORO LOMA | Bank 3 | CB 1115 | PGE\BXYD | 2016-10-10 15:30:38.2130610 -07:00 | 2553701115 | 255371115 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {FFFB51FE-E83C-487F-9835-30511B9B39E5}
2728 | 2325 | {5E3AA9DA-671D-11E5-80CA-005056A729E5} | YOSEMITE | ORO LOMA | Bank 3 | CB 1116 | PGE\BXYD | 2016-10-10 15:36:47.9910134 -07:00 | 2553701116 | 255371116 | 8 | 3 | 3 | 1 | 183 | 3.99 | 3.95 | 183 | 3.99 | 3.95 | 211 | 4.6 | 4.55 | 211 | 4.6 | 4.55 | 266 | 5.81 | 5.75 | 266 | 5.81 | 5.75 | 284 | 6.2 | 6.14 | 284 | 6.2 | 6.14 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {5D5C5C1A-6D60-4B6F-8C35-A5AEF5F7FE06}
2729 | 2325 | {5E3AA9DF-671D-11E5-80CA-005056A729E5} | YOSEMITE | ORO LOMA | Bank 3 | CB 1117 | PGE\BXYD | 2016-10-10 15:38:51.0177114 -07:00 | 2553701117 | 255371117 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {EEF56EFE-050A-4DE2-9313-889AF1BF7D76}
2730 | 2326 | {3AAAC542-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | CMC | Bank 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\A9S5 | 2016-11-11 08:53:16.0396949 -08:00 | 1831101101 | 183111101 | 8 | 3 | 3 | 2 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {8D02A002-1CF6-411E-B2DF-D7D03300B455}
2843 | 2393 | {1E0E9FD6-334D-11E6-B38D-D4BED91EFF1A} | EAST BAY | FAIRMOUNT | BANK 402 | CB 402 (Non-SCADA) | PGE\C7CF | 2016-12-12 14:51:42.8198152 -08:00 | 012650402 | 012650402 | 4 | 3 | 3 | 2 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 396 | 3 | 2.97 | 396 | 3 | 2.97 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {8651294A-ACCD-49D4-A919-1A6EC05CDE72}
2844 | 2330 | {A4579883-EB07-11E5-9614-9CB70D532D7F} | CENTRAL COAST | FORT ORD | Bank 2 | CB 2105 | PGE\ACT0 | 2016-11-23 12:09:20.3244829 -08:00 | 1824002105 | 182402105 | 22 | 3 | 3 | 2 | 369 | 13.28 | 13.15 | 369 | 13.28 | 13.15 | 414 | 14.9 | 14.75 | 414 | 14.9 | 14.75 | 415 | 14.94 | 14.79 | 415 | 14.94 | 14.79 | 443 | 15.94 | 15.78 | 443 | 15.94 | 15.78 | *Sheet not verified. |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1806 | {974608D5-78F0-48C7-A13A-BF958EE6097A}
2845 | 2394 | {79BD3362-2F56-11E6-B38D-D4BED91EFF1A} | EAST BAY | FLORENCE | UNIT SUB 401 | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-12 14:53:54.6851220 -08:00 | 012690401 | 012690401 | 4 | 3 | 3 | 2 | 319 | 2.41 | 2.39 | 319 | 2.41 | 2.39 | 414 | 3.13 | 3.1 | 414 | 3.13 | 3.1 | 383 | 2.9 | 2.87 | 383 | 2.9 | 2.87 | 478 | 3.62 | 3.58 | 478 | 3.62 | 3.58 |  |  | FALSE | FALSE | 319 | 414 | 383 | 478 | {79D3000E-2020-41AA-86D0-DEAFDC2C3E2A}
2847 | 2396 | {B93D8969-2F56-11E6-B38D-D4BED91EFF1A} | EAST BAY | HOLLYWOOD | UNIT SUB 401 | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-12 15:10:36.6762513 -08:00 | 013170401 | 013170401 | 4 | 3 | 3 | 2 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 396 | 3 | 2.97 | 396 | 3 | 2.97 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {D4307AAA-F1C1-4E93-9845-9CBD40690ACA}
2848 | 2330 | {DB485D86-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | FORT ORD | Bank 2 | CB 2106 | PGE\MTDR | 2017-07-18 08:46:38.6138996 -07:00 | 1824002106 | 182402106 | 12 | 3 | 3 | 2 | 205 | 7.75 | 7.67 | 194 | 7.33 | 7.26 | 230 | 8.69 | 8.6 | 218 | 8.24 | 8.16 | 230 | 8.69 | 8.6 | 218 | 8.24 | 8.16 | 231 | 8.73 | 8.64 | 231 | 8.73 | 8.64 |  |  | FALSE | FALSE | 600 | 600 | 600 | 600 | {80ACC01C-3488-46AE-84E2-720D2F16B3C2}
2849 | 2397 | {E1F1F996-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | MAPLE | Bank 1 (Non SCADA) | CB 401 | PGE\C7CF | 2016-12-12 15:27:20.3976174 -08:00 | 013520401 | 013520401 | 4 | 3 | 3 | 2 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 429 | 3.25 | 3.22 | 429 | 3.25 | 3.22 | 396 | 3 | 2.97 | 396 | 3 | 2.97 | 495 | 3.75 | 3.71 | 495 | 3.75 | 3.71 |  |  | FALSE | FALSE | 330 | 429 | 396 | 495 | {C52412F5-C97B-4209-8290-E52670440739}
2850 | 2330 | {E1A5F48D-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | FORT ORD | Bank 2 | CB 2108 | PGE\ACT0 | 2016-10-13 10:45:07.8880897 -07:00 | 1824002108 | 182402108 | 22 | 3 | 3 | 2 | 100 | 3.6 | 3.56 | 100 | 3.6 | 3.56 | 130 | 4.68 | 4.63 | 130 | 4.68 | 4.63 | 120 | 4.32 | 4.28 | 120 | 4.32 | 4.28 | 150 | 5.4 | 5.35 | 150 | 5.4 | 5.35 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1806 | {CCB919C6-DD17-41B9-9AF5-9053F546D13A}
2851 | 2398 | {E1F1F9A1-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | MIRA VISTA | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-12 15:39:26.2669672 -08:00 | 012330401 | 012330401 | 4 | 3 | 3 | 2 | 416 | 3.15 | 3.12 | 416 | 3.15 | 3.12 | 458 | 3.47 | 3.44 | 458 | 3.47 | 3.44 | 428 | 3.24 | 3.21 | 428 | 3.24 | 3.21 | 471 | 3.57 | 3.53 | 471 | 3.57 | 3.53 |  |  | FALSE | FALSE | 528 | 687 | 634 | 792 | {FF7B4CD1-7557-48A0-A7E6-8F64CFFAEEB8}
2852 | 2399 | {E1F1F9AA-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | MIRA VISTA | BANK 403 (Non SCADA) | CB 403 (Non-SCADA) | PGE\C7CF | 2016-12-12 15:40:53.1142205 -08:00 | 012330403 | 012330403 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 455 | 3.44 | 3.41 | 455 | 3.44 | 3.41 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {734CC992-3CED-4116-A0CC-A7992C69975C}
2853 | 2400 | {E1F1F9B3-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAK | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-12 15:47:11.6895585 -08:00 | 012600401 | 012600401 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {D72E41C4-1D46-4494-A217-AC3202209999}
2854 | 2402 | {E1F1F9E6-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND C | BANK 10 | CB 1109 | PGE\C7CF | 2016-10-19 16:48:28.5510724 -07:00 | 0120101109 | 012011109 | 8 | 3 | 3 | 2 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 504 | 11 | 10.89 | 504 | 11 | 10.89 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 519 | 11.33 | 11.22 | 519 | 11.33 | 11.22 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {25F4757D-1D2D-4002-B31F-3550DBC870CC}
2855 | 2402 | {E806531C-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND C | BANK 10 | CB 1113 | PGE\C7CF | 2016-12-12 16:42:31.9291730 -08:00 | 0120101113 | 012011113 | 8 | 3 | 3 | 2 | 455 | 9.93 | 9.83 | 455 | 9.93 | 9.83 | 529 | 11.54 | 11.42 | 529 | 11.54 | 11.42 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 540 | 11.78 | 11.66 | 540 | 11.78 | 11.66 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {C2A2EC2B-D104-4FD4-9FB6-E0103C00D9EC}
2857 | 2402 | {EE149228-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND C | BANK 10 | CB 1114 | PGE\C7CF | 2016-12-12 16:42:00.0261209 -08:00 | 0120101114 | 012011114 | 8 | 3 | 3 | 2 | 525 | 11.46 | 11.35 | 525 | 11.46 | 11.35 | 588 | 12.83 | 12.7 | 588 | 12.83 | 12.7 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {2D961CBC-23C8-4953-8FEC-AEE20EAE0B82}
2858 | 2402 | {EE14923C-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND C | BANK 10 | CB 1115 | PGE\C7CF | 2016-12-12 16:44:19.7392958 -08:00 | 0120101115 | 012011115 | 8 | 3 | 3 | 2 | 426 | 9.3 | 9.21 | 426 | 9.3 | 9.21 | 479 | 10.45 | 10.35 | 479 | 10.45 | 10.35 | 459 | 10.02 | 9.92 | 459 | 10.02 | 9.92 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {D7CC2E46-C863-4D6D-A4DC-8323DA131879}
2859 | 2402 | {EE14924A-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND C | BANK 10 | CB 1117 | PGE\C7CF | 2016-10-19 16:49:43.2314897 -07:00 | 0120101117 | 012011117 | 8 | 3 | 3 | 2 | 408 | 8.9 | 8.81 | 180 | 3.93 | 3.89 | 453 | 9.89 | 9.79 | 180 | 3.93 | 3.89 | 420 | 9.17 | 9.08 | 180 | 3.93 | 3.89 | 466 | 10.17 | 10.07 | 180 | 3.93 | 3.89 | The other limit represents 5MW crane power reserved for Port over harbor POO 231A |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {5CEF1EB6-3DB0-46A3-A070-40FA686395B5}
2860 | 2406 | {2FE3CABB-671D-11E5-80CA-005056A729E5} | STOCKTON | ALPINE | Bank 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\BXYD | 2017-01-17 10:53:17.0302310 -08:00 | 1635601101 | 163561101 | 8 | 3 | 3 | 1 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 |  |  | FALSE | FALSE | 158 | 205 | 189 | 212 | {2222677D-D449-4955-9176-61AFDA77FD57}
2861 | 2406 | {2FE3CABE-671D-11E5-80CA-005056A729E5} | STOCKTON | ALPINE | Bank 1 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\BXYD | 2017-01-17 10:53:44.2995554 -08:00 | 1635601102 | 163561102 | 8 | 3 | 3 | 1 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 |  |  | FALSE | FALSE | 158 | 205 | 189 | 212 | {232F1C00-C1C8-46E5-88C4-6503749D08B4}
2862 | 2405 | {CB6B590A-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | PETALUMA C | Bank 3 | CB 1105 | PGE\DCGa | 2016-11-03 11:28:22.4347033 -07:00 | 0426301105 | 042631105 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | TRUE | 1374 | 1787 | 1649 | 2061 | {F6B74AB0-5D59-4BE8-B8E3-99799DF9AB0A}
2863 | 2405 | {CB6B5913-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | PETALUMA C | Bank 3 | CB 1106 | PGE\DCGa | 2016-11-02 14:56:28.5771839 -07:00 | 0426301106 | 042631106 | 8 | 2 | 2 | 1 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | TRUE | 1374 | 1787 | 1649 | 2061 | {F03BFBC8-0402-493B-9005-F48F2E64AF79}
2864 | 2405 | {CB6B591C-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | PETALUMA C | Bank 3 | CB 1108 | PGE\DCGa | 2017-01-11 09:23:10.7472834 -08:00 | 0426301108 | 042631108 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 566 | 12.35 | 12.23 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | TRUE | 1374 | 1787 | 1649 | 2061 | {B5315110-C47C-4C38-9142-4603D1FA6384}
2865 | 2402 | {91CB252F-6004-11E6-9BE4-80000BC6CD8D} | EAST BAY | OAKLAND C | BANK 10 | CB 1119 | PGE\C7CF | 2016-10-19 16:51:04.7555776 -07:00 | 012011119 | 012011119 | 8 | 3 | 3 | 2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 370 | 8.07 | 7.99 | 370 | 8.07 | 7.99 | 343 | 7.49 | 7.42 | 343 | 7.49 | 7.42 | 381 | 8.31 | 8.23 | 381 | 8.31 | 8.23 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9D0A5581-1CA4-4583-A537-B69EDA3C2714}
2731 | 2325 | {5E3AA9E7-671D-11E5-80CA-005056A729E5} | YOSEMITE | ORO LOMA | Bank 3 | CB 1118 | PGE\BXYD | 2017-01-09 15:25:33.7153485 -08:00 | 2553701118 | 255371118 | 8 | 3 | 3 | 1 | 258 | 5.63 | 5.57 | 245 | 5.35 | 5.3 | 288 | 6.29 | 6.23 | 273 | 5.96 | 5.9 | 329 | 7.18 | 7.11 | 312 | 6.81 | 6.74 | 351 | 7.66 | 7.58 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {D385B29D-C587-42AE-B688-752FCF896A6C}
2732 | 2326 | {3AAAC545-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | CMC | Bank 1 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\A9S5 | 2016-11-11 08:53:30.4856509 -08:00 | 1831101102 | 183111102 | 8 | 3 | 3 | 2 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {75186921-99F3-4DF4-895D-B7DED466C108}
2733 | 2327 | {5E3AA9F8-671D-11E5-80CA-005056A729E5} | YOSEMITE | ORTIGA | Bank 1 | CB 1105 | PGE\APE3 | 2017-07-20 15:42:36.7412482 -07:00 | 2543101105 | 254311105 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 489 | 10.67 | 10.56 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {AFA22548-3060-4B0C-B6C8-87CC621E2540}
2734 | 2327 | {5E3AAA03-671D-11E5-80CA-005056A729E5} | YOSEMITE | ORTIGA | Bank 1 | CB 1106 | PGE\BXYD | 2017-01-09 14:24:35.6010015 -08:00 | 2543101106 | 254311106 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 489 | 10.67 | 10.56 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {249E3BEC-FDC0-45F7-92C0-32B014DCABC7}
2735 | 2329 | {369796DA-671D-11E5-80CA-005056A729E5} | STOCKTON | EAST STOCKTON | Bank 1 | CB 401 (Non-SCADA) | PGE\BXYD | 2017-01-12 15:28:22.0332244 -08:00 | 163130401 | 163130401 | 3 | 3 | 3 | 1 | 578 | 4.16 | 4.12 | 570 | 4.11 | 4.07 | 600 | 4.32 | 4.28 | 600 | 4.32 | 4.28 | 600 | 4.32 | 4.28 | 570 | 4.11 | 4.07 | 600 | 4.32 | 4.28 | 600 | 4.32 | 4.28 | 1. Update OH conductor new rating. 5/1/13 SZC1 |  | FALSE | FALSE | 1165 | 1515 | 1398 | 1748 | {A4DAA0E7-2A0B-4342-B6C2-1B6E79053AC9}
2736 | 2331 | {5E3AAA14-671D-11E5-80CA-005056A729E5} | YOSEMITE | PEORIA FLAT | Bank 1 | CB 1701 | PGE\BXYD | 2017-01-09 14:01:02.9782362 -08:00 | 1637801701 | 163781701 | 10 | 3 | 3 | 1 | 407 | 12.58 | 12.45 | 407 | 12.58 | 12.45 | 529 | 16.36 | 16.2 | 529 | 16.36 | 16.2 | 489 | 15.12 | 14.97 | 489 | 15.12 | 14.97 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 |  |  | FALSE | FALSE | 407 | 529 | 489 | 611 | {EE6A1892-591D-44FD-AC41-2682DC324549}
2737 | 2329 | {369796DD-671D-11E5-80CA-005056A729E5} | STOCKTON | EAST STOCKTON | Bank 1 | CB 402 (Non-SCADA) | PGE\BXYD | 2017-01-12 15:29:35.8372975 -08:00 | 163130402 | 163130402 | 3 | 3 | 3 | 1 | 517 | 3.73 | 3.69 | 517 | 3.73 | 3.69 | 517 | 3.73 | 3.69 | 517 | 3.73 | 3.69 | 517 | 3.73 | 3.69 | 517 | 3.73 | 3.69 | 517 | 3.73 | 3.69 | 517 | 3.73 | 3.69 | 1. Update OH conductor new rating. 5/1/13 SZC1 |  | FALSE | FALSE | 1165 | 1515 | 1398 | 1748 | {6B01A9B9-F69B-4246-90B8-8B86C52F290A}
2738 | 2332 | {5E3AAA2B-671D-11E5-80CA-005056A729E5} | YOSEMITE | PEORIA FLAT | Bank 2 | CB 1704 | PGE\BXYD | 2016-10-10 16:58:00.3728811 -07:00 | 1637801704 | 163781704 | 10 | 3 | 3 | 1 | 515 | 15.92 | 15.76 | 515 | 15.92 | 15.76 | 578 | 17.87 | 17.69 | 578 | 17.87 | 17.69 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 |  |  | FALSE | FALSE | 1455 | 1892 | 1746 | 2183 | {33C8F0D2-B9C5-42F0-A2C2-90220AEA61AA}
2739 | 2332 | {5E3AAA45-671D-11E5-80CA-005056A729E5} | YOSEMITE | PEORIA FLAT | Bank 2 | CB 1705 | PGE\BXYD | 2016-10-10 16:59:39.7483629 -07:00 | 1637801705 | 163781705 | 10 | 3 | 3 | 1 | 515 | 15.92 | 15.76 | 515 | 15.92 | 15.76 | 578 | 17.87 | 17.69 | 578 | 17.87 | 17.69 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 |  |  | FALSE | FALSE | 1455 | 1892 | 1746 | 2183 | {D207003A-6054-4169-A07C-95A2F67BD6E3}
2740 | 2336 | {5E3AAA77-671D-11E5-80CA-005056A729E5} | YOSEMITE | RACETRACK | Bank 1 | CB 1703 (Non-SCADA) | PGE\BXYD | 2017-01-09 13:51:57.2485416 -08:00 | 1637601703 | 163761703 | 10 | 3 | 3 | 1 | 517 | 15.98 | 15.82 | 517 | 15.98 | 15.82 | 667 | 20.62 | 20.41 | 667 | 20.62 | 20.41 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 667 | 20.62 | 20.41 | 667 | 20.62 | 20.41 |  |  | FALSE | FALSE | 517 | 672 | 621 | 676 | {B8078BC7-9D35-483E-83A7-BDB37C8A2460}
2741 | 2336 | {5E3AAA7F-671D-11E5-80CA-005056A729E5} | YOSEMITE | RACETRACK | Bank 1 | CB 1704 | PGE\BXYD | 2017-01-09 13:53:38.3540859 -08:00 | 1637601704 | 163761704 | 10 | 3 | 3 | 1 | 517 | 15.98 | 15.82 | 517 | 15.98 | 15.82 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 |  |  | FALSE | FALSE | 517 | 672 | 621 | 676 | {FFFD254A-8F99-4D2F-90F4-2B720547B4CD}
2742 | 2328 | {B8F4803B-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | WILLOW PASS | Bank 1 | CB 1101 | PGE\WCL5 | 2016-11-09 17:24:52.7409408 -08:00 | 0139101101 | 013911101 | 8 | 3 | 3 | 1 | 481 | 10 | 9.9 | 481 | 10 | 9.9 | 500 | 10.39 | 10.29 | 500 | 10.39 | 10.29 | 500 | 10.39 | 10.29 | 500 | 10.39 | 10.29 | 500 | 10.39 | 10.29 | 500 | 10.39 | 10.29 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {5E27D31D-A6DB-4A9D-A860-9236E9E61A9D}
2743 | 2328 | {B8F48040-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | WILLOW PASS | Bank 1 | CB 1102 | PGE\WCL5 | 2016-11-09 17:25:14.2840660 -08:00 | 0139101102 | 013911102 | 8 | 3 | 3 | 1 | 481 | 10 | 9.9 | 481 | 10 | 9.9 | 500 | 10.39 | 10.29 | 500 | 10.39 | 10.29 | 500 | 10.39 | 10.29 | 500 | 10.39 | 10.29 | 500 | 10.39 | 10.29 | 500 | 10.39 | 10.29 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {019B596F-939F-4A65-84B7-B1E5F198EB19}
2744 | 2337 | {643D9815-671D-11E5-80CA-005056A729E5} | YOSEMITE | RIVERBANK | Bank 2 | CB 1713 | PGE\JLDe | 2017-05-25 12:33:28.5175251 -07:00 | 1631901713 | 163191713 | 10 | 3 | 3 | 1 | 578 | 17.87 | 17.69 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 |  |  | FALSE | FALSE | 1455 | 1892 | 1746 | 2183 | {4AAB6896-0C98-47A7-8996-9D7C7E5696F7}
2745 | 2337 | {643D9829-671D-11E5-80CA-005056A729E5} | YOSEMITE | RIVERBANK | Bank 2 | CB 1715 | PGE\BXYD | 2016-10-11 08:10:29.7030627 -07:00 | 1631901715 | 163191715 | 10 | 3 | 3 | 1 | 515 | 15.92 | 15.76 | 515 | 15.92 | 15.76 | 578 | 17.87 | 17.69 | 578 | 17.87 | 17.69 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 |  |  | FALSE | FALSE | 1455 | 1892 | 1746 | 2183 | {E333A6EA-DD9B-45D9-BD18-4C3C411414DA}
2746 | 2337 | {643D9840-671D-11E5-80CA-005056A729E5} | YOSEMITE | RIVERBANK | Bank 2 | CB 1716 | PGE\BXYD | 2016-10-11 08:16:06.9413299 -07:00 | 1631901716 | 163191716 | 10 | 3 | 3 | 1 | 515 | 15.92 | 15.76 | 515 | 15.92 | 15.76 | 578 | 17.87 | 17.69 | 578 | 17.87 | 17.69 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 |  |  | FALSE | FALSE | 1455 | 1892 | 1746 | 2183 | {61668804-E29C-4A0C-B9FC-9A08FFC1872C}
2748 | 2338 | {5E3AAA68-671D-11E5-80CA-005056A729E5} | YOSEMITE | SAN JOAQUIN #3 PH | Bank 2 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\BXYD | 2016-10-11 08:42:54.3041681 -07:00 | 2525301101 | 252531101 | 8 | 2 | 2 | 1 | 316 | 6.9 | 6.83 | 316 | 6.9 | 6.83 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 316 | 411 | 379 | 474 | {9053BDAE-05DF-4944-AD0B-A9ACE8341F9D}
2749 | 2338 | {5E3AAA6B-671D-11E5-80CA-005056A729E5} | YOSEMITE | SAN JOAQUIN #3 PH | Bank 2 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\BXYD | 2016-10-11 08:40:22.4473767 -07:00 | 2525301102 | 252531102 | 8 | 2 | 2 | 1 | 282 | 6.15 | 6.09 | 282 | 6.15 | 6.09 | 315 | 6.87 | 6.8 | 315 | 6.87 | 6.8 | 358 | 7.81 | 7.73 | 358 | 7.81 | 7.73 | 382 | 8.34 | 8.26 | 382 | 8.34 | 8.26 |  |  | FALSE | FALSE | 316 | 411 | 379 | 474 | {61FF1710-25AE-48E5-A9AC-479EB2E5A77E}
2750 | 2338 | {5E3AAA6E-671D-11E5-80CA-005056A729E5} | YOSEMITE | SAN JOAQUIN #3 PH | Bank 2 (Non SCADA) | CB 1103 (Non-SCADA) | PGE\JWCp | 2017-04-24 10:32:08.9732268 -07:00 | 2525301103 | 252531103 | 8 | 2 | 2 | 1 | 183 | 3.99 | 3.95 | 173 | 3.78 | 3.74 | 211 | 4.6 | 4.55 | 200 | 4.36 | 4.32 | 230 | 5.02 | 4.97 | 230 | 5.02 | 4.97 | 230 | 5.02 | 4.97 | 230 | 5.02 | 4.97 |  |  | FALSE | FALSE | 316 | 411 | 379 | 474 | {2B1FA6BE-DF6B-4F60-8E87-F7768ABFFB2B}
2751 | 2339 | {643D985A-671D-11E5-80CA-005056A729E5} | YOSEMITE | SANTA NELLA | Bank 1 | CB 1101 (Non-SCADA) | PGE\BXYD | 2017-01-09 11:09:03.6178713 -08:00 | 2540501101 | 254051101 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {28E98AA6-C803-4E4D-8413-3C888B0CAC70}
2752 | 2340 | {643D9866-671D-11E5-80CA-005056A729E5} | YOSEMITE | SANTA NELLA | Bank 2 | CB 1104 | PGE\SJJ8 | 2017-07-03 15:18:50.4398017 -07:00 | 2540501104 | 254051104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {565F764E-52B1-4FF6-A085-17238C603450}
2753 | 2342 | {CF39CA75-275F-11E6-B38D-D4BED91EFF1A} | YOSEMITE | SANTA RITA | Bank 1 | CB 1102 | PGE\BXYD | 2016-10-11 09:58:30.0276554 -07:00 | 2535401102 | 253541102 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 512 | 666 | 615 | 702 | {C542B631-16C4-4040-B3C2-940C6A055B29}
2754 | 2342 | {D613FBCC-275F-11E6-B38D-D4BED91EFF1A} | YOSEMITE | SANTA RITA | Bank 1 | CB 1105 | PGE\BXYD | 2016-10-11 09:59:35.4241936 -07:00 | 2535401105 | 253541105 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 512 | 666 | 615 | 702 | {E1D26C1C-1635-470B-A8AD-724A7EC9296E}
2755 | 2344 | {2FE3CB30-671D-11E5-80CA-005056A729E5} | STOCKTON | CHANNEL | Bank 1 | CB 1101 | PGE\BXYD | 2017-01-12 17:19:52.6353126 -08:00 | 1630701101 | 163071101 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 |  |  | FALSE | FALSE | 572 | 721 | 687 | 721 | {24F20167-B852-4604-AC6F-B5A21895AB47}
2756 | 2344 | {2FE3CB35-671D-11E5-80CA-005056A729E5} | STOCKTON | CHANNEL | Bank 1 | CB 1102 | PGE\BXYD | 2017-01-12 17:24:25.1846597 -08:00 | 1630701102 | 163071102 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 |  |  | FALSE | FALSE | 572 | 721 | 687 | 721 | {55051FDC-29EC-4BEE-9479-F2179EA4B575}
2758 | 2346 | {2FE3CB43-671D-11E5-80CA-005056A729E5} | STOCKTON | CHEROKEE | Bank 1 | CB 1101 | PGE\BXYD | 2017-01-12 17:13:10.4335344 -08:00 | 1636501101 | 163651101 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 |  |  | FALSE | FALSE | 733 | 953 | 879 | 962 | {41F0444B-E0D5-43AD-8FF4-A97AEAFBF5BB}
2759 | 2346 | {2FE3CB4E-671D-11E5-80CA-005056A729E5} | STOCKTON | CHEROKEE | Bank 1 | CB 1102 | PGE\BXYD | 2017-01-12 17:14:41.3821174 -08:00 | 1636501102 | 163651102 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 |  |  | FALSE | FALSE | 733 | 953 | 879 | 962 | {9FA96256-0A2F-4B0B-A436-88A6D436A3DD}
2760 | 2347 | {5A8ACAD9-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | BIG RIVER | Bank 1 | CB 1101 | PGE\DCGa | 2017-08-07 11:48:08.1891667 -07:00 | 0430801101 | 043081101 | 8 | 3 | 3 | 2 | 354 | 7.73 | 7.65 | 229 | 5 | 4.95 | 354 | 7.73 | 7.65 | 298 | 6.5 | 6.43 | 354 | 7.73 | 7.65 | 275 | 6 | 5.94 | 354 | 7.73 | 7.65 | 344 | 7.51 | 7.43 | QA COMPLETED BY C8M4 ON 5/31/2017 |  | FALSE | TRUE | 229 | 298 | 275 | 344 | {4186D45E-728C-432D-A6C7-3C347F28B886}
2761 | 2343 | {2FE3CB89-671D-11E5-80CA-005056A729E5} | STOCKTON | COLONY | Bank 2 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\SKA1 | 2016-10-11 15:20:50.7226192 -07:00 | 1622301101 | 162231101 | 8 | 3 | 3 | 1 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 |  |  | FALSE | FALSE | 263 | 343 | 316 | 395 | {0C731BD7-318F-4193-9DB4-03D1F5495C63}
2762 | 2348 | {B91E8528-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | COTATI | Bank 1 | CB 1102 | PGE\C8M4 | 2016-11-03 21:50:10.7044191 -07:00 | 0422701102 | 042271102 | 8 | 2 | 2 | 1 | 575 | 12.55 | 12.42 | 286 | 6.24 | 6.18 | 600 | 13.09 | 12.96 | 372 | 8.12 | 8.04 | 600 | 13.09 | 12.96 | 343 | 7.49 | 7.42 | 600 | 13.09 | 12.96 | 429 | 9.36 | 9.27 |  |  | FALSE | TRUE | 286 | 372 | 343 | 429 | {43CFDC4F-7F1F-43FD-A23F-A6925445550E}
2763 | 2343 | {2FE3CB8C-671D-11E5-80CA-005056A729E5} | STOCKTON | COLONY | Bank 2 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\SKA1 | 2016-10-11 15:23:02.5753674 -07:00 | 1622301102 | 162231102 | 8 | 3 | 3 | 2 | 263 | 5.74 | 5.68 | 263 | 5.74 | 5.68 | 317 | 6.92 | 6.85 | 317 | 6.92 | 6.85 | 316 | 6.9 | 6.83 | 316 | 6.9 | 6.83 | 317 | 6.92 | 6.85 | 317 | 6.92 | 6.85 |  |  | FALSE | FALSE | 263 | 343 | 316 | 395 | {A46D30DC-EA1E-416B-89D7-BF108CA4A563}
2764 | 2348 | {B91E8586-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | COTATI | Bank 1 | CB 1103 | PGE\DCGa | 2017-03-16 06:55:31.7648330 -07:00 | 0422701103 | 042271103 | 8 | 2 | 2 | 1 | 533 | 11.63 | 11.51 | 164 | 3.58 | 3.54 | 533 | 11.63 | 11.51 | 214 | 4.67 | 4.62 | 533 | 11.63 | 11.51 | 197 | 4.3 | 4.26 | 533 | 11.63 | 11.51 | 247 | 5.39 | 5.34 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {70283FC8-F6E8-46B1-9821-14DAC903CB1A}
2765 | 2350 | {2FE3CB98-671D-11E5-80CA-005056A729E5} | STOCKTON | CORRAL | Bank 1 | CB 1101 | PGE\SKA1 | 2016-10-11 15:24:30.1430276 -07:00 | 1629901101 | 162991101 | 8 | 3 | 3 | 1 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {117156D2-BD8F-4888-B175-D6C6E045B7E3}
2766 | 2351 | {369797DD-671D-11E5-80CA-005056A729E5} | STOCKTON | HAMMER | Bank 2 | CB 1104 | PGE\BXYD | 2017-01-12 14:47:28.2466951 -08:00 | 1633001104 | 163301104 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1239 | 1482 | 1649 | 2061 | {8844A9F7-9AD4-49AA-BD2E-349B4EFA2336}
2767 | 2350 | {2FE3CBB2-671D-11E5-80CA-005056A729E5} | STOCKTON | CORRAL | Bank 1 | CB 1103 | PGE\SKA1 | 2016-10-11 15:24:51.3902656 -07:00 | 1629901103 | 162991103 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {29CC7CB3-3D57-405B-BEBA-0C7B90FD9ED6}
2768 | 2349 | {B91E85BC-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | COTATI | Bank 2 | CB 1104 | PGE\DCGa | 2017-07-19 07:44:27.7544410 -07:00 | 0422701104 | 042271104 | 8 | 2 | 2 | 1 | 575 | 12.55 | 12.42 | 481 | 10.5 | 10.39 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Done by ZJC1 7/1/2008 |  | FALSE | TRUE | 481 | 625 | 577 | 721 | {F3F400C0-62B2-44E2-8AA7-5C4012DFD5FD}
2769 | 2349 | {B91E85F6-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | COTATI | Bank 2 | CB 1105 | PGE\DCGa | 2017-07-19 07:44:40.3906030 -07:00 | 0422701105 | 042271105 | 8 | 2 | 2 | 1 | 500 | 10.91 | 10.8 | 481 | 10.5 | 10.39 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | TRUE | 481 | 625 | 577 | 721 | {B444511B-9BB3-40C8-BEAE-039E64A92E74}
2771 | 2353 | {2FE3CBC6-671D-11E5-80CA-005056A729E5} | STOCKTON | CORRAL | Bank 2 | CB 1102 | PGE\SKA1 | 2016-10-11 15:25:41.6392874 -07:00 | 1629901102 | 162991102 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {FCF5B692-99A7-4FC3-A728-5404E43312B9}
2772 | 2354 | {5A8ACB5F-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | CALPELLA | Bank 1 | CB 1101 | PGE\D5LZ | 2017-08-04 15:46:24.1260648 -07:00 | 0434101101 | 043411101 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | TRUE | 733 | 800 | 800 | 800 | {B1EE39B6-53E7-4582-83BC-AC3C135BE331}
2773 | 2354 | {5A8ACB68-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | CALPELLA | Bank 1 | CB 1102 | PGE\D5LZ | 2017-08-04 14:38:57.4343673 -07:00 | 0434101102 | 043411102 | 8 | 3 | 3 | 1 | 573 | 12.51 | 12.38 | 544 | 11.87 | 11.75 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | TRUE | 733 | 800 | 800 | 800 | {648BB4DA-3056-4040-9AE9-A074F7160ADA}
2774 | 2356 | {643D98A7-671D-11E5-80CA-005056A729E5} | YOSEMITE | SPRING GAP | BANK 1 (Non SCADA) | CB 1701 (Non-SCADA) | PGE\BXYD | 2017-01-09 09:46:07.8255754 -08:00 | 1628301701 | 162831701 | 10 | 3 | 3 | 1 | 154 | 4.76 | 4.71 | 146 | 4.51 | 4.46 | 173 | 5.35 | 5.3 | 164 | 5.07 | 5.02 | 180 | 5.57 | 5.51 | 180 | 5.57 | 5.51 | 180 | 5.57 | 5.51 | 180 | 5.57 | 5.51 |  |  | FALSE | FALSE | 180 | 180 | 180 | 180 | {DAAACF19-BAD3-4AC7-9E00-BF348BB9730A}
2775 | 2357 | {643D98B6-671D-11E5-80CA-005056A729E5} | YOSEMITE | STOREY | Bank 1 | CB 1104 | PGE\KRBk | 2016-12-06 11:20:44.0049836 -08:00 | 2546101104 | 254611104 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 2767 | {B8322B0C-A8EF-4736-BCD3-B4EFF267D56E}
2776 | 2357 | {643D98C1-671D-11E5-80CA-005056A729E5} | YOSEMITE | STOREY | Bank 1 | CB 1105 | PGE\KRBk | 2016-12-06 11:34:18.5570038 -08:00 | 2546101105 | 254611105 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 670 | 14.62 | 14.47 | 670 | 14.62 | 14.47 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 670 | 14.62 | 14.47 | 670 | 14.62 | 14.47 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 2767 | {6EADDC63-EF0B-4688-90E3-04D98DD13EE3}
2777 | 2357 | {643D98CC-671D-11E5-80CA-005056A729E5} | YOSEMITE | STOREY | Bank 1 | CB 1106 | PGE\KRBk | 2016-12-06 11:42:06.9081122 -08:00 | 2546101106 | 254611106 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 2767 | {C3C98C68-96F6-459C-89E4-A54B7FB3019D}
2778 | 2358 | {643D98DA-671D-11E5-80CA-005056A729E5} | YOSEMITE | STOREY | Bank 2 | CB 1107 | PGE\KRBk | 2016-12-07 09:27:19.0820773 -08:00 | 2546101107 | 254611107 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 2767 | {A798B31A-DA8F-494A-B340-CAA0DCE50370}
2779 | 2358 | {643D98F7-671D-11E5-80CA-005056A729E5} | YOSEMITE | STOREY | Bank 2 | CB 1108 | PGE\KRBk | 2016-12-07 09:43:04.0297182 -08:00 | 2546101108 | 254611108 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 2767 | {B7C608AC-7930-458F-B426-D388D2C25F98}
2780 | 2358 | {643D990B-671D-11E5-80CA-005056A729E5} | YOSEMITE | STOREY | Bank 2 | CB 1109 | PGE\JWCp | 2017-06-06 10:09:25.3018595 -07:00 | 2546101109 | 254611109 | 8 | 3 | 3 | 1 | 650 | 14.19 | 14.05 | 494 | 10.78 | 10.67 | 700 | 15.28 | 15.13 | 494 | 10.78 | 10.67 | 700 | 15.28 | 15.13 | 494 | 10.78 | 10.67 | 700 | 15.28 | 15.13 | 494 | 10.78 | 10.67 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 2767 | {07198632-633A-41FC-AE0A-99D1506FC84D}
2781 | 2358 | {643D9925-671D-11E5-80CA-005056A729E5} | YOSEMITE | STOREY | Bank 2 | CB 1111 | PGE\KRBk | 2016-12-07 14:20:24.4104071 -08:00 | 2546101111 | 254611111 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 670 | 14.62 | 14.47 | 670 | 14.62 | 14.47 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 670 | 14.62 | 14.47 | 670 | 14.62 | 14.47 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 2767 | {C0EAB324-8B87-43F8-94AE-DA8365CC8459}
2782 | 2361 | {643D995C-671D-11E5-80CA-005056A729E5} | YOSEMITE | VALLEY HOME | Bank 1 | CB 1702 (Non-SCADA) | PGE\BXYD | 2016-10-12 08:43:22.0179186 -07:00 | 1629801702 | 162981702 | 10 | 3 | 3 | 1 | 186 | 5.75 | 5.69 | 186 | 5.75 | 5.69 | 242 | 7.48 | 7.41 | 242 | 7.48 | 7.41 | 223 | 6.89 | 6.82 | 223 | 6.89 | 6.82 | 279 | 8.63 | 8.54 | 279 | 8.63 | 8.54 |  |  | FALSE | FALSE | 186 | 242 | 223 | 279 | {110B474C-5453-446F-B6B4-C999BB7B4B36}
2783 | 2362 | {2717D652-A5BE-11E5-A1F0-D4BED91EFF1A} | YOSEMITE | VALLEY HOME | Bank 2 | CB 1703 | PGE\JCD5 | 2017-05-23 15:21:21.9530474 -07:00 | 1629801703 | 162981703 | 10 | 3 | 3 | 1 | 483 | 14.93 | 14.78 | 483 | 14.93 | 14.78 | 483 | 14.93 | 14.78 | 483 | 14.93 | 14.78 | 483 | 14.93 | 14.78 | 483 | 14.93 | 14.78 | 483 | 14.93 | 14.78 | 483 | 14.93 | 14.78 |  |  | FALSE | FALSE | 800 | 800 | 800 | 800 | {B5E4F3EC-C8B6-4142-B587-BE8D4D6F863C}
2784 | 2362 | {2717D655-A5BE-11E5-A1F0-D4BED91EFF1A} | YOSEMITE | VALLEY HOME | Bank 2 | CB 1704 | PGE\JCD5 | 2017-05-23 15:26:36.8999790 -07:00 | 1629801704 | 162981704 | 10 | 3 | 3 | 1 | 325 | 10.05 | 9.95 | 308 | 9.52 | 9.42 | 350 | 10.82 | 10.71 | 344 | 10.64 | 10.53 | 350 | 10.82 | 10.71 | 350 | 10.82 | 10.71 | 350 | 10.82 | 10.71 | 350 | 10.82 | 10.71 |  |  | FALSE | FALSE | 800 | 800 | 800 | 800 | {52FFAB7E-7531-492B-9000-88B4590DCAF7}
2785 | 2363 | {643D996A-671D-11E5-80CA-005056A729E5} | YOSEMITE | WESTLEY | Bank 1 | CB 1101 (Non-SCADA) | PGE\BXYD | 2017-01-09 09:19:02.7787585 -08:00 | 1626701101 | 162671101 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 480 | 10.48 | 10.38 | 456 | 9.95 | 9.85 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 480 | 10.48 | 10.38 | 456 | 9.95 | 9.85 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {58288F58-A968-430D-A323-9BE02EF1EDE8}
2786 | 2363 | {643D9976-671D-11E5-80CA-005056A729E5} | YOSEMITE | WESTLEY | Bank 1 | CB 90110 (Non-SCADA) | PGE\BXYD | 2016-10-12 09:06:01.9465282 -07:00 | 162671102 | 162671102 | 8 | 3 | 3 | 1 | 572 | 12.48 | 12.36 | 572 | 12.48 | 12.36 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {00000000-0000-0000-0000-000000000000}
2787 | 2364 | {643D997F-671D-11E5-80CA-005056A729E5} | YOSEMITE | WESTLEY | Bank 2 | CB 1103 | PGE\BXYD | 2016-10-12 09:10:21.4462687 -07:00 | 1626701103 | 162671103 | 8 | 3 | 3 | 1 | 345 | 7.53 | 7.45 | 345 | 7.53 | 7.45 | 386 | 8.42 | 8.34 | 386 | 8.42 | 8.34 | 443 | 9.67 | 9.57 | 443 | 9.67 | 9.57 | 473 | 10.32 | 10.22 | 473 | 10.32 | 10.22 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {CC7B9215-C9C2-4C31-9F57-24F5091189AD}
2788 | 2365 | {5A8ACB94-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | CARLOTTA | Bank 1 | CB 1121 | PGE\D5LZ | 2017-08-04 18:16:24.9518671 -07:00 | 1922901121 | 192291121 | 8 | 3 | 3 | 2 | 137 | 2.99 | 2.96 | 137 | 2.99 | 2.96 | 179 | 3.91 | 3.87 | 178 | 3.88 | 3.84 | 165 | 3.6 | 3.56 | 164 | 3.58 | 3.54 | 206 | 4.5 | 4.46 | 200 | 4.36 | 4.32 | No capability sheet exists |  | FALSE | TRUE | 137 | 178 | 164 | 200 | {2411DD7F-F744-41D0-B9B2-78EBCC8BA2D2}
2789 | 2366 | {5A8ACBC6-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | CLEAR LAKE | Bank 1 | CB 1101 | PGE\C8M4 | 2016-11-18 11:44:19.8744080 -08:00 | 0421401101 | 042141101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 223 | 4.87 | 4.82 | 600 | 13.09 | 12.96 | 248 | 5.41 | 5.36 | 600 | 13.09 | 12.96 | 283 | 6.18 | 6.12 | 600 | 13.09 | 12.96 | 302 | 6.59 | 6.52 |  |  | FALSE | TRUE | 429 | 558 | 515 | 644 | {8BED71FA-4000-4B08-BCA4-CFC418DE7467}
2791 | 2367 | {61248239-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | CLEAR LAKE | Bank 2 | CB 1102 | PGE\C8M4 | 2016-11-18 11:46:02.6150860 -08:00 | 0421401102 | 042141102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 400 | 8.73 | 8.64 | 600 | 13.09 | 12.96 | 447 | 9.76 | 9.66 | 600 | 13.09 | 12.96 | 514 | 11.22 | 11.11 | 600 | 13.09 | 12.96 | 549 | 11.98 | 11.86 |  |  | FALSE | TRUE | 481 | 625 | 577 | 721 | {E5C7949A-D464-4F93-ABC9-860B90C99B42}
2792 | 2368 | {B2D1763B-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | CLOVERDALE | Bank 1 | CB 1101 (Non-SCADA) | PGE\C8M4 | 2016-11-03 17:51:08.6760498 -07:00 | 0428201101 | 042821101 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | TRUE | 859 | 1116 | 1030 | 1288 | {E4917E6F-1BA6-4862-A8C9-4C8A7009E9E7}
2793 | 2370 | {643D999C-671D-11E5-80CA-005056A729E5} | YOSEMITE | WILSON | Bank 3 | CB 1101 (Non-SCADA) | PGE\BXYD | 2016-10-12 10:54:03.4363062 -07:00 | 2543001101 | 254301101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {1C40643B-9B78-46F6-A72D-6F1BE7169527}
2794 | 2368 | {B2D1764B-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | CLOVERDALE | Bank 1 | CB 1102 (Non-SCADA) | PGE\C8M4 | 2016-11-03 17:56:18.0632376 -07:00 | 0428201102 | 042821102 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | TRUE | 859 | 1116 | 1030 | 1288 | {6F0D5676-09CD-435B-AF58-B3E40944E2A7}
2795 | 2370 | {643D999F-671D-11E5-80CA-005056A729E5} | YOSEMITE | WILSON | Bank 3 | CB 1102 (Non-SCADA) | PGE\JLDe | 2016-12-08 10:52:58.7161849 -08:00 | 2543001102 | 254301102 | 8 | 3 | 3 | 1 | 320 | 6.98 | 6.91 | 320 | 6.98 | 6.91 | 320 | 6.98 | 6.91 | 320 | 6.98 | 6.91 | 320 | 6.98 | 6.91 | 320 | 6.98 | 6.91 | 320 | 6.98 | 6.91 | 320 | 6.98 | 6.91 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {ED1E8CBA-6314-4697-BB86-C173510B8DC5}
2796 | 2370 | {643D99A8-671D-11E5-80CA-005056A729E5} | YOSEMITE | WILSON | Bank 3 | CB 1103 (Non-SCADA) | PGE\BXYD | 2016-10-12 10:57:15.2075212 -07:00 | 2543001103 | 254301103 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {E1362826-FC18-4B75-BE8F-5F1C78177C14}
2797 | 2369 | {6A24FF69-2F56-11E6-B38D-D4BED91EFF1A} | EAST BAY | BERKELEY T | BANK 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-10-19 16:37:34.5115091 -07:00 | 012660401 | 012660401 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 660 | 858 | 792 | 990 | {432FF9E3-5DC0-4FD8-8537-C7E84FA5C1B0}
2798 | 2369 | {5DF94328-2F56-11E6-B38D-D4BED91EFF1A} | EAST BAY | BERKELEY T | BANK 1 (Non SCADA) | CB 404 (Non-SCADA) | PGE\C7CF | 2016-10-19 16:37:49.6119214 -07:00 | 012660404 | 012660404 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 660 | 858 | 792 | 990 | {89CE60BC-81F5-479F-864A-5FB668B9F151}
2799 | 2371 | {731CEA50-2F56-11E6-B38D-D4BED91EFF1A} | EAST BAY | BERKELEY T | BANK 2 (Non SCADA) | CB 402 (Non-SCADA) | PGE\C7CF | 2016-12-12 13:08:57.3120421 -08:00 | 012660402 | 012660402 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 660 | 858 | 792 | 990 | {1AD21920-D2A8-425E-8B3B-2BF91735CBCD}
2800 | 2351 | {369797E3-671D-11E5-80CA-005056A729E5} | STOCKTON | HAMMER | Bank 2 | CB 1105 | PGE\BXYD | 2017-01-12 14:49:10.5989512 -08:00 | 1633001105 | 163301105 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1239 | 1482 | 1649 | 2061 | {4F9E3CC6-AEA1-4F8E-9FA1-407C792B4456}
2801 | 2351 | {369797E8-671D-11E5-80CA-005056A729E5} | STOCKTON | HAMMER | Bank 2 | CB 1106 | PGE\BXYD | 2017-01-12 14:49:40.8007448 -08:00 | 1633001106 | 163301106 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1239 | 1482 | 1649 | 2061 | {E77FD709-2294-446E-A572-110D43365E70}
2802 | 2371 | {731CEA4D-2F56-11E6-B38D-D4BED91EFF1A} | EAST BAY | BERKELEY T | BANK 2 (Non SCADA) | CB 403 (Non-SCADA) | PGE\C7CF | 2016-12-12 13:08:02.6033857 -08:00 | 012660403 | 012660403 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 660 | 858 | 792 | 990 | {29CDD0E5-2692-43F2-BEA6-CCCB69005938}
2803 | 2372 | {718347CA-0B43-11E6-9D37-D4BED91EFF1A} | YOSEMITE | CHENEY | BANK 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\BXYD | 2016-10-12 11:29:20.1377120 -07:00 | 2535601101 | 253561101 | 8 | 3 | 3 | 1 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {8436743B-988E-4044-8613-E6DD65E361A1}
2804 | 2372 | {662A1D42-DCCB-11E5-83B3-2016D89D35F7} | YOSEMITE | CHENEY | BANK 1 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\BXYD | 2016-10-12 11:30:47.8429627 -07:00 | 2535601102 | 253561102 | 8 | 3 | 3 | 1 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {E6CEC806-D8FA-451B-8D25-AF6CABBA3F62}
2805 | 2372 | {718347D0-0B43-11E6-9D37-D4BED91EFF1A} | YOSEMITE | CHENEY | BANK 1 (Non SCADA) | CB 1103 (Non-SCADA) | PGE\BXYD | 2016-10-12 11:31:56.7348420 -07:00 | 2535601103 | 253561103 | 8 | 3 | 3 | 1 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {D58FCFDF-B89D-45B0-AC8A-D13B1463F5EA}
2806 | 2373 | {F151BD6E-2F56-11E6-B38D-D4BED91EFF1A} | EAST BAY | BROOKSIDE | UNIT SUB 401 | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-12 13:10:47.2200014 -08:00 | 013210401 | 013210401 | 4 | 3 | 3 | 2 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 396 | 3 | 2.97 | 396 | 3 | 2.97 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {F16C6FEF-0E46-4A87-AB9A-CEE50C249E36}
2807 | 2375 | {B91E862C-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | DUNBAR | Bank 1 | CB 1102 | PGE\C8M4 | 2016-10-12 12:53:29.1060660 -07:00 | 0430701102 | 043071102 | 8 | 2 | 2 | 1 | 223 | 4.87 | 4.82 | 223 | 4.87 | 4.82 | 248 | 5.41 | 5.36 | 248 | 5.41 | 5.36 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 302 | 6.59 | 6.52 | 302 | 6.59 | 6.52 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {208A7E7C-03BA-4DE2-868A-D991B01C1F82}
2808 | 2375 | {B91E8635-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | DUNBAR | Bank 1 | CB 1103 | PGE\C8M4 | 2016-10-12 12:56:20.7679456 -07:00 | 0430701103 | 043071103 | 8 | 2 | 2 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 490 | 10.69 | 10.58 | 490 | 10.69 | 10.58 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {398F7352-168C-4B56-ABEC-8D03CC2CF16E}
2809 | 2376 | {B91E864B-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | DUNBAR | Bank 2 | CB 1101 | PGE\C8M4 | 2016-10-12 13:12:45.6323199 -07:00 | 0430701101 | 043071101 | 8 | 2 | 2 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Done by ZJc1 7/1/2010 |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {8F9FFCD5-82C3-4924-A891-2DBE25F11F44}
2810 | 2374 | {BF48EFB2-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | EDES | Bank 2 | CB 1101 | PGE\C7CF | 2016-10-19 16:39:03.4595272 -07:00 | 0136801101 | 013681101 | 8 | 3 | 3 | 2 | 525 | 11.46 | 11.35 | 525 | 11.46 | 11.35 | 588 | 12.83 | 12.7 | 588 | 12.83 | 12.7 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {457CF19E-861C-44EB-81C2-7897DAD21DAE}
2811 | 2374 | {C8E99F7F-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | EDES | Bank 2 | CB 1103 | PGE\C7CF | 2016-10-19 16:39:13.8839344 -07:00 | 0136801103 | 013681103 | 8 | 3 | 3 | 2 | 478 | 10.43 | 10.33 | 478 | 10.43 | 10.33 | 531 | 11.59 | 11.47 | 531 | 11.59 | 11.47 | 492 | 10.74 | 10.63 | 492 | 10.74 | 10.63 | 546 | 11.92 | 11.8 | 546 | 11.92 | 11.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {777D32CE-C7BE-4490-BF74-FA072E344EB2}
2812 | 2374 | {C8E99F93-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | EDES | Bank 2 | CB 1104 | PGE\C7CF | 2016-12-12 13:17:49.3631464 -08:00 | 0136801104 | 013681104 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {444D093A-91B5-4A97-A89A-D5F9F7162E06}
2813 | 2374 | {C8E99F98-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | EDES | Bank 2 | CB 1105 | PGE\C7CF | 2016-12-12 13:18:37.8457189 -08:00 | 0136801105 | 013681105 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {94BC764D-799D-4134-ADDF-754B1C5CFAA3}
2814 | 2378 | {612482A6-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | EEL RIVER | Bank 1 | CB 1102 | PGE\DCGa | 2017-02-02 14:20:59.0405429 -08:00 | 1923801102 | 192381102 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 321 | 7.01 | 6.94 | 600 | 13.09 | 12.96 | 360 | 7.86 | 7.78 | 600 | 13.09 | 12.96 | 358 | 7.81 | 7.73 | 600 | 13.09 | 12.96 | 382 | 8.34 | 8.26 |  |  | FALSE | TRUE | 429 | 558 | 515 | 600 | {B2EB4A1C-1AF7-47C8-A744-29230897408C}
2816 | 2377 | {C8E99FA3-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | EDES | Bank 3 | CB 1110 | PGE\C7CF | 2016-12-12 13:23:02.3513884 -08:00 | 0136801110 | 013681110 | 8 | 3 | 3 | 2 | 445 | 9.71 | 9.61 | 445 | 9.71 | 9.61 | 494 | 10.78 | 10.67 | 494 | 10.78 | 10.67 | 458 | 10 | 9.9 | 458 | 10 | 9.9 | 509 | 11.11 | 11 | 509 | 11.11 | 11 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {115CF060-9471-4E4A-A301-C98248337099}
2817 | 2379 | {F648DC4B-275C-11E6-B38D-D4BED91EFF1A} | HUMBOLDT | EEL RIVER | Bank 2 | CB 1103 | PGE\JLDe | 2016-12-16 15:09:38.6796127 -08:00 | 1923801103 | 192381103 | 8 | 3 | 3 | 2 | 533 | 11.63 | 11.51 | 391 | 8.53 | 8.44 | 533 | 11.63 | 11.51 | 440 | 9.6 | 9.5 | 533 | 11.63 | 11.51 | 443 | 9.67 | 9.57 | 533 | 11.63 | 11.51 | 473 | 10.32 | 10.22 |  |  | FALSE | TRUE | 733 | 953 | 879 | 1099 | {15DB5D33-A1D3-464A-A69E-85BFA7F98CF8}
2818 | 2377 | {C8E99FA8-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | EDES | Bank 3 | CB 1111 | PGE\C7CF | 2016-12-12 13:23:34.5770882 -08:00 | 0136801111 | 013681111 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 592 | 12.92 | 12.79 | 592 | 12.92 | 12.79 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 599 | 13.07 | 12.94 | 599 | 13.07 | 12.94 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {6DF229DC-7493-468F-AEE8-4C23DE13F796}
2819 | 2377 | {CF8EA078-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | EDES | Bank 3 | CB 1112 | PGE\C7CF | 2016-12-12 13:24:17.2138013 -08:00 | 0136801112 | 013681112 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 592 | 12.92 | 12.79 | 592 | 12.92 | 12.79 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 599 | 13.07 | 12.94 | 599 | 13.07 | 12.94 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {08EE9F4D-FCCC-4173-8EE4-3D161D4FB9EA}
2820 | 2377 | {CF8EA09B-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | EDES | Bank 3 | CB 1113 | PGE\C7CF | 2016-12-12 13:24:42.0032034 -08:00 | 0136801113 | 013681113 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9EC8210F-7224-40F2-A488-D5B81F7B6356}
2821 | 2377 | {CF8EA0A3-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | EDES | Bank 3 | CB 1114 | PGE\C7CF | 2016-12-12 13:25:26.9173038 -08:00 | 0136801114 | 013681114 | 8 | 3 | 3 | 2 | 478 | 10.43 | 10.33 | 478 | 10.43 | 10.33 | 531 | 11.59 | 11.47 | 531 | 11.59 | 11.47 | 492 | 10.74 | 10.63 | 492 | 10.74 | 10.63 | 546 | 11.92 | 11.8 | 546 | 11.92 | 11.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {CEF66C02-2BD3-45DC-86E5-AFD6CCB1B63A}
2823 | 2377 | {D5CDDA43-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | EDES | Bank 3 | CB 1115 | PGE\C7CF | 2016-12-12 13:26:01.5033906 -08:00 | 0136801115 | 013681115 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {218AFFBD-5B35-4C91-BDE3-85BD580628C9}
2824 | 2385 | {7A8F23FA-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | WILLOW CREEK | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-12 15:57:10.8791344 -07:00 | 1921701101 | 192171101 | 8 | 2 | 2 | 1 | 223 | 4.87 | 4.82 | 223 | 4.87 | 4.82 | 248 | 5.41 | 5.36 | 248 | 5.41 | 5.36 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 302 | 6.59 | 6.52 | 302 | 6.59 | 6.52 |  |  | FALSE | FALSE | 481 | 481 | 481 | 481 | {96D1C8BD-F117-413C-AA29-CAE571881E34}
2825 | 2385 | {7A8F2419-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | WILLOW CREEK | Bank 1 | CB 1102 | PGE\C8M4 | 2016-10-12 16:00:00.1928750 -07:00 | 1921701102 | 192171102 | 8 | 2 | 2 | 1 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 |  |  | FALSE | FALSE | 481 | 481 | 481 | 481 | {DEC4C857-4362-4CE5-A1EB-7A6A976D2957}
2826 | 2386 | {5E3AAA5F-671D-11E5-80CA-005056A729E5} | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | Bank 2 (Non SCADA) | CB 1103 (Non-SCADA) | PGE\BXYD | 2016-10-12 16:01:59.8078930 -07:00 | 2525201103 | 252521103 | 8 | 3 | 3 | 1 | 143 | 3.12 | 3.09 | 143 | 3.12 | 3.09 | 186 | 4.06 | 4.02 | 186 | 4.06 | 4.02 | 171 | 3.73 | 3.69 | 171 | 3.73 | 3.69 | 190 | 4.15 | 4.11 | 190 | 4.15 | 4.11 |  |  | FALSE | FALSE | 143 | 186 | 171 | 214 | {B9C6A18A-1C1B-4451-BA3B-696D0734CDB7}
2827 | 2385 | {7A8F2429-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | WILLOW CREEK | Bank 1 | CB 1103 | PGE\C8M4 | 2016-10-12 16:02:06.1878664 -07:00 | 1921701103 | 192171103 | 8 | 2 | 2 | 1 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 |  |  | FALSE | FALSE | 481 | 481 | 481 | 481 | {8D9E8410-7A41-4B05-AE9C-054647CF52A7}
2829 | 2387 | {7A8F23C4-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | WILLITS | Bank 1 | CB 1102 | PGE\C8M4 | 2016-10-12 16:33:04.2919815 -07:00 | 0426601102 | 042661102 | 8 | 2 | 2 | 2 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | Done by: ZJC1 10/2015 |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {B91A866E-7B60-4913-BE12-DDEC7D616881}
2830 | 2387 | {7A8F23D4-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | WILLITS | Bank 1 | CB 1103 | PGE\C8M4 | 2016-10-12 16:43:53.0997968 -07:00 | 0426601103 | 042661103 | 8 | 2 | 2 | 2 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | ZJC1 2015 |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {B99C7871-103E-4392-AD28-7EC4931A4F2D}
2831 | 2387 | {7A8F23E4-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | WILLITS | Bank 1 | CB 1104 | PGE\C8M4 | 2016-10-12 16:43:10.4666636 -07:00 | 0426601104 | 042661104 | 8 | 2 | 2 | 2 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | ZJC1 2015 |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {BCA24863-354E-42E3-8DC9-F7BA914D7B79}
2832 | 2389 | {CB6B58E7-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | PETALUMA C | Bank 2 | CB 1101 | PGE\C8M4 | 2016-10-13 08:39:10.8306193 -07:00 | 0426301101 | 042631101 | 8 | 2 | 2 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {F6079450-408B-4769-8374-758AB801FA72}
2833 | 2389 | {CB6B58F0-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | PETALUMA C | Bank 2 | CB 1102 | PGE\C8M4 | 2016-10-13 08:52:27.5018990 -07:00 | 0426301102 | 042631102 | 8 | 2 | 2 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | ZJC1 2010 |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {3E2C6A6F-D34B-4BAE-91AB-B680E23BF2EA}
2834 | 2390 | {B91B8E28-671D-11E5-80CA-005056A729E5} | FRESNO | COPPERMINE | Bank 1 | CB 1104 | PGE\BXYD | 2017-01-24 10:41:27.8370934 -08:00 | 2524101104 | 252411104 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 916 | 1191 | 1100 | 1200 | {81A62806-0765-49F3-A684-51C10E0802CA}
2835 | 2390 | {B91B8E3C-671D-11E5-80CA-005056A729E5} | FRESNO | COPPERMINE | Bank 1 | CB 1106 | PGE\BXYD | 2016-11-28 17:07:16.9835391 -08:00 | 2524101106 | 252411106 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 916 | 1191 | 1100 | 1375 | {B2F5C343-B4A8-41D2-AE44-1FBB3F7E759A}
2836 | 2390 | {2717D5AB-A5BE-11E5-A1F0-D4BED91EFF1A} | FRESNO | COPPERMINE | Bank 1 | CB 1110 | PGE\BXYD | 2017-01-24 10:43:56.7244478 -08:00 | 252411110 | 252411110 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 916 | 1191 | 1100 | 1200 | {39086FC9-2CA1-497E-8B7D-62130E8FCDAB}
2837 | 2390 | {B91B8E47-671D-11E5-80CA-005056A729E5} | FRESNO | COPPERMINE | Bank 1 | CB 1112 | PGE\BXYD | 2017-01-24 10:44:32.9790802 -08:00 | 2524101112 | 252411112 | 8 | 3 | 3 | 1 | 282 | 6.15 | 6.09 | 267 | 5.83 | 5.77 | 315 | 6.87 | 6.8 | 299 | 6.53 | 6.46 | 358 | 7.81 | 7.73 | 340 | 7.42 | 7.35 | 382 | 8.34 | 8.26 | 362 | 7.9 | 7.82 |  |  | FALSE | FALSE | 916 | 1191 | 1100 | 1200 | {EBCDAB72-899A-458E-969D-17815B920DCB}
2838 | 2391 | {B91B8DF9-671D-11E5-80CA-005056A729E5} | FRESNO | COALINGA NO 2 | Bank 1 | CB 1104 | PGE\JCS9 | 2016-12-15 15:27:00.0867351 -08:00 | 2523801104 | 252381104 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {F208C53F-F2AA-413F-ACAA-602C07608864}
2839 | 2391 | {B91B8DFE-671D-11E5-80CA-005056A729E5} | FRESNO | COALINGA NO 2 | Bank 1 | CB 1105 | PGE\JCS9 | 2016-12-15 15:35:00.5401266 -08:00 | 2523801105 | 252381105 | 8 | 3 | 3 | 1 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {3DBAEA11-C2B4-49D9-9148-B3CD7C37AD13}
2840 | 2391 | {B91B8E0F-671D-11E5-80CA-005056A729E5} | FRESNO | COALINGA NO 2 | Bank 1 | CB 1106 | PGE\JCS9 | 2016-12-15 15:34:46.8896016 -08:00 | 2523801106 | 252381106 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {955321E3-0BA5-4A5E-B769-97FEED42B37D}
2841 | 2391 | {B91B8E17-671D-11E5-80CA-005056A729E5} | FRESNO | COALINGA NO 2 | Bank 1 | CB 1107 | PGE\JCS9 | 2016-12-15 15:28:29.1960810 -08:00 | 2523801107 | 252381107 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {BD73B6D6-2E39-4468-B34E-FDEB77E3EA84}
2842 | 2392 | {1E0E9FD9-334D-11E6-B38D-D4BED91EFF1A} | EAST BAY | FAIRMOUNT | UNIT SUB 401 | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-12 14:52:25.8914152 -08:00 | 012650401 | 012650401 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 438 | 3.32 | 3.29 | 438 | 3.32 | 3.29 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {206554B5-A564-4186-99C0-A4933D53C92F}
2866 | 2407 | {E7DF13E0-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | GONZALES | Bank 3 | CB 1101 (Non-SCADA) | PGE\ACT0 | 2016-10-13 13:44:26.3167099 -07:00 | 1821301101 | 182131101 | 8 | 2 | 2 | 2 | 307 | 6.7 | 6.63 | 307 | 6.7 | 6.63 | 399 | 8.71 | 8.62 | 399 | 8.71 | 8.62 | 368 | 8.03 | 7.95 | 368 | 8.03 | 7.95 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 307 | 399 | 368 | 460 | {00000000-0000-0000-0000-000000000000}
2867 | 2407 | {E7DF13E9-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | GONZALES | Bank 3 | CB 1102 (Non-SCADA) | PGE\ACT0 | 2016-10-13 13:46:32.0327657 -07:00 | 1821301102 | 182131102 | 8 | 2 | 2 | 2 | 307 | 6.7 | 6.63 | 307 | 6.7 | 6.63 | 399 | 8.71 | 8.62 | 399 | 8.71 | 8.62 | 368 | 8.03 | 7.95 | 368 | 8.03 | 7.95 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 307 | 399 | 368 | 460 | {00000000-0000-0000-0000-000000000000}
2868 | 2408 | {EF0AF5C0-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | GONZALES | Bank 4 | CB 1103 | PGE\ACT0 | 2016-11-23 12:59:17.0541328 -08:00 | 1821301103 | 182131103 | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 582 | 12.7 | 12.57 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {7CA1BE0C-C3F8-4234-B5B1-9E9AE285122C}
2869 | 2408 | {EF0AF5C8-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | GONZALES | Bank 4 | CB 1104 | PGE\ACT0 | 2016-11-23 12:59:08.2710513 -08:00 | 1821301104 | 182131104 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {C05F0EE8-AE45-4E33-881E-7EFCB00DAACD}
2870 | 2409 | {EF0AF5E2-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | GREEN VALLEY | Bank 2 | CB 2102 | PGE\JLDe | 2016-12-12 08:51:31.1124140 -08:00 | 0831902102 | 083192102 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {67DF9C29-8313-47B5-A200-DBD27922F1F5}
2871 | 2409 | {F53966D1-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | GREEN VALLEY | Bank 2 | CB 2103 | PGE\ACT0 | 2016-10-13 14:17:22.0681275 -07:00 | 0831902103 | 083192103 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {0CF62E5A-1219-445C-85DE-CA7AD3BBC620}
2872 | 2410 | {C9E29CE6-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN LEANDRO | Bank 1 | CB 1101 | PGE\RDR1 | 2017-05-10 14:27:32.1821320 -07:00 | 0131101101 | 013111101 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | U1101 substation outlet has been upgraded from 750Cu P&L to 1100Al EPR cable in 2015 initiated by PM# 30866456 & has been completed under PM# 31109438 |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {82F52100-EF6A-4495-9E78-3704DCB379DD}
2873 | 2411 | {FC5124BD-78E8-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | GREEN VALLEY | Bank 3 | CB 2101 | PGE\ACT0 | 2016-10-13 14:30:10.0705592 -07:00 | 0831902101 | 083192101 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {93586C54-175B-4630-B0C6-E1EDF1C11C44}
2874 | 2411 | {029AE5C0-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | GREEN VALLEY | Bank 3 | CB 2104 | PGE\ACT0 | 2016-11-23 09:38:39.4097421 -08:00 | 0831902104 | 083192104 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {D1A59FA5-2552-4F83-A3BF-A78861E1487F}
2875 | 2402 | {F4276517-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND C | BANK 10 | CB 1134 | PGE\C7CF | 2016-10-19 16:51:14.2259309 -07:00 | 0120101134 | 012011134 | 8 | 3 | 3 | 2 | 390 | 8.51 | 8.42 | 250 | 5.46 | 5.41 | 433 | 9.45 | 9.36 | 250 | 5.46 | 5.41 | 402 | 8.77 | 8.68 | 250 | 5.46 | 5.41 | 446 | 9.73 | 9.63 | 250 | 5.46 | 5.41 | 3MW power reserved for EMBMUD generation 139A |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {4DFAA457-E98C-4E88-899E-848A9D5738E8}
2876 | 2402 | {675E61E0-2F52-11E6-B38D-D4BED91EFF1A} | EAST BAY | OAKLAND C | BANK 10 | CB 1108 | PGE\C7CF | 2016-12-12 16:39:33.3792303 -08:00 | 0120101108 | 012011108 | 8 | 3 | 3 | 2 | 581 | 12.68 | 12.55 | 581 | 12.68 | 12.55 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {6B8463A2-2DD7-4DA7-81F8-DA449F454187}
2877 | 2403 | {E1F1F9BC-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND C | Bank 2 | CB 1111 | PGE\C7CF | 2016-10-19 17:02:37.9388003 -07:00 | 012011111 | 012011111 | 8 | 3 | 3 | 2 | 390 | 8.51 | 8.42 | 390 | 8.51 | 8.42 | 433 | 9.45 | 9.36 | 433 | 9.45 | 9.36 | 402 | 8.77 | 8.68 | 402 | 8.77 | 8.68 | 446 | 9.73 | 9.63 | 446 | 9.73 | 9.63 |  |  | FALSE | FALSE | 2749 | 3574 | 3299 | 4123 | {5526D418-F149-4289-8C5E-948350DF53AD}
2878 | 2412 | {CB6B594B-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | PETALUMA C | Bank 4 | CB 1109 | PGE\DCGa | 2017-01-11 09:24:56.0479584 -08:00 | 0426301109 | 042631109 | 8 | 2 | 2 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | TRUE | 733 | 953 | 879 | 1099 | {5D2AA7A5-4173-4AB6-896E-B453518A0B94}
2879 | 2412 | {CB6B5954-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | PETALUMA C | Bank 4 | CB 1110 | PGE\DCGa | 2016-11-02 14:57:11.8986957 -07:00 | 0426301110 | 042631110 | 8 | 2 | 2 | 1 | 326 | 7.11 | 7.04 | 326 | 7.11 | 7.04 | 385 | 8.4 | 8.32 | 385 | 8.4 | 8.32 | 336 | 7.33 | 7.26 | 336 | 7.33 | 7.26 | 396 | 8.64 | 8.55 | 396 | 8.64 | 8.55 |  |  | FALSE | TRUE | 733 | 953 | 879 | 1099 | {F6719BAE-9658-455D-9A0B-F9C93BC7695D}
2880 | 2413 | {08C02F33-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | HATTON | Bank 1 | CB 1101 | PGE\MTDR | 2017-07-10 15:52:08.5145110 -07:00 | 1822901101 | 182291101 | 8 | 3 | 3 | 2 | 342 | 7.46 | 7.39 | 342 | 7.46 | 7.39 | 421 | 9.19 | 9.1 | 421 | 9.19 | 9.1 | 353 | 7.7 | 7.62 | 353 | 7.7 | 7.62 | 427 | 9.32 | 9.23 | 427 | 9.32 | 9.23 |  |  | FALSE | FALSE | 721 | 721 | 721 | 721 | {AC1E2F4E-3DD3-45E1-A46F-F80EFE626FEE}
2881 | 2413 | {0ECFF4BB-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | HATTON | Bank 1 | CB 1102 | PGE\ACT0 | 2016-11-23 13:02:30.4686842 -08:00 | 1822901102 | 182291102 | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 582 | 12.7 | 12.57 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 750 | 750 | 750 | {FE7CD2FF-E3D4-4350-A709-73836A9A84F2}
2882 | 2414 | {14EAB6DB-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | HOLLISTER | Bank 1 | CB 2101 | PGE\ACT0 | 2016-10-13 16:24:22.4190403 -07:00 | 1824902101 | 182492101 | 12 | 3 | 3 | 2 | 524 | 19.8 | 19.6 | 524 | 19.8 | 19.6 | 591 | 22.34 | 22.12 | 591 | 22.34 | 22.12 | 599 | 22.64 | 22.41 | 599 | 22.64 | 22.41 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 635 | 825 | 762 | 952 | {D0253891-058F-4805-B2D3-4C9C2DA5E103}
2883 | 2414 | {14EAB6EF-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | HOLLISTER | Bank 1 | CB 2102 | PGE\MTDR | 2017-07-10 15:57:49.2852798 -07:00 | 1824902102 | 182492102 | 12 | 3 | 3 | 2 | 391 | 14.78 | 14.63 | 371 | 14.02 | 13.88 | 440 | 16.63 | 16.46 | 418 | 15.8 | 15.64 | 443 | 16.74 | 16.57 | 420 | 15.87 | 15.71 | 473 | 17.88 | 17.7 | 449 | 16.97 | 16.8 |  |  | FALSE | FALSE | 635 | 668 | 668 | 668 | {1CE0E284-59CE-475C-858C-37848CB71790}
2884 | 2403 | {F4276529-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND C | Bank 2 | CB 1118 | PGE\C7CF | 2016-12-12 16:48:43.7697916 -08:00 | 012011118 | 012011118 | 8 | 3 | 3 | 2 | 455 | 9.93 | 9.83 | 400 | 8.73 | 8.64 | 529 | 11.54 | 11.42 | 400 | 8.73 | 8.64 | 464 | 10.13 | 10.03 | 400 | 8.73 | 8.64 | 540 | 11.78 | 11.66 | 400 | 8.73 | 8.64 | 50 Amps to be reserved for SF side of Bay Bridge back up reserve capacity. |  | FALSE | FALSE | 2749 | 3574 | 3299 | 4123 | {A0A48125-4DE6-446D-ADC9-5478FD37AF80}
2885 | 2415 | {CB6B5A4A-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SANTA ROSA A | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-13 16:56:09.2573298 -07:00 | 0421501101 | 042151101 | 8 | 2 | 2 | 1 | 534 | 11.65 | 11.53 | 534 | 11.65 | 11.53 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 591 | 12.9 | 12.77 | 591 | 12.9 | 12.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Done by C8M4 2016 |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {0D0FAB57-A5F6-445E-A18C-D9199D1A8275}
2886 | 2415 | {CB6B5A6B-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SANTA ROSA A | Bank 1 | CB 1102 | PGE\MTN6 | 2017-05-15 16:54:17.9761201 -07:00 | 0421501102 | 042151102 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Done by C8M4 10/13/2016 |  | FALSE | FALSE | 1848 | 2270 | 2000 | 2400 | {9A8E88AE-7F4D-49F7-954A-FAD0ADD1EF89}
2887 | 2415 | {CB6B5A7B-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SANTA ROSA A | Bank 1 | CB 1103 | PGE\DCGa | 2017-03-30 11:46:21.1859690 -07:00 | 0421501103 | 042151103 | 8 | 2 | 2 | 1 | 582 | 12.7 | 12.57 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Done by C8M4 10/16/2016 |  | FALSE | FALSE | 1848 | 2270 | 2000 | 2400 | {113AF39B-CEBD-46E6-92E4-6948C3F0C3AD}
2888 | 2415 | {CB6B5A9A-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SANTA ROSA A | Bank 1 | CB 1104 | PGE\C8M4 | 2016-10-13 17:16:31.7710322 -07:00 | 0421501104 | 042151104 | 8 | 2 | 2 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 591 | 12.9 | 12.77 | 591 | 12.9 | 12.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Done by C8M4 2016 |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {AE4F5829-0197-4F23-80A0-CD7EA73769FD}
2889 | 2416 | {CB6B5AD7-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SANTA ROSA A | Bank 2 | CB 1105 | PGE\JAMR | 2017-08-15 11:55:24.3322234 -07:00 | 0421501105 | 042151105 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | C8M4 2016 |  | FALSE | FALSE | 2000 | 2400 | 2000 | 2400 | {0AC7981C-6E4C-4EF0-82F8-D2FF0AB7BBED}
2890 | 2416 | {CB6B5AE0-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SANTA ROSA A | Bank 2 | CB 1106 | PGE\DCGa | 2017-02-09 15:44:54.6999448 -08:00 | 0421501106 | 042151106 | 8 | 2 | 2 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | C8M4 10/13/2016 |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {1A133479-6594-49BE-916D-03752B7FA869}
2891 | 2416 | {D1672DB4-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SANTA ROSA A | Bank 2 | CB 1107 | PGE\C8M4 | 2017-04-27 18:01:22.8701921 -07:00 | 0421501107 | 042151107 | 8 | 3 | 3 | 1 | 488 | 10.65 | 10.54 | 488 | 10.65 | 10.54 | 576 | 12.57 | 12.44 | 570 | 12.44 | 12.32 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 593 | 12.94 | 12.81 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2000 | 2400 | 2000 | 2400 | {30746768-754F-488A-B56E-5EC0DC13AE1C}
2892 | 2416 | {D1672DBD-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SANTA ROSA A | Bank 2 | CB 1108 | PGE\MTN6 | 2017-05-15 12:28:47.6645305 -07:00 | 0421501108 | 042151108 | 8 | 3 | 3 | 1 | 512 | 11.17 | 11.06 | 512 | 11.17 | 11.06 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | C8M4 10/2016 |  | FALSE | FALSE | 2000 | 2400 | 2000 | 2400 | {C47B7DCA-A5F3-4B80-8A97-66151DFBAF59}
2893 | 2417 | {D1672DE5-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SANTA ROSA A | Bank 3 | CB 1109 | PGE\C8M4 | 2016-10-14 07:25:48.5717815 -07:00 | 0421501109 | 042151109 | 8 | 2 | 2 | 1 | 457 | 9.97 | 9.87 | 457 | 9.97 | 9.87 | 576 | 12.57 | 12.44 | 576 | 12.57 | 12.44 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 593 | 12.94 | 12.81 | 593 | 12.94 | 12.81 | C8M4 10/2016 |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {A18FB5E1-39F6-4DFE-9095-06DE8FF3C4F0}
2894 | 2417 | {D1672DEE-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SANTA ROSA A | Bank 3 | CB 1110 | PGE\RVS7 | 2017-06-20 07:08:47.3008725 -07:00 | 0421501110 | 042151110 | 8 | 3 | 2 | 1 | 415 | 9.06 | 8.97 | 415 | 9.06 | 8.97 | 527 | 11.5 | 11.39 | 527 | 11.5 | 11.39 | 591 | 12.9 | 12.77 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | C8M4 10/2016 |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {8EF6A387-BFB3-450D-904D-DBD3360B944C}
2895 | 2417 | {D1672E21-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SANTA ROSA A | Bank 3 | CB 1111 | PGE\JAMR | 2017-08-15 13:50:03.4507009 -07:00 | 0421501111 | 042151111 | 8 | 3 | 3 | 1 | 415 | 9.06 | 8.97 | 415 | 9.06 | 8.97 | 527 | 11.5 | 11.39 | 527 | 11.5 | 11.39 | 459 | 10.02 | 9.92 | 459 | 10.02 | 9.92 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | C8M4 10/2016 |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {8AF9363A-B952-437B-A3C1-68AA5424CB13}
2896 | 2418 | {D10E1F8A-671D-11E5-80CA-005056A729E5} | FRESNO | SAND CREEK | Bank 1 | CB 1103 | PGE\BXYD | 2017-01-23 10:13:20.4990601 -08:00 | 2546001103 | 254601103 | 8 | 3 | 3 | 1 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 |  |  | FALSE | FALSE | 343 | 446 | 412 | 515 | {B648DC7F-6840-4A27-965D-FA299B954399}
2897 | 2417 | {D1672E4D-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SANTA ROSA A | Bank 3 | CB 1112 | PGE\C8M4 | 2016-10-14 08:19:51.6700790 -07:00 | 0421501112 | 042151112 | 8 | 2 | 2 | 1 | 474 | 10.34 | 10.24 | 474 | 10.34 | 10.24 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 525 | 11.46 | 11.35 | 525 | 11.46 | 11.35 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | C8M4 10/2016 |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {64D0819B-F6D7-4702-B1E3-71AF7413C24F}
2898 | 2420 | {5E3AAA8A-671D-11E5-80CA-005056A729E5} | YOSEMITE | RIVERBANK | Bank 1 | CB 1711 | PGE\BXYD | 2016-10-14 09:59:04.3793315 -07:00 | 1631901711 | 163191711 | 10 | 3 | 3 | 1 | 464 | 14.35 | 14.21 | 464 | 14.35 | 14.21 | 520 | 16.08 | 15.92 | 520 | 16.08 | 15.92 | 599 | 18.52 | 18.33 | 599 | 18.52 | 18.33 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 |  |  | FALSE | FALSE | 910 | 1183 | 1092 | 1365 | {D10BE708-C859-4E29-AAC2-866AA8B5E3A3}
2899 | 2420 | {5E3AAA95-671D-11E5-80CA-005056A729E5} | YOSEMITE | RIVERBANK | Bank 1 | CB 1712 | PGE\BXYD | 2017-01-09 13:15:31.1449807 -08:00 | 1631901712 | 163191712 | 10 | 3 | 3 | 1 | 325 | 10.05 | 9.95 | 308 | 9.52 | 9.42 | 363 | 11.22 | 11.11 | 344 | 10.64 | 10.53 | 415 | 12.83 | 12.7 | 394 | 12.18 | 12.06 | 443 | 13.7 | 13.56 | 420 | 12.99 | 12.86 |  |  | FALSE | FALSE | 910 | 1183 | 1092 | 1365 | {32F918DC-F937-46B1-BF2F-0194708ED761}
2900 | 2420 | {5E3AAAA3-671D-11E5-80CA-005056A729E5} | YOSEMITE | RIVERBANK | Bank 1 | CB 1714 | PGE\BXYD | 2016-10-14 10:06:17.1267668 -07:00 | 1631901714 | 163191714 | 10 | 3 | 3 | 1 | 530 | 16.39 | 16.23 | 530 | 16.39 | 16.23 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 |  |  | FALSE | FALSE | 910 | 1183 | 1092 | 1365 | {9E8E00E7-F475-4092-B88B-65494719A396}
2901 | 2359 | {40A38736-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | FAIRWAY | Bank 1 | CB 1103 | PGE\A9S5 | 2016-11-11 09:12:35.8664322 -08:00 | 1820601103 | 182061103 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {3421427F-8B34-4222-951B-939DE51DF8B4}
2902 | 2359 | {40A38747-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | FAIRWAY | Bank 1 | CB 1104 | PGE\A9S5 | 2016-11-11 09:13:27.7258880 -08:00 | 1820601104 | 182061104 | 8 | 3 | 3 | 2 | 677 | 14.77 | 14.62 | 677 | 14.77 | 14.62 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 717 | 15.65 | 15.49 | 717 | 15.65 | 15.49 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {8759B149-BBCA-4556-B0AB-A0815804DB10}
2903 | 2419 | {40A38758-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | FAIRWAY | Bank 2 | CB 1106 | PGE\ACT0 | 2016-12-01 07:29:50.2272146 -08:00 | 1820601106 | 182061106 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {D9BD6C9B-C770-4D22-9B99-40FC7C73D538}
2904 | 2419 | {40A38760-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | FAIRWAY | Bank 2 | CB 1107 | PGE\ACT0 | 2016-12-01 07:30:27.2006526 -08:00 | 1820601107 | 182061107 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {3EF34C44-2A96-4269-9F58-271F2BCA4ECA}
2905 | 2419 | {469FD8B8-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | FAIRWAY | Bank 2 | CB 1108 | PGE\ACT0 | 2016-12-01 07:30:59.3719742 -08:00 | 1820601108 | 182061108 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {6A2A5632-C259-4EFE-A498-846584EA3AA5}
2907 | 2421 | {58406C80-671D-11E5-80CA-005056A729E5} | YOSEMITE | INDIAN FLAT | Bank 1 (Non SCADA) | CB 1104 (Non-SCADA) | PGE\BXYD | 2017-01-10 12:58:06.1550936 -08:00 | 2526901104 | 252691104 | 8 | 3 | 3 | 1 | 197 | 4.3 | 4.26 | 197 | 4.3 | 4.26 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 |  |  | FALSE | FALSE | 197 | 257 | 237 | 296 | {72D48D11-2C0F-4F58-BB79-3B949E825C1D}
2908 | 2422 | {4CBBD35D-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | FOOTHILL | Bank 1 | CB 1101 | PGE\A9S5 | 2016-11-11 09:37:56.3615881 -08:00 | 1829501101 | 182951101 | 8 | 3 | 2 | 2 | 468 | 10.21 | 10.11 | 468 | 10.21 | 10.11 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 552 | 12.05 | 11.93 | 552 | 12.05 | 11.93 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {79E72185-C6E5-4EB6-B2D1-49EA48A41A0A}
2909 | 2424 | {523E8E36-671D-11E5-80CA-005056A729E5} | YOSEMITE | CROWS LANDING | Bank 1 | CB 1101 | PGE\BXYD | 2016-10-14 11:08:21.0237893 -07:00 | 1632501101 | 163251101 | 8 | 3 | 3 | 1 | 223 | 4.87 | 4.82 | 223 | 4.87 | 4.82 | 248 | 5.41 | 5.36 | 248 | 5.41 | 5.36 | 267 | 5.83 | 5.77 | 267 | 5.83 | 5.77 | 267 | 5.83 | 5.77 | 267 | 5.83 | 5.77 |  |  | FALSE | FALSE | 263 | 343 | 316 | 395 | {D55B4233-E735-44D7-A5BF-801A288F620A}
2910 | 2424 | {523E8E44-671D-11E5-80CA-005056A729E5} | YOSEMITE | CROWS LANDING | Bank 1 | CB 1102 | PGE\BXYD | 2016-10-14 11:10:42.2068603 -07:00 | 1632501102 | 163251102 | 8 | 3 | 3 | 1 | 230 | 5.02 | 4.97 | 230 | 5.02 | 4.97 | 230 | 5.02 | 4.97 | 230 | 5.02 | 4.97 | 230 | 5.02 | 4.97 | 230 | 5.02 | 4.97 | 230 | 5.02 | 4.97 | 230 | 5.02 | 4.97 |  |  | FALSE | FALSE | 263 | 343 | 316 | 395 | {436EF6CD-D3C1-41B5-AA65-0937FBAF11EB}
2912 | 2422 | {4CBBD365-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | FOOTHILL | Bank 1 | CB 1102 | PGE\ACT0 | 2016-12-01 07:32:25.8826500 -08:00 | 1829501102 | 182951102 | 8 | 2 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {EA2DC015-1B9C-41C0-B518-C8CC458602FD}
2913 | 2427 | {523E8D7B-671D-11E5-80CA-005056A729E5} | YOSEMITE | COARSEGOLD | Bank 1 | CB 2102 (Non-SCADA) | PGE\JWCp | 2016-11-03 12:21:13.1972105 -07:00 | 2544302102 | 254432102 | 12 | 3 | 3 | 1 | 423 | 15.99 | 15.83 | 282 | 10.66 | 10.55 | 500 | 18.9 | 18.71 | 315 | 11.9 | 11.78 | 500 | 18.9 | 18.71 | 358 | 13.53 | 13.39 | 500 | 18.9 | 18.71 | 382 | 14.44 | 14.3 |  |  | FALSE | FALSE | 423 | 550 | 508 | 635 | {01408B06-B07E-4A7A-8D86-2BFAFBC22C97}
2914 | 2428 | {523E8DFC-671D-11E5-80CA-005056A729E5} | YOSEMITE | CRESSEY | Bank 1 | CB 2103 | PGE\BXYD | 2016-11-08 15:48:03.3676744 -08:00 | 2547002103 | 254702103 | 12 | 3 | 3 | 1 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | Parker PP 2.2MVA Cogen: Summer Norm/Emerg=60/60, Winter Norm/Emerg=60/60 Canel Creek PP .9MVA Cogen: Summer Norm/Emerg=25/25, Winter Norm/Emerg=25/25 |  | FALSE | FALSE | 661 | 859 | 793 | 991 | {BD22C100-5DAF-4B99-B2A9-8A623D9FCD7A}
2915 | 2430 | {BD86DA88-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | FREMONT | Bank 1 | CB 1103 | PGE\RDR1 | 2017-05-31 12:26:14.2688346 -07:00 | 0143501103 | 014351103 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {5D55A1B3-1DD6-4535-9DFB-CFB10026473F}
2917 | 2428 | {523E8E1C-671D-11E5-80CA-005056A729E5} | YOSEMITE | CRESSEY | Bank 1 | CB 2104 | PGE\BXYD | 2016-11-08 15:48:17.7829984 -08:00 | 2547002104 | 254702104 | 12 | 3 | 3 | 1 | 661 | 24.98 | 24.73 | 661 | 24.98 | 24.73 | 717 | 27.1 | 26.83 | 717 | 27.1 | 26.83 | 717 | 27.1 | 26.83 | 717 | 27.1 | 26.83 | 717 | 27.1 | 26.83 | 717 | 27.1 | 26.83 |  |  | FALSE | FALSE | 661 | 859 | 793 | 991 | {60F6E866-DA8B-40C5-8AFD-D7972243126F}
2918 | 2430 | {BD86DABB-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | FREMONT | Bank 1 | CB 1104 | PGE\RDR1 | 2017-06-01 10:31:38.1744890 -07:00 | 0143501104 | 014351104 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {4A95E979-02FB-43A3-BDC4-512DD8DB915B}
2919 | 2430 | {BD86DAE3-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | FREMONT | Bank 1 | CB 1105 | PGE\RDR1 | 2017-06-01 10:36:29.5294270 -07:00 | 0143501105 | 014351105 | 7 | 3 | 3 | 2 | 615 | 13.28 | 13.15 | 615 | 13.28 | 13.15 | 667 | 14.41 | 14.27 | 667 | 14.41 | 14.27 | 627 | 13.54 | 13.4 | 627 | 13.54 | 13.4 | 667 | 14.41 | 14.27 | 667 | 14.41 | 14.27 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {34A47C65-96A4-4E5F-AAA3-8B2FF385D7ED}
2920 | 2432 | {5A80370C-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | KNIGHTS LANDING | Bank 1 | CB 1101 | PGE\JMB4 | 2016-10-14 17:42:30.3891691 -07:00 | 0627201101 | 062721101 | 8 | 2 | 2 | 1 | 500 | 10.91 | 10.8 | 430 | 9.38 | 9.29 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | TRUE | 430 | 559 | 516 | 646 | {0063AEA4-AD5C-4F60-9EEA-D36DA68F7FD9}
2921 | 2432 | {5A803723-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | KNIGHTS LANDING | Bank 1 | CB 1102 | PGE\JMB4 | 2017-02-24 15:39:43.9781089 -08:00 | 0627201102 | 062721102 | 8 | 2 | 2 | 1 | 282 | 6.15 | 6.09 | 269 | 5.87 | 5.81 | 315 | 6.87 | 6.8 | 302 | 6.59 | 6.52 | 358 | 7.81 | 7.73 | 342 | 7.46 | 7.39 | 382 | 8.34 | 8.26 | 365 | 7.97 | 7.89 |  |  | FALSE | FALSE | 282 | 315 | 358 | 382 | {6E094E4E-14F4-4DC4-8727-2C340D7CAD83}
2922 | 2442 | {C5615078-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | MONROE | Bank 1 | CB 2102 | PGE\C8M4 | 2016-10-15 11:48:40.7823569 -07:00 | 0433002102 | 043302102 | 12 | 2 | 2 | 1 | 493 | 18.63 | 18.44 | 493 | 18.63 | 18.44 | 589 | 22.26 | 22.04 | 589 | 22.26 | 22.04 | 534 | 20.18 | 19.98 | 534 | 20.18 | 19.98 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {EC627C11-8E46-47AA-9ABC-1A07C2BADFDE}
2923 | 2442 | {C5615096-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | MONROE | Bank 1 | CB 2103 | PGE\DCGa | 2017-01-30 13:35:07.1819442 -08:00 | 0433002103 | 043302103 | 12 | 2 | 2 | 1 | 530 | 20.03 | 19.83 | 530 | 20.03 | 19.83 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | C8M4 10/2016 |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {4CFB831C-44AD-47CF-99A3-190F8A9C28A9}
2924 | 2443 | {C56150D4-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | MONROE | Bank 2 | CB 1104 | PGE\C8M4 | 2017-04-27 17:53:54.6423725 -07:00 | 0433001104 | 043301104 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | C8M4 10/2016 |  | FALSE | FALSE | 1908 | 2000 | 2000 | 2000 | {CB211A6A-A751-4022-AFEA-416049EE37E6}
2925 | 2443 | {C56150DD-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | MONROE | Bank 2 | CB 1105 | PGE\C8M4 | 2017-04-27 17:54:23.4873272 -07:00 | 0433001105 | 043301105 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | C8M4 10/2016 |  | FALSE | FALSE | 1908 | 2000 | 2000 | 2000 | {850B874E-BB86-4ABB-9D72-8F5FC68C51FB}
2926 | 2443 | {C56150F4-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | MONROE | Bank 2 | CB 1106 | PGE\C8M4 | 2017-04-27 17:54:56.3103584 -07:00 | 0433001106 | 043301106 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1908 | 2000 | 2000 | 2000 | {581C8567-694A-45E1-B5BE-CBF4564C9F23}
2927 | 2444 | {C5615138-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | MONROE | Bank 3 | CB 2107 | PGE\C8M4 | 2017-04-27 17:55:31.5826367 -07:00 | 0433002107 | 043302107 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {A4CF42A0-64E6-4319-9C28-F633581224C9}
2928 | 2445 | {6DFF145E-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | HIGHLANDS | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-15 12:57:48.1148623 -07:00 | 0433601101 | 043361101 | 8 | 2 | 2 | 1 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 | Feeder for future use. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {0578FD5A-3CED-4A2D-800D-73399DCEEFB4}
2929 | 2445 | {6DFF1467-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | HIGHLANDS | Bank 1 | CB 1102 | PGE\DCGa | 2017-08-08 18:30:03.7016950 -07:00 | 0433601102 | 043361102 | 8 | 2 | 2 | 1 | 600 | 13.09 | 12.96 | 489 | 10.67 | 10.56 | 600 | 13.09 | 12.96 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {EAC62334-4356-4932-A4AF-F18D828D0D42}
2930 | 2445 | {6DFF147E-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | HIGHLANDS | Bank 1 | CB 1103 | PGE\C8M4 | 2016-10-15 13:25:41.4614307 -07:00 | 0433601103 | 043361103 | 8 | 2 | 2 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F830B474-20C7-4CA4-9155-D35CEBCF5E6D}
2931 | 2447 | {6DFF14BB-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | HIGHLANDS | Bank 2 | CB 1104 | PGE\DCGa | 2017-08-08 18:34:39.4561330 -07:00 | 0433601104 | 043361104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 345 | 7.53 | 7.45 | 600 | 13.09 | 12.96 | 386 | 8.42 | 8.34 | 600 | 13.09 | 12.96 | 443 | 9.67 | 9.57 | 600 | 13.09 | 12.96 | 473 | 10.32 | 10.22 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {DA8AE893-C77F-4C6A-B90F-3CA3AA3AC4D5}
2932 | 2435 | {620DC818-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | MADISON | Bank 1 | CB 1103 | PGE\SDK6 | 2017-01-31 15:06:50.1352447 -08:00 | 0631701103 | 063171103 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {10618F0F-BA95-4C03-B6CA-7BFB4F555E22}
2934 | 2448 | {620DC847-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | MADISON | Bank 2 | CB 1105 | PGE\SDK6 | 2017-01-20 15:45:04.8096299 -08:00 | 0631701105 | 063171105 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {628ECCD1-94EC-4AC2-AB42-D1AFDFA2A641}
2935 | 2449 | {6124836C-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | FORT BRAGG A | Bank 1 | CB 1101 | PGE\DCGa | 2016-11-09 17:34:07.4568883 -08:00 | 0427601101 | 042761101 | 8 | 3 | 3 | 2 | 426 | 9.3 | 9.21 | 426 | 9.3 | 9.21 | 479 | 10.45 | 10.35 | 479 | 10.45 | 10.35 | 482 | 10.52 | 10.41 | 482 | 10.52 | 10.41 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {120DF452-0613-402F-B393-6788F4384DF3}
2936 | 2449 | {61248375-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | FORT BRAGG A | Bank 1 | CB 1102 | PGE\DCGa | 2016-11-09 17:34:57.5806037 -08:00 | 0427601102 | 042761102 | 8 | 3 | 3 | 2 | 426 | 9.3 | 9.21 | 426 | 9.3 | 9.21 | 479 | 10.45 | 10.35 | 479 | 10.45 | 10.35 | 482 | 10.52 | 10.41 | 482 | 10.52 | 10.41 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {D2BA55C6-7159-4108-87C9-092CF3A544D6}
2938 | 2450 | {620DC86F-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | MADISON | Bank 3 | CB 2101 | PGE\SDK6 | 2017-01-31 15:42:00.6395021 -08:00 | 0631702101 | 063172101 | 12 | 3 | 3 | 1 | 423 | 15.99 | 15.83 | 423 | 15.99 | 15.83 | 550 | 20.79 | 20.58 | 549 | 20.75 | 20.54 | 508 | 19.2 | 19.01 | 508 | 19.2 | 19.01 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 423 | 550 | 508 | 635 | {0A95DC1A-84E3-4FFE-B0D3-BEB592D6671A}
2944 | 2449 | {6124837E-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | FORT BRAGG A | Bank 1 | CB 1103 | PGE\DCGa | 2016-11-09 17:33:06.3481630 -08:00 | 0427601103 | 042761103 | 8 | 3 | 3 | 2 | 321 | 7.01 | 6.94 | 321 | 7.01 | 6.94 | 360 | 7.86 | 7.78 | 360 | 7.86 | 7.78 | 358 | 7.81 | 7.73 | 358 | 7.81 | 7.73 | 382 | 8.34 | 8.26 | 382 | 8.34 | 8.26 | Not sure what the notes denote - C8M4 10/2016 |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {7A2B02A2-E7C4-4C9D-8E65-FA62E91D46A6}
2945 | 2455 | {6124839A-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | FORT BRAGG A | Bank 2 | CB 1104 | PGE\DCGa | 2016-11-03 14:34:52.4583993 -07:00 | 0427601104 | 042761104 | 8 | 3 | 3 | 2 | 369 | 8.05 | 7.97 | 232 | 5.06 | 5.01 | 414 | 9.04 | 8.95 | 262 | 5.72 | 5.66 | 415 | 9.06 | 8.97 | 308 | 6.72 | 6.65 | 443 | 9.67 | 9.57 | 329 | 7.18 | 7.11 |  |  | FALSE | TRUE | 1374 | 1787 | 1649 | 2061 | {3F0C781D-9CFE-4C89-AC46-A61964DB1256}
2946 | 2456 | {5A8036ED-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | JAMESON | Bank 1 | CB 1101 | PGE\TEJ2 | 2016-11-03 08:46:19.1489684 -07:00 | 0638001101 | 063801101 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 639 | 13.95 | 13.81 | 639 | 13.95 | 13.81 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 |  |  | FALSE | TRUE | 2061 | 2680 | 2474 | 3092 | {37038C93-E5C1-44E9-ADA2-6F7F49029448}
2947 | 2456 | {5A8036F6-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | JAMESON | Bank 1 | CB 1102 (Non-SCADA) | PGE\TEJ2 | 2016-11-03 15:39:12.5684260 -07:00 | 0638001102 | 063801102 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {3461D7BC-399A-43F0-BF06-62ED4796C3FB}
2948 | 2456 | {5A8036F9-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | JAMESON | Bank 1 | CB 1103 (Non-SCADA) | PGE\TEJ2 | 2016-11-03 08:51:54.3872921 -07:00 | 0638001103 | 063801103 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 639 | 13.95 | 13.81 | 639 | 13.95 | 13.81 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {D67EE371-CE89-4C60-A74A-0638CB24F677}
2949 | 2459 | {BF2DC04B-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | LAKEVILLE | Bank 4 | CB 1101 | PGE\C8M4 | 2016-10-15 17:57:17.3202857 -07:00 | 0433701101 | 043371101 | 8 | 2 | 2 | 1 | 565 | 12.33 | 12.21 | 565 | 12.33 | 12.21 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | PVC RISER: 1100 MCM AL should be rated at 578 for Summer Normal limiting capability. |  | FALSE | FALSE | 1145 | 1489 | 1374 | 1718 | {707145EF-E89B-47F3-B191-9B921C2B4C87}
2954 | 2459 | {BF2DC054-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | LAKEVILLE | Bank 4 | CB 1102 | PGE\C8M4 | 2016-10-15 18:03:10.6175912 -07:00 | 0433701102 | 043371102 | 8 | 2 | 2 | 1 | 565 | 12.33 | 12.21 | 565 | 12.33 | 12.21 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | OPERATIONAL AND PLANNING CAPABILITIES SHOULD READ: 578/600/600/600 SEE NOTE FOR PVC RISER |  | FALSE | FALSE | 1145 | 1489 | 1374 | 1718 | {45596F17-1039-4CB3-928B-01CD6B8413E2}
2955 | 2456 | {5A8036FC-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | JAMESON | Bank 1 | CB 1104 (Non-SCADA) | PGE\TEJ2 | 2016-11-03 08:55:14.5535041 -07:00 | 0638001104 | 063801104 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {85E1815D-ECC2-4247-9857-54ECDFA339C2}
2956 | 2461 | {81F19B7E-0E49-11E6-95F2-D4BED91EFF1A} | SACRAMENTO | JAMESON | BANK 2 (Non SCADA) | CB 1105 (Non-SCADA) | PGE\TEJ2 | 2016-11-03 15:47:11.0902924 -07:00 | 0638001105 | 063801105 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {1B9FDB86-C75D-4923-9C9D-0745D827B8AD}
2957 | 2462 | {BF2DBF26-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | FULTON | Bank 5 | CB 1101 (Non-SCADA) | PGE\C8M4 | 2016-10-15 18:58:35.9563017 -07:00 | 0425601101 | 042561101 | 8 | 3 | 2 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {240B68E2-C09D-4EDC-8EC3-2A8841594457}
2958 | 2462 | {BF2DBF36-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | FULTON | Bank 5 | CB 1102 (Non-SCADA) | PGE\C8M4 | 2016-10-15 19:01:19.1958007 -07:00 | 0425601102 | 042561102 | 8 | 3 | 2 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {E7A80342-95AC-4587-ABB3-F592375BB0A5}
2959 | 2462 | {BF2DBF54-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | FULTON | Bank 5 | CB 1103 (Non-SCADA) | PGE\C8M4 | 2016-10-15 19:12:19.0001686 -07:00 | 0425601103 | 042561103 | 8 | 3 | 2 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {5D3BE138-526F-4B4F-9F73-9B052A6EE0C0}
2960 | 2462 | {BF2DBF5D-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | FULTON | Bank 5 | CB 1104 (Non-SCADA) | PGE\DCGa | 2017-05-30 00:07:38.0897319 -07:00 | 0425601104 | 042561104 | 8 | 3 | 2 | 1 | 600 | 13.09 | 12.96 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | CAPABILITY NEEDS TO BE REDONE.... |  | FALSE | FALSE | 1374 | 1500 | 1500 | 1500 | {CADFFBD8-8472-4ED4-B445-A55DC410CE8F}
2961 | 2464 | {BF2DBF81-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | FULTON | Bank 6 | CB 1105 (Non-SCADA) | PGE\C8M4 | 2016-10-15 19:55:19.9575471 -07:00 | 0425601105 | 042561105 | 8 | 3 | 2 | 1 | 636 | 13.88 | 13.74 | 636 | 13.88 | 13.74 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {E6FB745B-784D-48CE-BEB7-BB188CF729D0}
2962 | 2464 | {BF2DBFA6-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | FULTON | Bank 6 | CB 1106 (Non-SCADA) | PGE\C8M4 | 2016-10-15 19:57:31.1478353 -07:00 | 0425601106 | 042561106 | 8 | 3 | 2 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {B6BA373A-9F67-471C-BBD2-C165B02C9019}
2963 | 2464 | {BF2DBFC5-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | FULTON | Bank 6 | CB 1107 (Non-SCADA) | PGE\C8M4 | 2016-10-15 19:59:23.1045103 -07:00 | 0425601107 | 042561107 | 8 | 3 | 2 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {CE83DEBC-6F70-460A-9086-0C3C8D7F68EB}
2964 | 2463 | {620DC9E1-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | MERIDIAN | Bank 1 | CB 1101 | PGE\JMB4 | 2016-10-16 18:19:47.6698142 -07:00 | 0625401101 | 062541101 | 8 | 1 | 1 | 1 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 |  |  | FALSE | TRUE | 962 | 1250 | 1154 | 1443 | {1D64EC8C-F145-4CF2-AAD7-E27F29C3CB68}
2965 | 2465 | {4D89159C-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | COLUSA | Bank 1 | CB 1101 | PGE\TEJ2 | 2016-11-10 09:39:58.8778556 -08:00 | 0620201101 | 062021101 | 8 | 3 | 3 | 1 | 325 | 7.09 | 7.02 | 325 | 7.09 | 7.02 | 363 | 7.92 | 7.84 | 363 | 7.92 | 7.84 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | Indication are that on 3/29/2016 changes were made as indicated on the CB and CT to 1200/5. No indication to what the ØMCT was changed to. Email was sent to capacity and reliability. |  | FALSE | FALSE | 481 | 601 | 577 | 601 | {9435474D-8C9F-4BA9-BCC7-661C0239C161}
2966 | 2465 | {4D8915AC-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | COLUSA | Bank 1 | CB 1103 | PGE\TEJ2 | 2016-11-10 09:40:44.0292427 -08:00 | 0620201103 | 062021103 | 8 | 3 | 3 | 1 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | There is a split off the 500 Cu UG going in two directions. One way of 700 Al going to switch 14181 and 4/o Al OH conductor and the other 700 Al going to switch 14173 and 1/o Cu. |  | FALSE | FALSE | 481 | 601 | 577 | 601 | {EBC91694-3CE2-47B2-B89E-007875871AD0}
2967 | 2467 | {4D8915CD-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | COLUSA | Bank 2 | CB 1104 | PGE\TEJ2 | 2016-10-17 12:39:26.6451369 -07:00 | 0620201104 | 062021104 | 8 | 3 | 3 | 1 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | CT ratio updated in 2016. MCT unknown. |  | FALSE | FALSE | 481 | 601 | 577 | 601 | {1512DD08-2723-4018-9050-951AE735E0B2}
2968 | 2467 | {4D8915EB-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | COLUSA | Bank 2 | CB 1105 | PGE\TEJ2 | 2016-11-10 09:41:39.3199112 -08:00 | 0620201105 | 062021105 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 |  |  | FALSE | FALSE | 481 | 601 | 577 | 601 | {1EB51961-7BE2-4E7E-A3FD-B179EEAC769D}
2970 | 2468 | {4D891687-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | CORDELIA | Bank 4 | CB 1101 | PGE\TEJ2 | 2016-10-17 12:44:42.4289450 -07:00 | 0627001101 | 062701101 | 8 | 3 | 3 | 1 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 577 | 750 | 692 | 866 | {81FB5CAF-1133-404C-9776-BA712A413369}
2972 | 2468 | {4D8916A5-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | CORDELIA | Bank 4 | CB 1102 | PGE\TEJ2 | 2016-10-17 12:45:03.4897550 -07:00 | 0627001102 | 062701102 | 8 | 3 | 3 | 1 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 577 | 750 | 692 | 866 | {BA123D6D-9E51-439A-8D26-6383FB36D0BC}
2973 | 2434 | {4D891601-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | COLUSA JUNCTION | Bank 1 | CB 1101 | PGE\TEJ2 | 2016-10-17 12:43:22.8671930 -07:00 | 0620701101 | 062071101 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 601 | 601 | 601 | 601 | {B7BC345D-40C0-4936-8413-B8E9FD850621}
2974 | 2469 | {53849DF2-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DUNNIGAN | Bank 1 | CB 1101 | PGE\SDK6 | 2017-01-20 15:40:50.5715408 -08:00 | 0638101101 | 063811101 | 8 | 4 | 4 | 1 | 384 | 8.38 | 8.3 | 364 | 7.94 | 7.86 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 461 | 10.06 | 9.96 | 437 | 9.54 | 9.44 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | Emerg Reg R1101 Bypassed - 200A OD blocked at 5% 448 amps |  | TRUE | FALSE | 384 | 500 | 461 | 577 | {4A97692B-86BF-4087-B528-12B2B8EBCD48}
2975 | 2471 | {8E5DEE13-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | ZAMORA | Bank 2 | CB 1107 | PGE\WRA4 | 2016-10-16 16:27:35.5804206 -07:00 | 0631901107 | 063191107 | 8 | 4 | 4 | 2 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {95324DF9-60F9-4640-A710-470491CF938C}
2976 | 2470 | {8E5DEDDB-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | ZAMORA | Bank 1 | CB 1105 | PGE\WRA4 | 2016-10-16 16:29:28.5104592 -07:00 | 0631901105 | 063191105 | 8 | 1 | 1 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {DB5B3B03-A668-4ECC-A492-F3DC2AF117F7}
2977 | 2470 | {8E5DEDF2-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | ZAMORA | Bank 1 | CB 1106 | PGE\WRA4 | 2016-10-16 16:31:07.5438114 -07:00 | 0631901106 | 063191106 | 8 | 1 | 1 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {19AAC47F-B0A4-49F8-A603-CD89D5D8B652}
2978 | 2463 | {620DC9F8-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | MERIDIAN | Bank 1 | CB 1102 | PGE\JMB4 | 2016-10-16 18:21:34.8580213 -07:00 | 0625401102 | 062541102 | 8 | 1 | 1 | 2 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 |  |  | FALSE | TRUE | 962 | 1250 | 1154 | 1443 | {EC02ED83-F7F5-46E5-A715-FD512AAF79CD}
2979 | 2472 | {58406C30-671D-11E5-80CA-005056A729E5} | YOSEMITE | GALLO | Bank 1 (Non SCADA) | CB 1101 | PGE\BXYD | 2016-11-14 17:15:55.0793922 -08:00 | 2549001101 | 254901101 | 8 | 3 | 3 | 1 | 661 | 14.43 | 14.29 | 661 | 14.43 | 14.29 | 792 | 17.28 | 17.11 | 792 | 17.28 | 17.11 | 717 | 15.65 | 15.49 | 717 | 15.65 | 15.49 | 842 | 18.38 | 18.2 | 842 | 18.38 | 18.2 |  |  | FALSE | FALSE | 1145 | 1489 | 1374 | 1718 | {1540BA8E-9844-4584-8642-208EBD2B9231}
2980 | 2472 | {58406C35-671D-11E5-80CA-005056A729E5} | YOSEMITE | GALLO | Bank 1 (Non SCADA) | CB 1102 | PGE\BXYD | 2016-10-17 10:10:33.1500793 -07:00 | 2549001102 | 254901102 | 8 | 3 | 3 | 1 | 661 | 14.43 | 14.29 | 661 | 14.43 | 14.29 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 |  |  | FALSE | FALSE | 1145 | 1489 | 1374 | 1718 | {A1E74FFD-CE15-4258-9B30-9A6093CB3DF2}
2981 | 2381 | {369797C2-671D-11E5-80CA-005056A729E5} | STOCKTON | HAMMER | Bank 1 | CB 1101 | PGE\BXYD | 2017-01-12 14:42:09.7394534 -08:00 | 1633001101 | 163301101 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 489 | 10.67 | 10.56 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2000 | {13BF9F52-D643-444D-AC4E-E54E17AF5A2B}
2982 | 2473 | {1B0578FE-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | HOLLISTER | Bank 2 | CB 2103 | PGE\MTDR | 2017-07-10 16:03:04.3937196 -07:00 | 1824902103 | 182492103 | 12 | 3 | 3 | 2 | 564 | 21.32 | 21.11 | 552 | 20.86 | 20.65 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 |  |  | FALSE | FALSE | 635 | 668 | 668 | 668 | {3CD8DBFA-1B76-479E-A979-33E3FEEF29A6}
2983 | 2381 | {369797CA-671D-11E5-80CA-005056A729E5} | STOCKTON | HAMMER | Bank 1 | CB 1102 | PGE\BXYD | 2017-01-12 14:42:42.1876614 -08:00 | 1633001102 | 163301102 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2000 | {79380E3A-C253-4F7A-B6CC-56B8544665FC}
2985 | 2381 | {369797D2-671D-11E5-80CA-005056A729E5} | STOCKTON | HAMMER | Bank 1 | CB 1103 | PGE\BXYD | 2017-01-12 14:43:58.9089532 -08:00 | 1633001103 | 163301103 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2000 | {10703E20-2EF2-4BBA-926E-7A786BB56AA2}
2986 | 2474 | {23C95D33-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | HOLLISTER | Bank 3 | CB 2104 | PGE\ACT0 | 2016-10-17 11:14:17.6042211 -07:00 | 1824902104 | 182492104 | 22 | 3 | 2 | 1 | 578 | 20.8 | 20.59 | 578 | 20.8 | 20.59 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {D8AF3E8F-FD1D-45A2-8B10-CB1FB464799D}
2987 | 2474 | {23C95D5C-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | HOLLISTER | Bank 3 | CB 2105 | PGE\ACT0 | 2016-10-17 11:18:20.0034427 -07:00 | 1824902105 | 182492105 | 22 | 3 | 3 | 2 | 391 | 14.07 | 13.93 | 391 | 14.07 | 13.93 | 440 | 15.84 | 15.68 | 440 | 15.84 | 15.68 | 443 | 15.94 | 15.78 | 443 | 15.94 | 15.78 | 473 | 17.02 | 16.85 | 473 | 17.02 | 16.85 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {39D173AC-A08D-40F3-951F-DA57759B981E}
2988 | 2476 | {369797F6-671D-11E5-80CA-005056A729E5} | STOCKTON | HAMMER | Bank 3 | CB 1108 | PGE\BXYD | 2017-01-12 14:52:16.7081442 -08:00 | 1633001108 | 163301108 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 916 | 1191 | 1100 | 1375 | {2F814F33-611E-4421-A5A1-75927CF3A241}
2989 | 2474 | {29C3C672-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | HOLLISTER | Bank 3 | CB 2106 | PGE\ACT0 | 2016-11-23 13:15:39.7640396 -08:00 | 1824902106 | 182492106 | 22 | 3 | 3 | 1 | 530 | 19.08 | 18.89 | 530 | 19.08 | 18.89 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {40BDB3AC-281E-4EA6-A544-A85927162EE9}
2990 | 2476 | {369797FB-671D-11E5-80CA-005056A729E5} | STOCKTON | HAMMER | Bank 3 | CB 1109 | PGE\BXYD | 2017-01-12 14:53:19.2645452 -08:00 | 1633001109 | 163301109 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 916 | 1191 | 1100 | 1375 | {D997251B-1047-4BF2-82EE-CAFF4C569424}
2991 | 2480 | {612482C3-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | ELK | Bank 1 | CB 1101 | PGE\C8M4 | 2016-11-18 11:51:02.9824597 -08:00 | 0429801101 | 042981101 | 8 | 3 | 3 | 2 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {DED03173-6255-4C46-A8C9-ECE2EF3803DB}
2992 | 2481 | {3003274A-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | INDUSTRIAL ACRES | Bank 1 | CB 411 (Non-SCADA) | PGE\ACT0 | 2016-10-17 12:03:53.6796279 -07:00 | 182300411 | 182300411 | 4 | 2 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 1238 | 1610 | 1486 | 1857 | {49DCEF8C-6A6B-4A3C-B478-E02052A33F52}
2993 | 2478 | {7530FE9D-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | SUISUN | Bank 1 | CB 1101 | PGE\TEJ2 | 2016-10-17 16:09:56.1480521 -07:00 | 0621301101 | 062131101 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {27CACEAC-B5BB-4A84-8AA3-DA0AA503C1D4}
2994 | 2478 | {7530FEA6-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | SUISUN | Bank 1 | CB 1102 | PGE\TEJ2 | 2016-10-17 16:05:36.7621422 -07:00 | 0621301102 | 062131102 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {03C7A232-EDDF-4DEB-A1A6-FDEEB954195B}
2995 | 2482 | {612482D9-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | EUREKA A | Bank 1 | CB 1103 | PGE\C8M4 | 2016-11-18 11:54:09.5007522 -08:00 | 1921201103 | 192121103 | 8 | 3 | 3 | 2 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | TRUE | 572 | 744 | 687 | 859 | {12043136-52B5-47CE-91C4-8B454DE88B41}
2996 | 2481 | {3003274D-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | INDUSTRIAL ACRES | Bank 1 | CB 412 (Non-SCADA) | PGE\ACT0 | 2016-10-17 12:48:36.1532493 -07:00 | 182300412 | 182300412 | 4 | 2 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 1238 | 1610 | 1486 | 1857 | {5557DE64-5A0C-443B-AD91-CF637995683A}
2997 | 2478 | {7530FEBD-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | SUISUN | Bank 1 | CB 1103 | PGE\TEJ2 | 2016-10-17 16:05:12.9851514 -07:00 | 0621301103 | 062131103 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {384886D6-74E6-4671-8C46-1CB0BDED72B5}
2998 | 2481 | {30032753-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | INDUSTRIAL ACRES | Bank 1 | CB 413 (Non-SCADA) | PGE\ACT0 | 2016-10-17 13:03:21.1343151 -07:00 | 182300413 | 182300413 | 4 | 2 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 1238 | 1610 | 1486 | 1857 | {E749A599-2F2B-4541-A245-9F1D70AD44BA}
3000 | 2481 | {30032756-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | INDUSTRIAL ACRES | Bank 1 | CB 415 (Non-SCADA) | PGE\K1LW | 2017-05-23 11:37:29.7191460 -07:00 | 182300415 | 182300415 | 4 | 2 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 380 | 2.88 | 2.85 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | IA-415 Regulator replaced under PM# 74006321. 3-300A +/-10% 2500V 3-75kVA |  | FALSE | FALSE | 1238 | 1610 | 1486 | 1857 | {95C3C230-4048-463C-9C7E-6FAF7580CB37}
3001 | 2483 | {4CBBD379-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | GOLDTREE | Bank 1 | CB 1105 | PGE\A9S5 | 2016-11-11 09:40:41.1509321 -08:00 | 1825801105 | 182581105 | 8 | 3 | 3 | 2 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 | 567 | 12.37 | 12.25 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {8572FDE6-C137-48CB-B6AE-92E7B39A760D}
3002 | 2483 | {4CBBD37E-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | GOLDTREE | Bank 1 | CB 1107 | PGE\A9S5 | 2016-11-11 09:41:20.9158419 -08:00 | 182581107 | 182581107 | 8 | 3 | 3 | 2 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {9DE3F8EE-B46A-4A22-9895-986FD6D8F319}
3004 | 2478 | {7530FECD-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | SUISUN | Bank 1 | CB 1104 | PGE\TEJ2 | 2016-10-17 13:19:21.7967605 -07:00 | 0621301104 | 062131104 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {1DEFF33F-4186-4FB5-92EC-0FCF6B3188E9}
3005 | 2483 | {4CBBD383-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | GOLDTREE | Bank 1 | CB 1108 | PGE\A9S5 | 2016-11-11 09:41:50.6041691 -08:00 | 182581108 | 182581108 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {9EBC9ADB-552F-42D3-972B-DCD1A295FACC}
3007 | 2484 | {7530FEEE-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | SUISUN | Bank 2 | CB 1105 | PGE\TEJ2 | 2016-10-17 16:02:39.8661963 -07:00 | 0621301105 | 062131105 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {1F576E0F-D2B2-42C3-A055-5AEA502AED4B}
3008 | 2484 | {7530FEF7-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | SUISUN | Bank 2 | CB 1106 | PGE\TEJ2 | 2016-10-17 16:01:37.8752986 -07:00 | 0621301106 | 062131106 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {AA327C81-47B8-49E4-93AC-AB3A1A15477E}
3009 | 2484 | {7530FF00-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | SUISUN | Bank 2 | CB 1107 | PGE\TEJ2 | 2016-10-17 14:36:08.4937425 -07:00 | 0621301107 | 062131107 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {88CAFA94-698B-4F69-A4DE-E90F1B72B34D}
3010 | 2485 | {4CBBD38F-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | MESA | Bank 4 | CB 1101 | PGE\A9S5 | 2016-11-11 09:42:50.8669703 -08:00 | 1828201101 | 182821101 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 4/0 Al LIMITS LOAD ADDITIONS AND TRANSFERS FROM EITHER OCEANO 1102 OR SANTA MARIA 1106 |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {90CD2E10-D146-452E-A503-DC49281FE31F}
3011 | 2485 | {4CBBD3A0-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | MESA | Bank 4 | CB 1102 | PGE\A9S5 | 2016-11-11 09:43:15.2790923 -08:00 | 1828201102 | 182821102 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {92755B55-3984-43E6-9B6A-4E0C79A8E2A9}
3012 | 2485 | {5314D67F-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | MESA | Bank 4 | CB 1103 | PGE\A9S5 | 2016-11-11 09:43:45.4189754 -08:00 | 1828201103 | 182821103 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {AB1A3CE8-8B90-4C5A-8659-C4A4544B86C6}
3014 | 2484 | {7530FF25-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | SUISUN | Bank 2 | CB 1108 | PGE\TEJ2 | 2016-10-17 16:00:24.8156709 -07:00 | 0621301108 | 062131108 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {8FE7B62A-1E9A-4812-8378-74599E77F8EA}
3015 | 2489 | {66556E82-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | OCEANO | Bank 1 | CB 1104 | PGE\A9S5 | 2016-11-11 09:46:04.8398677 -08:00 | 1826001104 | 182601104 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9B05982B-40B2-405D-AF93-07190658DA5C}
3016 | 2489 | {66556E9F-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | OCEANO | Bank 1 | CB 1106 | PGE\A9S5 | 2016-11-11 09:46:28.3643165 -08:00 | 1826001106 | 182601106 | 8 | 3 | 3 | 2 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {0474E6E2-9E61-4AE6-98EE-52431C188692}
3017 | 2486 | {3C91AE2B-671D-11E5-80CA-005056A729E5} | STOCKTON | MOSHER | Bank 1 | CB 2104 | PGE\BXYD | 2017-01-11 15:02:01.4840078 -08:00 | 1637202104 | 163722104 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {296685F0-4E5A-44AF-8414-95B67375B51B}
3018 | 2488 | {7B288CAD-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | SUISUN | Bank 3 | CB 1109 | PGE\TEJ2 | 2016-12-01 16:06:04.5979653 -08:00 | 0621301109 | 062131109 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {8AD54AD7-E7A5-4A80-8DA4-B4BD1F2D1A56}
3019 | 2489 | {6C58FF3C-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | OCEANO | Bank 1 | CB 1108 | PGE\A9S5 | 2016-11-11 09:46:50.2678397 -08:00 | 1826001108 | 182601108 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {D78B2F43-3CCA-408E-AC37-FA7FEF9E94B1}
3020 | 2486 | {3C91AE30-671D-11E5-80CA-005056A729E5} | STOCKTON | MOSHER | Bank 1 | CB 2105 | PGE\BXYD | 2017-01-11 15:03:40.9385654 -08:00 | 1637202105 | 163722105 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 674 | 25.47 | 25.22 | 674 | 25.47 | 25.22 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {34B7F61B-7E4F-4458-A3A4-75455B6A58D6}
3021 | 2488 | {7B288CCB-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | SUISUN | Bank 3 | CB 1110 | PGE\TEJ2 | 2016-12-01 16:06:44.7423859 -08:00 | 0621301110 | 062131110 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {63390E9A-B8FC-4F28-8FD5-7BFDC669AEC5}
3022 | 2494 | {30032762-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | JOLON | Bank 1 | CB 1102 | PGE\ACT0 | 2016-11-23 13:23:05.9155632 -08:00 | 1829801102 | 182981102 | 8 | 3 | 3 | 1 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 |  |  | FALSE | FALSE | 481 | 601 | 577 | 601 | {14D2FFF9-DE1F-4334-9BCE-8FBE8C3877E6}
3023 | 4476 | {E1F1F9CB-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND C | Bank 2 | CB 1120 | PGE\MFN3 | 2017-07-13 10:45:45.3860363 -07:00 | 012011120 | 012011120 | 7 | 3 | 3 | 2 | 492 | 10.63 | 10.52 | 467 | 10.09 | 9.99 | 554 | 11.97 | 11.85 | 526 | 11.36 | 11.25 | 527 | 11.38 | 11.27 | 527 | 11.38 | 11.27 | 598 | 12.92 | 12.79 | 568 | 12.27 | 12.15 | C1120 or L1102 is normal feeder for POO load and is reserved to serve 185A. 7-15-2014; currently reserved on L 1102 |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {9CD1D1A1-872F-4C5D-8AA4-4AB8BD3730B4}
3024 | 2403 | {DDFCE680-22CF-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND C | Bank 2 | CB 1132 | PGE\C7CF | 2016-12-12 16:49:46.5952085 -08:00 | 0120101132 | 012011132 | 8 | 3 | 3 | 2 | 445 | 9.71 | 9.61 | 445 | 9.71 | 9.61 | 494 | 10.78 | 10.67 | 494 | 10.78 | 10.67 | 458 | 10 | 9.9 | 458 | 10 | 9.9 | 509 | 11.11 | 11 | 509 | 11.11 | 11 |  |  | FALSE | FALSE | 2749 | 3574 | 3299 | 4123 | {28B02E35-FA99-4DEB-9C2F-9E0818DD8846}
3025 | 2488 | {7B288D01-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | SUISUN | Bank 3 | CB 1112 | PGE\TEJ2 | 2016-10-17 15:50:52.5491963 -07:00 | 0621301112 | 062131112 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {44672258-AD1C-42D4-86B6-3B3FF754C6B6}
3026 | 2488 | {7B288CD4-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | SUISUN | Bank 3 | CB 1111 | PGE\TEJ2 | 2016-10-17 15:57:59.5043920 -07:00 | 0621301111 | 062131111 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {645182B1-7EDF-4AFF-B4F5-22C33AA9AA56}
3028 | 2495 | {6C58FF53-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | OCEANO | Bank 2 | CB 1101 | PGE\A9S5 | 2016-11-11 10:01:56.3417009 -08:00 | 1826001101 | 182601101 | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 582 | 12.7 | 12.57 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {DF22DCC2-7D50-4655-BD63-76F81568262B}
3029 | 2403 | {ECDC37AC-22CF-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND C | Bank 2 | CB 1133 | PGE\C7CF | 2016-12-12 16:50:01.5562798 -08:00 | 0120101133 | 012011133 | 8 | 3 | 3 | 2 | 462 | 10.08 | 9.98 | 462 | 10.08 | 9.98 | 538 | 11.74 | 11.62 | 538 | 11.74 | 11.62 | 471 | 10.28 | 10.18 | 471 | 10.28 | 10.18 | 549 | 11.98 | 11.86 | 549 | 11.98 | 11.86 |  |  | FALSE | FALSE | 2749 | 3574 | 3299 | 4123 | {D3DD0D5A-C0FF-42D9-AB0F-D99CD4F6E397}
3033 | 2495 | {6C58FF58-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | OCEANO | Bank 2 | CB 1102 | PGE\A9S5 | 2016-11-11 10:03:16.1090583 -08:00 | 1826001102 | 182601102 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {77E6CD3D-7E86-4EFE-BC60-D0E6F6A51206}
3034 | 2495 | {6C58FF5D-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | OCEANO | Bank 2 | CB 1103 | PGE\ACT0 | 2016-12-01 07:33:15.2592376 -08:00 | 1826001103 | 182601103 | 8 | 3 | 3 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {9172A643-B4F2-4109-B9CF-46DB17A0A136}
3035 | 2495 | {72505B1E-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | OCEANO | Bank 2 | CB 1105 | PGE\ACT0 | 2016-12-01 07:33:44.3701212 -08:00 | 1826001105 | 182601105 | 8 | 3 | 3 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {BC43C737-4515-4E91-A63A-CE9650C08656}
3036 | 2496 | {CA12BBE4-2F56-11E6-B38D-D4BED91EFF1A} | EAST BAY | PALO SECO | UNIT SUB 401 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-19 11:40:24.3203534 -08:00 | 013180401 | 013180401 | 4 | 3 | 3 | 2 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 429 | 3.25 | 3.22 | 429 | 3.25 | 3.22 | 396 | 3 | 2.97 | 396 | 3 | 2.97 | 495 | 3.75 | 3.71 | 495 | 3.75 | 3.71 |  |  | FALSE | FALSE | 330 | 429 | 396 | 495 | {9AC5D00D-F37E-4520-A1B2-2CC8C21BD6FB}
3037 | 2497 | {36053160-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | KING CITY | Bank 1 | CB 1105 | PGE\ACT0 | 2016-10-17 16:21:37.7826408 -07:00 | 1820301105 | 182031105 | 8 | 3 | 2 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {233ABB90-CEE5-4011-96E1-1E8F7732D48D}
3038 | 2497 | {36053168-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | KING CITY | Bank 1 | CB 1106 | PGE\ACT0 | 2016-10-17 16:25:17.0106425 -07:00 | 1820301106 | 182031106 | 8 | 3 | 2 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {896D4DF1-63D6-4F18-9BBA-E1CE14BD2EC1}
3039 | 2499 | {305A1A45-2F56-11E6-B38D-D4BED91EFF1A} | EAST BAY | RICHMOND Q | BANK 401 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-10-19 17:36:05.7455931 -07:00 | 012520401 | 012520401 | 4 | 3 | 3 | 2 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 392 | 2.97 | 2.94 | 392 | 2.97 | 2.94 | 367 | 2.78 | 2.75 | 367 | 2.78 | 2.75 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 330 | 429 | 396 | 495 | {626B22B4-B9AA-4405-9144-6635C26905D8}
3040 | 2500 | {264037C6-2F56-11E6-B38D-D4BED91EFF1A} | EAST BAY | RICHMOND Q | BANK 402 (Non SCADA) | CB 402 (Non-SCADA) | PGE\C7CF | 2016-12-19 11:48:20.6723903 -08:00 | 012520402 | 012520402 | 4 | 3 | 3 | 2 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 396 | 3 | 2.97 | 396 | 3 | 2.97 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {9DEEE75C-E5D2-4FDE-A68B-51E1F3D60CCB}
3041 | 2502 | {13F40525-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | RIDGE | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-19 11:56:47.5966834 -08:00 | 012840401 | 012840401 | 4 | 3 | 3 | 2 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 396 | 3 | 2.97 | 396 | 3 | 2.97 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {D9366148-A7EB-4C98-ADE0-3A0F73F4D3BE}
3042 | 2503 | {13F4052B-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | RIDGE | Bank 2 (Non SCADA) | CB 402 (Non-SCADA) | PGE\C7CF | 2016-12-19 11:57:47.3781128 -08:00 | 012840402 | 012840402 | 4 | 3 | 3 | 2 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 382 | 2.89 | 2.86 | 382 | 2.89 | 2.86 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {3EAFD6EA-9590-4ED6-8DDB-14B8FDEA461D}
3043 | 2504 | {13F40534-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | RUSSELL | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-19 11:58:57.1588843 -08:00 | 013310401 | 013310401 | 4 | 3 | 3 | 2 | 369 | 2.79 | 2.76 | 369 | 2.79 | 2.76 | 414 | 3.13 | 3.1 | 414 | 3.13 | 3.1 | 415 | 3.14 | 3.11 | 415 | 3.14 | 3.11 | 443 | 3.35 | 3.32 | 443 | 3.35 | 3.32 |  |  | FALSE | FALSE | 528 | 687 | 634 | 792 | {16E80A4E-729A-45DB-BAE4-A5DE1038BEC3}
3044 | 2504 | {13F40537-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | RUSSELL | Bank 1 (Non SCADA) | CB 402 (Non-SCADA) | PGE\C7CF | 2016-12-19 12:00:11.0883496 -08:00 | 013310402 | 013310402 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 528 | 687 | 634 | 792 | {14D21A6D-8317-45C8-8C4C-DA28385B9B5D}
3045 | 2505 | {218A500E-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | SOLANO | Bank 2 | CB 402 (Non-SCADA) | PGE\C7CF | 2016-10-19 17:39:20.7382016 -07:00 | 013140402 | 013140402 | 4 | 3 | 3 | 2 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 396 | 3 | 2.97 | 396 | 3 | 2.97 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {6F64FD29-8521-4BA8-BBE1-5CB64BD14F0B}
3046 | 2506 | {218A5023-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | STUART | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-19 12:40:04.3712098 -08:00 | 013840401 | 013840401 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {3CF3CB25-3C5B-430E-954F-8FD4271FCAF1}
3047 | 2506 | {218A5026-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | STUART | Bank 1 (Non SCADA) | CB 402 (Non-SCADA) | PGE\C7CF | 2016-12-19 12:40:30.8681602 -08:00 | 013840402 | 013840402 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {00E45CF7-D7A6-4485-AE5D-A3C2D43850CD}
3048 | 2506 | {218A5029-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | STUART | Bank 1 (Non SCADA) | CB 403 (Non-SCADA) | PGE\C7CF | 2016-12-19 12:40:43.4599101 -08:00 | 013840403 | 013840403 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {D56768E6-D40D-41D6-BBA4-6C1F4A98E225}
3049 | 2507 | {218A502F-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | STUART | Bank 2 (Non SCADA) | CB 404 (Non-SCADA) | PGE\C7CF | 2016-12-19 12:41:10.7160800 -08:00 | 013840404 | 013840404 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {FF51EFCC-4698-4ECA-93F8-EE1138D92954}
3050 | 2507 | {218A5032-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | STUART | Bank 2 (Non SCADA) | CB 405 (Non-SCADA) | PGE\C7CF | 2016-12-19 12:41:21.8244904 -08:00 | 013840405 | 013840405 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {03408352-8923-4EE3-A026-09B116C2212A}
3051 | 2507 | {218A5035-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | STUART | Bank 2 (Non SCADA) | CB 406 (Non-SCADA) | PGE\C7CF | 2016-12-19 12:41:37.1297266 -08:00 | 013840406 | 013840406 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {03960893-D54A-41FF-AB44-397AB62BE447}
3052 | 2508 | {752A825A-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | SOBRANTE | Bank 3 | CB 1101 | PGE\MFN3 | 2016-11-30 14:32:23.8235230 -08:00 | 0146701101 | 014671101 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 639 | 13.95 | 13.81 | 639 | 13.95 | 13.81 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {C966213C-CE1F-440E-B6AE-AD60C0EC53EC}
3053 | 2508 | {7B5C049A-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | SOBRANTE | Bank 3 | CB 1102 | PGE\MFN3 | 2016-11-30 14:32:38.0506318 -08:00 | 0146701102 | 014671102 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 728 | 15.89 | 15.73 | 728 | 15.89 | 15.73 | 634 | 13.84 | 13.7 | 634 | 13.84 | 13.7 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {1CA17259-86D6-4F41-8DCF-807ADFA672EA}
3055 | 2508 | {A759AB0F-FDB8-11E5-9D37-D4BED91EFF1A} | DIABLO | SOBRANTE | Bank 3 | CB 1103 | PGE\MFN3 | 2016-11-30 14:33:17.1886267 -08:00 | 0146701103 | 014671103 | 8 | 3 | 3 | 1 | 440 | 9.6 | 9.5 | 440 | 9.6 | 9.5 | 606 | 13.23 | 13.1 | 606 | 13.23 | 13.1 | 528 | 11.52 | 11.4 | 528 | 11.52 | 11.4 | 639 | 13.95 | 13.81 | 639 | 13.95 | 13.81 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {E6BDCFC2-09EE-454E-89C0-F2A523B212EA}
3058 | 1239 | {B2D174D1-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | BELLEVUE | Bank 1 | CB 1103 | PGE\DCGa | 2017-07-19 07:39:06.6087238 -07:00 | 43182103 | 043182103 | 8 | 3 | 3 | 1 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | TRUE | 733 | 953 | 879 | 1099 | {59275CE9-2F39-4345-930D-C28396C587A4}
3059 | 2512 | {3C91AE3B-671D-11E5-80CA-005056A729E5} | STOCKTON | MOSHER | Bank 2 | CB 2107 | PGE\BXYD | 2017-01-11 15:10:57.9851706 -08:00 | 1637202107 | 163722107 | 12 | 3 | 3 | 1 | 345 | 13.04 | 12.91 | 327 | 12.36 | 12.24 | 386 | 14.59 | 14.44 | 366 | 13.83 | 13.69 | 443 | 16.74 | 16.57 | 420 | 15.87 | 15.71 | 473 | 17.88 | 17.7 | 449 | 16.97 | 16.8 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {FFDC261D-599D-426D-8939-568A58561F9D}
3060 | 2512 | {464AAEA5-671D-11E5-80CA-005056A729E5} | STOCKTON | MOSHER | Bank 2 | CB 2108 | PGE\BXYD | 2017-01-11 15:11:48.5876034 -08:00 | 1637202108 | 163722108 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {1D66BB4D-9FC2-43DF-A27F-4D2F57898DC1}
3061 | 2384 | {BF2DBEA4-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | FITCH MOUNTAIN | Bank 1 | CB 1111 | PGE\DCGa | 2016-11-18 19:11:02.3318591 -08:00 | 42751111 | 042751111 | 8 | 3 | 3 | 1 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {9DAFBC27-A324-4AF5-83F3-AC420D3A1B83}
3062 | 2384 | {BF2DBEBB-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | FITCH MOUNTAIN | Bank 1 | CB 1112 | PGE\DCGa | 2016-11-18 19:02:37.8801485 -08:00 | 42751112 | 042751112 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {5BB5AA42-940A-44DB-9BD5-2B7BDAA513F2}
3063 | 2513 | {BF2DBECE-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | FITCH MOUNTAIN | Bank 2 | CB 1113 | PGE\DCGa | 2016-11-18 19:40:27.2153449 -08:00 | 42751113 | 042751113 | 8 | 3 | 3 | 1 | 558 | 12.18 | 12.06 | 430 | 9.38 | 9.29 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 516 | 11.26 | 11.15 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 |  |  | FALSE | TRUE | 430 | 559 | 516 | 646 | {A67ADBF0-3C98-4EF9-B7E6-A78C5C376379}
3064 | 2514 | {BF2DBFE9-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | GEYSERVILLE | Bank 1 | CB 1101 | PGE\C8M4 | 2016-11-17 11:48:03.4803505 -08:00 | 0428901101 | 042891101 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 447 | 9.76 | 9.66 | 447 | 9.76 | 9.66 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 429 | 558 | 515 | 644 | {616D9F3E-5B2C-4D34-A4D4-B0C4275D4DEC}
3065 | 2516 | {BF2DC01F-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | GEYSERVILLE | Bank 2 | CB 1102 | PGE\C8M4 | 2016-10-18 09:51:49.0639583 -07:00 | 0428901102 | 042891102 | 8 | 2 | 2 | 1 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 572 | 722 | 687 | 722 | {6036B8DE-94DB-47DB-90E4-13882F718583}
3066 | 2519 | {B1F47D36-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | VIRGINIA | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-19 12:47:03.1351350 -08:00 | 013780401 | 013780401 | 4 | 3 | 3 | 2 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 396 | 3 | 2.97 | 396 | 3 | 2.97 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {5DA98D94-A39E-4C13-90AD-C2F9321C4C0D}
3067 | 2518 | {BF2DC08B-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | MIRABEL | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-18 10:01:27.7017298 -07:00 | 0420901101 | 042091101 | 8 | 3 | 3 | 1 | 430 | 9.38 | 9.29 | 430 | 9.38 | 9.29 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 430 | 559 | 516 | 601 | {E8CAA2AE-E0F7-435E-85F8-BF0FDB1335E9}
3068 | 2517 | {464AAEC2-671D-11E5-80CA-005056A729E5} | STOCKTON | MOSHER | Bank 3 | CB 2110 | PGE\BXYD | 2017-01-11 15:17:04.4634348 -08:00 | 1637202110 | 163722110 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {5118F93F-FC34-4045-ADCC-720B5D23443D}
3069 | 2517 | {464AAECD-671D-11E5-80CA-005056A729E5} | STOCKTON | MOSHER | Bank 3 | CB 2111 | PGE\T1SI | 2017-04-04 14:31:02.9706885 -07:00 | 1637202111 | 163722111 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {C6AF41C4-A5D2-4464-ABF0-CAA4154B1F84}
3071 | 2520 | {B1F47D3F-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | WALDO | WALDO UNIT SUB 401 | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-19 12:48:03.3859343 -08:00 | 013350401 | 013350401 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 428 | 3.24 | 3.21 | 428 | 3.24 | 3.21 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {90B855A3-CDA3-4A8A-8045-4DA1FCFC81AE}
3072 | 2518 | {BF2DC094-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | MIRABEL | Bank 1 | CB 1102 | PGE\C8M4 | 2016-10-18 10:21:39.3734453 -07:00 | 0420901102 | 042091102 | 8 | 3 | 3 | 1 | 430 | 9.38 | 9.29 | 430 | 9.38 | 9.29 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 430 | 559 | 516 | 601 | {F736CDDC-1EA8-4786-BDBC-99F57835CEE0}
3073 | 2521 | {FF83DFB6-2F56-11E6-B38D-D4BED91EFF1A} | EAST BAY | WALDO | WALDO UNIT SUB 402 | CB 402 (Non-SCADA) | PGE\C7CF | 2016-12-19 12:49:02.8057069 -08:00 | 013350402 | 013350402 | 4 | 3 | 3 | 2 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 396 | 3 | 2.97 | 396 | 3 | 2.97 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {973D0344-8172-4D72-85ED-4ECFE888262A}
3074 | 2522 | {B1F47D4E-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | WALL | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-10-19 17:44:39.8052476 -07:00 | 013740401 | 013740401 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 433 | 3.28 | 3.25 | 433 | 3.28 | 3.25 |  |  | FALSE | FALSE | 303 | 395 | 364 | 433 | {F3993587-9853-4AEB-B76D-742354AB3DBE}
3075 | 2523 | {C5614FBF-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | MOLINO | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-18 10:42:35.2378113 -07:00 | 0425701101 | 042571101 | 8 | 3 | 3 | 1 | 572 | 12.48 | 12.36 | 572 | 12.48 | 12.36 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {FBF40A9C-1DF9-4093-B1EA-4DC617415793}
3076 | 2524 | {B1F47D57-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | WOOD | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-10-19 17:45:06.3603622 -07:00 | 013380401 | 013380401 | 4 | 3 | 3 | 2 | 277 | 2.1 | 2.08 | 277 | 2.1 | 2.08 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 333 | 2.52 | 2.49 | 333 | 2.52 | 2.49 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 277 | 360 | 333 | 416 | {D2D1058C-462D-42B1-9112-5E4F18B2F8C4}
3077 | 2515 | {D5F17606-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | EDENVALE | Bank 1 | CB 1101 | PGE\DVN5 | 2016-11-28 10:32:34.5787738 -08:00 | 0829501101 | 082951101 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {E11603A7-ADFB-43EB-A004-351CCB6B430C}
3078 | 2525 | {C5614FEE-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | MOLINO | Bank 2 | CB 1102 | PGE\DCGa | 2016-11-16 17:47:17.8221879 -08:00 | 0425701102 | 042571102 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {034DEE73-00C7-4B52-AF0C-233254CD305F}
3079 | 2525 | {C5615028-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | MOLINO | Bank 2 | CB 1103 | PGE\C8M4 | 2016-10-18 11:13:21.5010253 -07:00 | 0425701103 | 042571103 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {1B8ABE04-BD4E-45FB-BAC4-132DBC344EB1}
3080 | 2525 | {C561504D-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | MOLINO | Bank 2 | CB 1104 | PGE\DCGa | 2016-11-16 17:50:51.3868540 -08:00 | 0425701104 | 042571104 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {B8F429AD-DC9A-4AC7-BBA7-8DEC34DCBADD}
3081 | 2530 | {C5615179-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | MONTE RIO | Bank 1 | CB 1111 | PGE\DCGa | 2017-08-05 16:56:52.6398558 -07:00 | 0428101111 | 042811111 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 434 | 9.47 | 9.38 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {97C891EA-D820-4927-B631-FE7E2035D021}
3082 | 2530 | {C5615190-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | MONTE RIO | Bank 1 | CB 1112 | PGE\DCGa | 2016-11-17 16:04:55.0345576 -08:00 | 0428101112 | 042811112 | 8 | 3 | 3 | 1 | 572 | 12.48 | 12.36 | 572 | 12.48 | 12.36 | 744 | 16.24 | 16.08 | 744 | 16.24 | 16.08 | 687 | 14.99 | 14.84 | 687 | 14.99 | 14.84 | 859 | 18.75 | 18.56 | 859 | 18.75 | 18.56 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {F3C98E31-A0D0-4840-A75F-A7A01F18FB7B}
3084 | 2532 | {C56151A3-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | MONTE RIO | Bank 2 | CB 1113 | PGE\C8M4 | 2016-11-17 15:40:35.8270293 -08:00 | 0428101113 | 042811113 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | TRUE | 722 | 722 | 722 | 722 | {1B7CEF30-0C94-4546-9BCC-D6BA3DE7D8DF}
3085 | 2526 | {218A503E-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND D | Bank 3 | CB 1103 | PGE\C7CF | 2016-11-17 13:24:15.1544547 -08:00 | 0120401103 | 012041103 | 8 | 3 | 3 | 2 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 448 | 9.78 | 9.68 | 448 | 9.78 | 9.68 | 412 | 8.99 | 8.9 | 412 | 8.99 | 8.9 | 461 | 10.06 | 9.96 | 461 | 10.06 | 9.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {4052085C-6D24-4A2F-9FCA-F48FF59B660F}
3086 | 2515 | {D5F17616-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | EDENVALE | Bank 1 | CB 1102 | PGE\DVN5 | 2016-11-28 10:32:48.4828628 -08:00 | 0829501102 | 082951102 | 8 | 3 | 3 | 2 | 475 | 10.37 | 10.27 | 475 | 10.37 | 10.27 | 584 | 12.75 | 12.62 | 584 | 12.75 | 12.62 | 489 | 10.67 | 10.56 | 489 | 10.67 | 10.56 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {60670C09-584C-4865-9E7F-AB96C2EC1393}
3087 | 2526 | {218A5043-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND D | Bank 3 | CB 1117 | PGE\C7CF | 2016-10-19 17:28:15.1502469 -07:00 | 0120401117 | 012041117 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {1E15DD45-8E03-4480-A538-8BFE115872D9}
3088 | 2527 | {218A5057-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND D | Bank 4 - 12kV | CB 1104 | PGE\C7CF | 2016-12-13 10:17:01.9023624 -08:00 | 0120401104 | 012041104 | 8 | 3 | 3 | 2 | 492 | 10.74 | 10.63 | 492 | 10.74 | 10.63 | 554 | 12.09 | 11.97 | 554 | 12.09 | 11.97 | 527 | 11.5 | 11.38 | 527 | 11.5 | 11.38 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {62E04417-A31B-4D94-8918-4B2359F564FF}
3089 | 2527 | {218A5062-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND D | Bank 4 - 12kV | CB 1105 | PGE\C7CF | 2016-12-13 10:17:21.7304708 -08:00 | 0120401105 | 012041105 | 8 | 3 | 3 | 2 | 478 | 10.43 | 10.33 | 478 | 10.43 | 10.33 | 531 | 11.59 | 11.47 | 531 | 11.59 | 11.47 | 492 | 10.74 | 10.63 | 492 | 10.74 | 10.63 | 546 | 11.92 | 11.8 | 546 | 11.92 | 11.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9F64FFA4-809B-4245-849F-A3DB489B7E01}
3090 | 2533 | {CB6B5871-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | PENNGROVE | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-18 12:08:40.7193952 -07:00 | 43471101 | 043471101 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {00000000-0000-0000-0000-000000000000}
3091 | 2527 | {218A506D-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND D | Bank 4 - 12kV | CB 1106 | PGE\C7CF | 2016-11-17 13:33:22.4615810 -08:00 | 0120401106 | 012041106 | 8 | 3 | 3 | 2 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {D753358A-954A-4912-9015-15A022745613}
3092 | 2527 | {218A5084-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND D | Bank 4 - 12kV | CB 1107 | PGE\C7CF | 2016-11-17 13:38:26.0730204 -08:00 | 0120401107 | 012041107 | 8 | 3 | 3 | 2 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {633DE53D-55A0-4090-BF3E-66B1DE80944C}
3093 | 2527 | {2795D017-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND D | Bank 4 - 12kV | CB 1110 | PGE\C7CF | 2016-11-17 13:38:43.8575904 -08:00 | 0120401110 | 012041110 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 592 | 12.92 | 12.79 | 592 | 12.92 | 12.79 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 599 | 13.07 | 12.94 | 599 | 13.07 | 12.94 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {07D742C9-01DB-4DAB-8C52-B13EC14DF2F0}
3094 | 2534 | {6DFF157F-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | JANES CREEK | Bank 1 | CB 1101 | PGE\DCGa | 2016-10-18 12:42:11.9363562 -07:00 | 1923901101 | 192391101 | 8 | 3 | 3 | 2 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 430 | 559 | 516 | 646 | {A7B265FB-C181-4163-BD6D-BB472DBB2929}
3095 | 2534 | {6DFF1596-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | JANES CREEK | Bank 1 | CB 1102 | PGE\DCGa | 2016-10-18 12:42:33.8105402 -07:00 | 1923901102 | 192391102 | 8 | 3 | 3 | 2 | 267 | 5.83 | 5.77 | 267 | 5.83 | 5.77 | 267 | 5.83 | 5.77 | 267 | 5.83 | 5.77 | 267 | 5.83 | 5.77 | 267 | 5.83 | 5.77 | 267 | 5.83 | 5.77 | 267 | 5.83 | 5.77 |  |  | FALSE | TRUE | 430 | 559 | 516 | 646 | {2A357C79-9830-4AAC-88F1-07E048104A1F}
3096 | 2527 | {2795D037-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND D | Bank 4 - 12kV | CB 1115 | PGE\C7CF | 2016-12-13 10:18:19.0319690 -08:00 | 0120401115 | 012041115 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 592 | 12.92 | 12.79 | 592 | 12.92 | 12.79 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 599 | 13.07 | 12.94 | 599 | 13.07 | 12.94 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {C24BAE5C-D592-4EAB-B88B-D51F4F736037}
3097 | 2528 | {2E13720C-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND D | Bank 5 | CB 1101 | PGE\C7CF | 2016-10-19 17:31:24.2957121 -07:00 | 0120401101 | 012041101 | 8 | 3 | 3 | 2 | 360 | 7.86 | 7.78 | 360 | 7.86 | 7.78 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 371 | 8.1 | 8.02 | 371 | 8.1 | 8.02 | 412 | 8.99 | 8.9 | 412 | 8.99 | 8.9 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {D5975888-7BDC-44D0-9C39-4982505D2935}
3098 | 2537 | {D1672E90-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SONOMA | Bank 1 | CB 1102 | PGE\C8M4 | 2016-10-18 12:52:18.9258590 -07:00 | 0427201102 | 042721102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {0090C9D9-0A8D-4DE9-85A4-21A8149714B3}
3099 | 2528 | {2E137211-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND D | Bank 5 | CB 1102 | PGE\C7CF | 2016-12-13 10:18:54.4451300 -08:00 | 0120401102 | 012041102 | 8 | 3 | 3 | 2 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 527 | 11.5 | 11.38 | 527 | 11.5 | 11.38 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {C9F0D1B0-DD39-4F61-9219-488BF9D2F619}
3100 | 2528 | {2E137216-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND D | Bank 5 | CB 1111 | PGE\C7CF | 2016-12-13 10:19:13.7266064 -08:00 | 0120401111 | 012041111 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 592 | 12.92 | 12.79 | 592 | 12.92 | 12.79 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 599 | 13.07 | 12.94 | 599 | 13.07 | 12.94 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {C6EF3AA0-3771-427D-9F4F-C59F1F881041}
3101 | 2528 | {2E137227-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND D | Bank 5 | CB 1112 | PGE\C7CF | 2016-11-17 13:45:21.7259454 -08:00 | 0120401112 | 012041112 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 592 | 12.92 | 12.79 | 592 | 12.92 | 12.79 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 599 | 13.07 | 12.94 | 599 | 13.07 | 12.94 | NOT COMPLETE! UG Cable is 2,1000A-XL |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B1125B7D-9751-4048-B7C9-E854033C4E49}
3102 | 2528 | {342E8258-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND D | Bank 5 | CB 1116 | PGE\C7CF | 2016-12-13 10:19:34.3964739 -08:00 | 0120401116 | 012041116 | 8 | 3 | 3 | 2 | 427 | 9.32 | 9.23 | 427 | 9.32 | 9.23 | 474 | 10.34 | 10.24 | 474 | 10.34 | 10.24 | 440 | 9.6 | 9.5 | 440 | 9.6 | 9.5 | 488 | 10.65 | 10.54 | 488 | 10.65 | 10.54 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {526D4D8C-DA86-4945-A56C-0DE8559A3F13}
3103 | 2537 | {D1672E99-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SONOMA | Bank 1 | CB 1103 | PGE\C8M4 | 2016-10-18 13:58:48.3905020 -07:00 | 0427201103 | 042721103 | 8 | 3 | 3 | 1 | 477 | 10.41 | 10.31 | 440 | 9.6 | 9.5 | 600 | 13.09 | 12.96 | 578 | 12.61 | 12.48 | 528 | 11.52 | 11.4 | 528 | 11.52 | 11.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {9988AC29-F7D8-4659-97C7-3580DDBF5A93}
3104 | 2529 | {342E8263-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND D | Bank 6 | CB 1130 | PGE\C7CF | 2016-12-13 10:23:40.3483329 -08:00 | 0120401130 | 012041130 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {0519D980-7C38-4218-A27D-A1B461425332}
3105 | 2529 | {342E8275-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND D | Bank 6 | CB 1131 | PGE\C7CF | 2016-12-13 10:28:37.4863682 -08:00 | 0120401131 | 012041131 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {25D1624B-4A6A-4B01-8977-440E46CD0E98}
3106 | 2529 | {3A5B93CC-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND D | Bank 6 | CB 1132 | PGE\C7CF | 2016-12-13 10:31:04.9830109 -08:00 | 0120401132 | 012041132 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {FE385F42-8116-4D50-9E09-4E63BBEFEE97}
3107 | 2515 | {D5F17626-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | EDENVALE | Bank 1 | CB 1103 | PGE\DVN5 | 2016-11-28 10:33:26.0544052 -08:00 | 0829501103 | 082951103 | 8 | 3 | 3 | 2 | 581 | 12.68 | 12.55 | 581 | 12.68 | 12.55 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {550B41FD-7232-44A5-A7DF-9697B8EF2259}
3108 | 2529 | {3A5B93D2-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND D | Bank 6 | CB 1133 | PGE\C7CF | 2016-12-13 10:32:49.0430675 -08:00 | 0120401133 | 012041133 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {DF098164-2EB8-4CB8-AC12-B292FD689DA9}
3109 | 2540 | {464AAFB9-671D-11E5-80CA-005056A729E5} | STOCKTON | STAGG | Bank 3 | CB 1103 | PGE\BXYD | 2017-01-11 10:45:05.4495877 -08:00 | 1624201103 | 162421103 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1200 | 1440 | 1200 | 1440 | {EF4DAA20-945E-49AB-8C53-A9C4B579D6E8}
3110 | 2539 | {EEFC7476-671D-11E5-80CA-005056A729E5} | KERN | 7TH STANDARD | Bank 1 | CB 2101 | PGE\BXYD | 2016-10-18 14:25:57.0441275 -07:00 | 2545802101 | 254582101 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {03E9D448-018C-4F97-B13F-50D8996AD7D3}
3112 | 2540 | {464AAFC1-671D-11E5-80CA-005056A729E5} | STOCKTON | STAGG | Bank 3 | CB 1105 | PGE\BXYD | 2017-01-11 10:46:23.4812879 -08:00 | 1624201105 | 162421105 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1200 | 1440 | 1200 | 1440 | {293C5E31-AD96-47B6-B00E-3982A61377BE}
3114 | 2539 | {EEFC747B-671D-11E5-80CA-005056A729E5} | KERN | 7TH STANDARD | Bank 1 | CB 2102 | PGE\BXYD | 2016-10-18 14:25:45.2776559 -07:00 | 2545802102 | 254582102 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {986F2D46-954C-4FE4-B548-DD47736E34CF}
3115 | 2537 | {D1672EB0-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SONOMA | Bank 1 | CB 1104 | PGE\C8M4 | 2016-10-18 14:03:41.9892180 -07:00 | 0427201104 | 042721104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {658C863F-5BFA-4F4A-9168-C311EE3320F9}
3116 | 2539 | {EEFC7489-671D-11E5-80CA-005056A729E5} | KERN | 7TH STANDARD | Bank 1 | CB 2103 | PGE\BXYD | 2016-10-18 14:25:35.1029351 -07:00 | 2545802103 | 254582103 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {5CED59E6-DD2F-4E47-AA46-DF84DB232FFF}
3117 | 2543 | {D1672ECA-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SONOMA | Bank 2 | CB 1105 | PGE\C8M4 | 2016-10-18 14:26:21.9814839 -07:00 | 0427201105 | 042721105 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {70553593-057F-46A6-80BD-81DC10963C72}
3118 | 2542 | {4D5B04C2-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND I | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-15 10:31:57.8508225 -08:00 | 012080401 | 012080401 | 4 | 3 | 3 | 2 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 384 | 2.91 | 2.88 | 384 | 2.91 | 2.88 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {5F08C6AF-8FC8-4F5C-B60C-7EB8C2814BED}
3119 | 2545 | {D7085D4A-671D-11E5-80CA-005056A729E5} | KERN | ANTELOPE | Bank 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\BXYD | 2016-10-18 14:32:39.2249533 -07:00 | 2520201101 | 252021101 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 481 | 625 | 577 | 702 | {19834F58-5F01-4385-A3DC-9493ECBB30D0}
3120 | 2543 | {D1672EEF-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SONOMA | Bank 2 | CB 1106 | PGE\C8M4 | 2016-10-18 14:32:44.7636278 -07:00 | 0427201106 | 042721106 | 8 | 2 | 2 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {33E00EE0-6401-494A-A3D7-2D9DB4DDFE31}
3121 | 2545 | {D7085D56-671D-11E5-80CA-005056A729E5} | KERN | ANTELOPE | Bank 1 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\BXYD | 2016-10-18 14:33:56.3868240 -07:00 | 2520201102 | 252021102 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 481 | 625 | 577 | 702 | {0B19843A-D8E8-4F41-9980-2E828068A81B}
3122 | 2544 | {4D5B04C8-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND I | Bank 2 (Non SCADA) | CB 402 (Non-SCADA) | PGE\C7CF | 2016-12-15 10:32:28.6777021 -08:00 | 012080402 | 012080402 | 4 | 3 | 3 | 2 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 384 | 2.91 | 2.88 | 384 | 2.91 | 2.88 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {D00F78B4-B75F-409B-9567-BE6DAAAA389A}
3123 | 2543 | {D1672EF8-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SONOMA | Bank 2 | CB 1107 | PGE\C8M4 | 2016-10-18 14:38:05.1344000 -07:00 | 0427201107 | 042721107 | 8 | 2 | 2 | 1 | 345 | 7.53 | 7.45 | 345 | 7.53 | 7.45 | 386 | 8.42 | 8.34 | 386 | 8.42 | 8.34 | 443 | 9.67 | 9.57 | 443 | 9.67 | 9.57 | 473 | 10.32 | 10.22 | 473 | 10.32 | 10.22 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {507DA2EE-78CC-4705-A1CA-C6018CDF797C}
3124 | 2546 | {0DDAA05D-5FD1-11E6-9BE4-80000BC6CD8D} | SACRAMENTO | CORDELIA | BANK 3 | CB 1104 | PGE\TEJ2 | 2016-10-18 14:51:27.4466051 -07:00 | 062701104 | 062701104 | 8 | 3 | 3 | 1 | 636 | 13.88 | 13.74 | 636 | 13.88 | 13.74 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {4AC05CAE-C6F3-4FA6-951D-6EE74883502A}
3125 | 2548 | {D7085D5F-671D-11E5-80CA-005056A729E5} | KERN | ARVIN | Bank 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\BXYD | 2016-10-18 14:53:06.0080782 -07:00 | 2538001101 | 253801101 | 8 | 3 | 3 | 1 | 512 | 11.17 | 11.06 | 512 | 11.17 | 11.06 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 512 | 666 | 615 | 702 | {4BACDEDE-35E2-4556-81CB-7AADEC6FBCA6}
3126 | 2548 | {D7085D71-671D-11E5-80CA-005056A729E5} | KERN | ARVIN | Bank 1 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\BXYD | 2016-10-18 14:56:22.1660618 -07:00 | 2538001102 | 253801102 | 8 | 3 | 3 | 1 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 |  |  | FALSE | FALSE | 512 | 666 | 615 | 702 | {302BAC59-0031-42DA-8DB2-6F6E4EF12686}
3127 | 2548 | {D7085D77-671D-11E5-80CA-005056A729E5} | KERN | ARVIN | Bank 1 (Non SCADA) | CB 1103 (Non-SCADA) | PGE\BXYD | 2016-10-18 14:58:20.1500256 -07:00 | 2538001103 | 253801103 | 8 | 3 | 3 | 1 | 512 | 11.17 | 11.06 | 512 | 11.17 | 11.06 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 512 | 666 | 615 | 702 | {DEDE0DCE-E1C3-46B9-9499-898D81CF474E}
3128 | 2546 | {24B4C9A3-5FD1-11E6-9BE4-80000BC6CD8D} | SACRAMENTO | CORDELIA | BANK 3 | CB 1110 | PGE\TEJ2 | 2016-10-18 14:59:29.3823648 -07:00 | 062701110 | 062701110 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9F85688D-37DE-4B35-A034-E2EB82EDEA71}
3129 | 2550 | {CB6B596A-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | RINCON | Bank 1 | CB 1101 | PGE\RVS7 | 2017-06-20 12:43:44.1308897 -07:00 | 0433201101 | 043321101 | 8 | 2 | 2 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {F366191E-BF6C-4BB3-BEA2-3A969F029C4B}
3130 | 2550 | {CB6B5984-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | RINCON | Bank 1 | CB 1102 | PGE\C8M4 | 2016-10-18 15:10:59.1506792 -07:00 | 0433201102 | 043321102 | 8 | 2 | 2 | 1 | 534 | 11.65 | 11.53 | 534 | 11.65 | 11.53 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 591 | 12.9 | 12.77 | 591 | 12.9 | 12.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {BC8EF6C1-273A-44E6-8CBF-C3B005BA7103}
3131 | 2541 | {D5F17639-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | EDENVALE | Bank 2 | CB 2106 | PGE\DVN5 | 2016-11-28 10:58:14.0615494 -08:00 | 0829502106 | 082952106 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {DF01ABDA-F971-4E1A-8D5E-2B6BE6C4B8DF}
3132 | 2551 | {CB6B599E-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | RINCON | Bank 2 | CB 1103 | PGE\C8M4 | 2016-10-18 15:17:47.6106290 -07:00 | 0433201103 | 043321103 | 8 | 2 | 2 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {5E583D13-E835-4A91-BBFD-CD429A20C145}
3134 | 2551 | {CB6B59D1-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | RINCON | Bank 2 | CB 1104 | PGE\C8M4 | 2016-10-18 15:21:14.2517869 -07:00 | 0433201104 | 043321104 | 8 | 2 | 2 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {01285DCA-CC9F-4B16-A676-BD5BC9F2FDD9}
3136 | 2552 | {D7085D80-671D-11E5-80CA-005056A729E5} | KERN | BAKERSFIELD | Bank 1 | CB 2104 | PGE\BXYD | 2017-01-20 09:22:12.9155040 -08:00 | 2533702104 | 253372104 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {D91FD17D-F9EF-45C1-909D-0662518F5276}
3137 | 2554 | {D7085DAC-671D-11E5-80CA-005056A729E5} | KERN | BAKERSFIELD | Bank 2 | CB 2106 | PGE\BXYD | 2017-01-20 09:29:07.3842744 -08:00 | 2533702106 | 253372106 | 12 | 3 | 3 | 1 | 584 | 22.07 | 21.85 | 584 | 22.07 | 21.85 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 647 | 24.45 | 24.21 | 647 | 24.45 | 24.21 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {E1069098-4FB1-4C7A-A767-C818461862CF}
3138 | 2554 | {2717D540-A5BE-11E5-A1F0-D4BED91EFF1A} | KERN | BAKERSFIELD | Bank 2 | CB 2107 | PGE\BXYD | 2017-01-20 09:29:35.8392216 -08:00 | 2533702107 | 253372107 | 12 | 3 | 3 | 1 | 515 | 19.46 | 19.27 | 489 | 18.48 | 18.3 | 578 | 21.84 | 21.62 | 549 | 20.75 | 20.54 | 634 | 23.96 | 23.72 | 632 | 23.89 | 23.65 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {C359F718-FABC-4203-9976-827691EE6F9E}
3139 | 2553 | {72FF920F-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND L | Bank 1 | CB 1101 (Non-SCADA) | PGE\C7CF | 2016-10-18 16:48:16.4802287 -07:00 | 0121101101 | 012111101 | 8 | 3 | 3 | 2 | 383 | 8.36 | 8.28 | 383 | 8.36 | 8.28 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 | 394 | 8.6 | 8.51 | 394 | 8.6 | 8.51 | 438 | 9.56 | 9.46 | 438 | 9.56 | 9.46 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {005313EF-52ED-436C-B4C7-35E88FA3F23D}
3140 | 2554 | {2717D543-A5BE-11E5-A1F0-D4BED91EFF1A} | KERN | BAKERSFIELD | Bank 2 | CB 2108 | PGE\BXYD | 2017-01-20 09:30:26.5401966 -08:00 | 2533702108 | 253372108 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {F97BED75-4C09-4208-A749-38AA9E9DB461}
3141 | 2538 | {6DFF15A9-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | JANES CREEK | Bank 2 | CB 1103 | PGE\DCGa | 2016-10-18 16:51:48.6887030 -07:00 | 1923901103 | 192391103 | 8 | 3 | 3 | 2 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | TRUE | 722 | 722 | 722 | 722 | {45485062-B45B-412A-98D6-03E3F3FCAC68}
3143 | 4773 | {794386C2-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND L | Bank 1 | CB 1102 (Non-SCADA) | PGE\MFN3 | 2017-07-13 10:57:49.3723619 -07:00 | 0121101102 | 012111102 | 7 | 3 | 3 | 2 | 475 | 10.26 | 10.16 | 290 | 6.26 | 6.2 | 500 | 10.8 | 10.69 | 290 | 6.26 | 6.2 | 489 | 10.56 | 10.45 | 290 | 6.26 | 6.2 | 500 | 10.8 | 10.69 | 290 | 6.26 | 6.2 | L 1102 or C 1120 reserve capacity for POO 185 amps 07.13.17 ; currently reserved on L1102 |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {9516495B-00DC-44D2-AFB6-A2AC4C66053D}
3144 | 2556 | {CB6B59FC-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | SALMON CREEK | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-18 16:15:26.1389732 -07:00 | 0431601101 | 043161101 | 8 | 2 | 2 | 2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {8BA61389-DB8B-4454-9C7C-7CA80EA2EE84}
3145 | 2553 | {7F4D3201-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND L | Bank 1 | CB 1107 (Non-SCADA) | PGE\C7CF | 2016-12-19 09:21:55.6609726 -08:00 | 0121101107 | 012111107 | 8 | 3 | 3 | 2 | 478 | 10.43 | 10.33 | 478 | 10.43 | 10.33 | 531 | 11.59 | 11.47 | 531 | 11.59 | 11.47 | 492 | 10.74 | 10.63 | 492 | 10.74 | 10.63 | 546 | 11.92 | 11.8 | 546 | 11.92 | 11.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {3E893CA4-61C1-4D45-85F8-5E34DF3A3056}
3146 | 2557 | {7A8F2399-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | UPPER LAKE | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-18 16:32:41.2576682 -07:00 | 0428701101 | 042871101 | 8 | 3 | 3 | 2 | 158 | 3.45 | 3.42 | 158 | 3.45 | 3.42 | 205 | 4.47 | 4.43 | 205 | 4.47 | 4.43 | 189 | 4.12 | 4.08 | 189 | 4.12 | 4.08 | 237 | 5.17 | 5.12 | 237 | 5.17 | 5.12 |  |  | FALSE | FALSE | 158 | 205 | 189 | 237 | {2F0EB00F-D81F-4E09-8D82-8327E00B602E}
3147 | 2558 | {D7085DCF-671D-11E5-80CA-005056A729E5} | KERN | BAKERSFIELD | Bank 3 | CB 2109 | PGE\BXYD | 2016-10-18 16:36:17.2225928 -07:00 | 2533702109 | 253372109 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 3436 | 4467 | 4123 | 5154 | {5ACA8D40-BFF3-437F-9B87-C51DA1CBC859}
3148 | 2553 | {1EF20AEA-22D1-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND L | Bank 1 | CB 1111 | PGE\C7CF | 2016-10-18 16:47:34.0895947 -07:00 | 0121101111 | 012111111 | 8 | 3 | 3 | 2 | 445 | 9.71 | 9.61 | 445 | 9.71 | 9.61 | 494 | 10.78 | 10.67 | 494 | 10.78 | 10.67 | 458 | 10 | 9.9 | 458 | 10 | 9.9 | 509 | 11.11 | 11 | 509 | 11.11 | 11 | Network Feeder |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {25E8DFA2-C27E-4E0E-91CA-26229FAEC94E}
3149 | 2538 | {6DFF15C7-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | JANES CREEK | Bank 2 | CB 1104 | PGE\DCGa | 2017-01-25 09:47:52.6755839 -08:00 | 1923901104 | 192391104 | 8 | 3 | 3 | 2 | 468 | 10.21 | 10.11 | 468 | 10.21 | 10.11 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | TRUE | 722 | 722 | 722 | 722 | {553C19E1-96E8-4DCE-BFE8-3CD07EF52D37}
3152 | 2559 | {7A8F235E-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | UKIAH | Bank 1 | CB 1113 | PGE\C8M4 | 2016-10-18 16:49:35.1575865 -07:00 | 0427701113 | 042771113 | 8 | 2 | 2 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {37CF34BA-35F4-4600-A8CD-D65B6A3B8FA3}
3153 | 2559 | {7A8F2367-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | UKIAH | Bank 1 | CB 1114 | PGE\C8M4 | 2016-10-18 16:50:48.9222140 -07:00 | 0427701114 | 042771114 | 8 | 2 | 2 | 1 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 520 | 11.35 | 11.24 | 520 | 11.35 | 11.24 | 599 | 13.07 | 12.94 | 599 | 13.07 | 12.94 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {519BD643-2362-4BAF-B58F-D855D55B83C8}
3154 | 2559 | {7A8F2370-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | UKIAH | Bank 1 | CB 1115 | PGE\DCGa | 2017-03-23 11:53:12.5260731 -07:00 | 0427701115 | 042771115 | 8 | 2 | 2 | 1 | 500 | 10.91 | 10.8 | 357 | 7.79 | 7.71 | 500 | 10.91 | 10.8 | 399 | 8.71 | 8.62 | 500 | 10.91 | 10.8 | 457 | 9.97 | 9.87 | 500 | 10.91 | 10.8 | 489 | 10.67 | 10.56 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {E62944D0-73EE-4D24-B56B-71C3ECB5D421}
3155 | 2560 | {7A8F2383-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | UKIAH | Bank 2 | CB 1111 | PGE\C8M4 | 2016-10-18 16:57:44.4381049 -07:00 | 0427701111 | 042771111 | 8 | 2 | 2 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | TRUE | 572 | 744 | 687 | 859 | {C3248621-F2E1-4AF7-A800-A7C7DBC2D51A}
3156 | 2553 | {1EF20AF6-22D1-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND L | Bank 1 | CB 1112 | PGE\C7CF | 2016-10-18 17:06:53.3890510 -07:00 | 0121101112 | 012111112 | 8 | 3 | 3 | 2 | 445 | 9.71 | 9.61 | 445 | 9.71 | 9.61 | 494 | 10.78 | 10.67 | 494 | 10.78 | 10.67 | 458 | 10 | 9.9 | 458 | 10 | 9.9 | 509 | 11.11 | 11 | 509 | 11.11 | 11 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {C6A0F060-CE04-4DF5-AA2B-46EB49711658}
3157 | 2553 | {26F5EF85-22D1-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND L | Bank 1 | CB 1113 | PGE\C7CF | 2016-10-18 17:33:05.4987174 -07:00 | 0121101113 | 012111113 | 8 | 3 | 3 | 2 | 445 | 9.71 | 9.61 | 445 | 9.71 | 9.61 | 494 | 10.78 | 10.67 | 494 | 10.78 | 10.67 | 458 | 10 | 9.9 | 458 | 10 | 9.9 | 509 | 11.11 | 11 | 509 | 11.11 | 11 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {287DFD54-64D8-4B8A-9FB8-3AAB4456406D}
3158 | 2562 | {7A8F2331-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | TRINIDAD | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-18 18:19:56.7295580 -07:00 | 192231101 | 192231101 | 8 | 2 | 2 | 2 | 201 | 4.39 | 4.35 | 201 | 4.39 | 4.35 | 227 | 4.95 | 4.9 | 227 | 4.95 | 4.9 | 230 | 5.02 | 4.97 | 230 | 5.02 | 4.97 | 230 | 5.02 | 4.97 | 230 | 5.02 | 4.97 |  |  | FALSE | FALSE | 385 | 385 | 385 | 385 | {D05F0091-523B-46E6-B80C-102C2C106084}
3159 | 2562 | {7A8F2341-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | TRINIDAD | Bank 1 | CB 1102 | PGE\C8M4 | 2016-10-18 18:22:00.8415008 -07:00 | 192231102 | 192231102 | 8 | 2 | 2 | 2 | 201 | 4.39 | 4.35 | 201 | 4.39 | 4.35 | 227 | 4.95 | 4.9 | 227 | 4.95 | 4.9 | 230 | 5.02 | 4.97 | 230 | 5.02 | 4.97 | 230 | 5.02 | 4.97 | 230 | 5.02 | 4.97 |  |  | FALSE | FALSE | 385 | 385 | 385 | 385 | {1D135121-9796-4763-8D74-55EDC8769171}
3160 | 2561 | {612483B0-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | FORT SEWARD | Bank 1 | CB 1121 | PGE\DCGa | 2017-04-23 12:33:51.1951878 -07:00 | 1923201121 | 192321121 | 8 | 3 | 3 | 1 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | QA COMPLETED BY DCGA ON 04/22/17 |  | FALSE | TRUE | 274 | 300 | 300 | 300 | {C873B7F7-158B-4ACE-8280-55EA3F104F6A}
3161 | 2561 | {612483C7-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | FORT SEWARD | Bank 1 | CB 1122 | PGE\DCGa | 2017-04-23 12:34:21.1789644 -07:00 | 1923201122 | 192321122 | 8 | 3 | 3 | 1 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | QA COMPLETED BY DCGA ON 04/22/17 |  | FALSE | TRUE | 274 | 300 | 300 | 300 | {2E8BDAD7-4547-45A0-94F8-DEABB65720BF}
3162 | 2482 | {612482E2-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | EUREKA A | Bank 1 | CB 1106 | PGE\DCGa | 2017-02-28 16:26:54.7465960 -08:00 | 1921201106 | 192121106 | 8 | 3 | 3 | 2 | 492 | 10.74 | 10.63 | 306 | 6.68 | 6.61 | 500 | 10.91 | 10.8 | 416 | 9.08 | 8.99 | 500 | 10.91 | 10.8 | 348 | 7.59 | 7.51 | 500 | 10.91 | 10.8 | 442 | 9.65 | 9.55 |  |  | FALSE | TRUE | 572 | 744 | 687 | 859 | {07A94600-0CA2-4631-A95B-64D38FD594EF}
3163 | 2482 | {612482EB-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | EUREKA A | Bank 1 | CB 1107 | PGE\C8M4 | 2016-11-18 11:55:15.3207177 -08:00 | 1921201107 | 192121107 | 8 | 4 | 3 | 2 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | TRUE | 572 | 744 | 687 | 859 | {FD55FE29-80C6-4F48-A598-A317111F26AD}
3164 | 2563 | {4829E61A-0BDF-11E6-9D37-D4BED91EFF1A} | SONOMA | FORT ROSS | BANK 1 | CB 1121 (Non-SCADA) | PGE\DCGa | 2016-10-18 20:27:35.4952974 -07:00 | 0428501121 | 042851121 | 8 | 3 | 3 | 2 | 100 | 2.18 | 2.16 | 91 | 1.99 | 1.97 | 130 | 2.84 | 2.81 | 119 | 2.6 | 2.57 | 120 | 2.62 | 2.59 | 110 | 2.4 | 2.38 | 150 | 3.27 | 3.24 | 137 | 2.99 | 2.96 | **NEED TO ADD 1-3PH 7.62KV 250KVA 65C REG TO LIBRARY |  | FALSE | TRUE | 91 | 119 | 110 | 137 | {04AF6A6B-50B9-4795-BC65-E0640B277576}
3165 | 2564 | {61248308-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | EUREKA E | Bank 1 | CB 1101 | PGE\C8M4 | 2016-11-18 12:26:11.8731523 -08:00 | 1923301101 | 192331101 | 8 | 3 | 3 | 2 | 492 | 10.74 | 10.63 | 492 | 10.74 | 10.63 | 554 | 12.09 | 11.97 | 554 | 12.09 | 11.97 | 560 | 12.22 | 12.1 | 560 | 12.22 | 12.1 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {7935EA8F-F662-45AA-BE02-32ECBE4067D0}
3166 | 2564 | {61248318-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | EUREKA E | Bank 1 | CB 1104 | PGE\C8M4 | 2016-10-18 19:30:53.1850139 -07:00 | 1923301104 | 192331104 | 8 | 3 | 3 | 2 | 492 | 10.74 | 10.63 | 492 | 10.74 | 10.63 | 554 | 12.09 | 11.97 | 554 | 12.09 | 11.97 | 560 | 12.22 | 12.1 | 560 | 12.22 | 12.1 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 |  |  | FALSE | TRUE | 962 | 1250 | 1154 | 1443 | {FE989355-00C2-4670-B81B-6C00546F1111}
3167 | 2564 | {61248337-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | EUREKA E | Bank 1 | CB 1105 | PGE\DCGa | 2017-02-28 11:42:50.2309019 -08:00 | 1923301105 | 192331105 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 369 | 8.05 | 7.97 | 600 | 13.09 | 12.96 | 414 | 9.04 | 8.95 | 600 | 13.09 | 12.96 | 415 | 9.06 | 8.97 | 600 | 13.09 | 12.96 | 443 | 9.67 | 9.57 |  |  | FALSE | TRUE | 962 | 1250 | 1154 | 1440 | {00A41D71-669E-4080-8239-3350A6FC108D}
3169 | 2541 | {D5F1767B-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | EDENVALE | Bank 2 | CB 2107 | PGE\DVN5 | 2016-11-28 11:07:49.0383726 -08:00 | 0829502107 | 082952107 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {443D5462-5373-4BB9-8846-71BFD1CF963F}
3171 | 2570 | {620DC9B1-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | MAXWELL | Bank 1 | CB 1102 | PGE\TEJ2 | 2016-10-19 08:51:52.7083237 -07:00 | 0628801102 | 062881102 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 447 | 9.76 | 9.66 | 447 | 9.76 | 9.66 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 577 | 722 | 692 | 722 | {452D01F2-F629-4136-A89D-2B91FA0381D2}
3172 | 2571 | {DD064219-671D-11E5-80CA-005056A729E5} | KERN | BAKERSFIELD | Bank 4 | CB 1101 | PGE\BXYD | 2016-10-19 08:52:29.1600817 -07:00 | 2533701101 | 253371101 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1603 | 2079 | 1924 | 2079 | {6EB8A7BE-C0F0-478D-96C0-35FCC36F63ED}
3173 | 2571 | {DD06421E-671D-11E5-80CA-005056A729E5} | KERN | BAKERSFIELD | Bank 4 | CB 1105 | PGE\BXYD | 2016-10-19 08:54:22.1328499 -07:00 | 2533701105 | 253371105 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1603 | 2079 | 1924 | 2079 | {375E70CE-2A86-4B02-9D8B-F4B630197E1D}
3174 | 2571 | {DD064223-671D-11E5-80CA-005056A729E5} | KERN | BAKERSFIELD | Bank 4 | CB 1107 | PGE\BXYD | 2016-10-19 08:58:27.5082741 -07:00 | 2533701107 | 253371107 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1603 | 2079 | 1924 | 2079 | {CECF0D40-7E80-42C5-A00C-0A3D28CE0A81}
3175 | 2571 | {DD064231-671D-11E5-80CA-005056A729E5} | KERN | BAKERSFIELD | Bank 4 | CB 1115 | PGE\BXYD | 2016-10-19 09:00:03.2916470 -07:00 | 2533701115 | 253371115 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1603 | 2079 | 1924 | 2079 | {0E6B3510-EEAC-4075-8492-0EF249B2A9FA}
3177 | 2572 | {DD06423C-671D-11E5-80CA-005056A729E5} | KERN | BAKERSFIELD | Bank 5 (Non SCADA) | CB 1114 | PGE\BXYD | 2017-01-20 09:39:26.6849838 -08:00 | 2533701114 | 253371114 | 8 | 3 | 3 | 1 | 397 | 8.66 | 8.57 | 397 | 8.66 | 8.57 | 486 | 10.61 | 10.5 | 461 | 10.06 | 9.96 | 409 | 8.93 | 8.84 | 409 | 8.93 | 8.84 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | Circuit Cap: Summer Norm/Emerg=478/535; Winter Norm/Emerg=541/600 |  | FALSE | FALSE | 1603 | 2078 | 1924 | 2078 | {1561A836-5C4D-4893-8022-A945016DDE09}
3178 | 2575 | {6DFF15F3-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | LAYTONVILLE | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-19 10:00:15.4501154 -07:00 | 0426801101 | 042681101 | 8 | 3 | 3 | 1 | 231 | 5.04 | 4.99 | 231 | 5.04 | 4.99 | 252 | 5.5 | 5.44 | 252 | 5.5 | 5.44 | 287 | 6.26 | 6.2 | 287 | 6.26 | 6.2 | 303 | 6.61 | 6.54 | 303 | 6.61 | 6.54 |  |  | FALSE | TRUE | 481 | 481 | 481 | 481 | {86A23848-59E1-4EAF-A268-23E0F457AED5}
3604 | 2786 | {A3EB5BDE-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | RESERVATION ROAD | Bank 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\ACT0 | 2016-10-26 14:28:49.6942727 -07:00 | 1827301101 | 182731101 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {8C50A87E-8407-452C-A5E6-A3D9E9C32D45}
3606 | 2785 | {E3005921-671D-11E5-80CA-005056A729E5} | KERN | KERN OIL | Bank 2 | CB 1116 | PGE\BXYD | 2016-11-29 08:50:56.0229245 -08:00 | 2527201116 | 252721116 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {C6AA2E22-DD58-4DC1-BBFE-FF1CB9AA9807}
3607 | 2786 | {A3EB5BE4-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | RESERVATION ROAD | Bank 1 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\ACT0 | 2016-10-26 14:38:36.8869042 -07:00 | 1827301102 | 182731102 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {F449AA84-1A82-47A4-A089-49F16D929A92}
3608 | 2789 | {464AAFF9-671D-11E5-80CA-005056A729E5} | STOCKTON | STAGG | Bank 6 | CB 2106 | PGE\BXYD | 2017-01-11 11:21:37.9968424 -08:00 | 1624202106 | 162422106 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {27003B5D-0DE5-42BD-A70B-CAF29803C053}
3609 | 2789 | {464AB00E-671D-11E5-80CA-005056A729E5} | STOCKTON | STAGG | Bank 6 | CB 2107 | PGE\BXYD | 2017-01-11 11:23:39.9584242 -08:00 | 1624202107 | 162422107 | 12 | 3 | 3 | 1 | 540 | 20.41 | 20.21 | 540 | 20.41 | 20.21 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 598 | 22.6 | 22.37 | 598 | 22.6 | 22.37 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {D1042D71-2295-4081-AC50-D496E805650F}
3610 | 2789 | {464AB01F-671D-11E5-80CA-005056A729E5} | STOCKTON | STAGG | Bank 6 | CB 2108 | PGE\BXYD | 2017-01-11 11:24:30.7523498 -08:00 | 1624202108 | 162422108 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {548BBCEB-6FD4-4D98-A6BB-64D142BCB6DE}
3611 | 2782 | {959A7E7A-3D5A-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | RANDOLPH | BANK 402 (Non SCADA) | CB 402 (Non-SCADA) | PGE\DMAL | 2017-05-12 18:52:44.8834943 -07:00 | 022590402 | 022590402 | 3 | 3 | 3 | 2 | 319 | 2.3 | 2.28 | 319 | 2.3 | 2.28 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 383 | 2.76 | 2.73 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 319 | 414 | 383 | 478 | {7D3A56AB-88C0-4C9D-927D-4AC219E5BBF0}
3179 | 2501 | {3605317F-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | KING CITY | Bank 3 | CB 1101 | PGE\ACT0 | 2016-10-19 10:02:26.4203787 -07:00 | 1820301101 | 182031101 | 8 | 3 | 1 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {6D266A9D-C6B9-4027-8830-58FD42F3529B}
3180 | 2575 | {6DFF160A-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | LAYTONVILLE | Bank 1 | CB 1102 | PGE\C8M4 | 2016-10-19 10:05:07.7111133 -07:00 | 0426801102 | 042681102 | 8 | 2 | 3 | 1 | 367 | 8.01 | 7.93 | 367 | 8.01 | 7.93 | 367 | 8.01 | 7.93 | 367 | 8.01 | 7.93 | 367 | 8.01 | 7.93 | 367 | 8.01 | 7.93 | 367 | 8.01 | 7.93 | 367 | 8.01 | 7.93 |  |  | FALSE | TRUE | 481 | 481 | 481 | 481 | {EB77E272-AC76-475D-BDE0-756C94FAADB0}
3181 | 2576 | {6DFF1627-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | LOW GAP | Bank 1 | CB 1101 | PGE\DCGa | 2017-04-27 08:34:53.5330725 -07:00 | 192411101 | 192411101 | 8 | 3 | 3 | 2 | 137 | 2.99 | 2.96 | 137 | 2.99 | 2.96 | 179 | 3.91 | 3.87 | 179 | 3.91 | 3.87 | 165 | 3.6 | 3.56 | 165 | 3.6 | 3.56 | 206 | 4.5 | 4.46 | 206 | 4.5 | 4.46 | QA COMPLETED BY DCGA ON 04/27/2017 |  | FALSE | TRUE | 160 | 208 | 192 | 240 | {811C996B-4979-4489-88CF-D0A8395B8B70}
3182 | 2577 | {742E10C7-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | LUCERNE | Bank 1 | CB 1103 | PGE\C8M4 | 2016-10-19 10:45:16.2758464 -07:00 | 0433501103 | 043351103 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 345 | 7.53 | 7.45 | 578 | 12.61 | 12.48 | 386 | 8.42 | 8.34 | 557 | 12.16 | 12.04 | 443 | 9.67 | 9.57 | 600 | 13.09 | 12.96 | 473 | 10.32 | 10.22 | OPERATING AND PLANNING CAPABILITY SHOULD BE 503/600/557/600 UNDER NORMAL CONDITIONS |  | FALSE | TRUE | 572 | 744 | 687 | 859 | {3BF52F48-2084-4AFD-A7AA-B3239DB3CE9D}
3183 | 2578 | {8E5DEFAD-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | BRUNSWICK | Bank 1 | CB 1102 | PGE\RVS7 | 2016-10-19 10:58:08.6607086 -07:00 | 1524801102 | 152481102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | *Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. Actual Capability is 620 Amps. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {B9839F3A-64C5-47BF-988C-CA29D4F4AE5B}
3184 | 2578 | {8E5DEFBD-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | BRUNSWICK | Bank 1 | CB 1103 | PGE\RVS7 | 2016-11-22 10:41:11.9845430 -08:00 | 1524801103 | 152481103 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | * Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300 |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {FFE67317-164C-484A-A565-36044F17A92F}
3185 | 2579 | {742E10E8-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | LUCERNE | Bank 2 | CB 1106 | PGE\C8M4 | 2016-10-19 10:59:10.5906866 -07:00 | 0433501106 | 043351106 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 345 | 7.53 | 7.45 | 600 | 13.09 | 12.96 | 386 | 8.42 | 8.34 | 557 | 12.16 | 12.04 | 443 | 9.67 | 9.57 | 600 | 13.09 | 12.96 | 473 | 10.32 | 10.22 |  |  | FALSE | TRUE | 733 | 953 | 879 | 1099 | {30E62AF8-EF4E-4BBF-92AC-33672D3C5723}
3186 | 2578 | {8E5DEFC6-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | BRUNSWICK | Bank 1 | CB 1104 | PGE\RVS7 | 2016-10-19 11:08:07.0553616 -07:00 | 1524801104 | 152481104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | * Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F5F8A8AC-F868-43E3-A1E4-E52A6705353D}
3187 | 2586 | {742E111A-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | MAPLE CREEK | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-19 11:13:23.8725295 -07:00 | 1921001101 | 192101101 | 8 | 3 | 3 | 1 | 100 | 2.18 | 2.16 | 91 | 1.99 | 1.97 | 100 | 2.18 | 2.16 | 100 | 2.18 | 2.16 | 100 | 2.18 | 2.16 | 100 | 2.18 | 2.16 | 100 | 2.18 | 2.16 | 100 | 2.18 | 2.16 |  |  | FALSE | TRUE | 91 | 119 | 110 | 137 | {F073EB49-B10D-466F-A281-F6802E0FA1AF}
3188 | 2587 | {742E1137-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | MENDOCINO | Bank 2 | CB 1101 | PGE\C8M4 | 2016-10-19 11:28:23.9466594 -07:00 | 0429501101 | 042951101 | 8 | 3 | 3 | 1 | 350 | 7.64 | 7.56 | 237 | 5.17 | 5.12 | 350 | 7.64 | 7.56 | 309 | 6.74 | 6.67 | 350 | 7.64 | 7.56 | 285 | 6.22 | 6.16 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 |  |  | FALSE | TRUE | 237 | 309 | 285 | 356 | {74ADE18E-450F-4865-A63B-A3C4493A199D}
3189 | 2587 | {742E1140-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | MENDOCINO | Bank 2 | CB 1102 | PGE\C8M4 | 2016-10-19 11:30:05.4141423 -07:00 | 0429501102 | 042951102 | 8 | 3 | 3 | 1 | 350 | 7.64 | 7.56 | 237 | 5.17 | 5.12 | 350 | 7.64 | 7.56 | 309 | 6.74 | 6.67 | 350 | 7.64 | 7.56 | 285 | 6.22 | 6.16 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 |  |  | FALSE | TRUE | 237 | 309 | 285 | 356 | {599D5CD6-A904-4FD6-B351-BE4886D0C1C4}
3190 | 2588 | {79E5373D-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | PALMER | Bank 1 | CB 1101 | PGE\A9S5 | 2016-11-11 10:11:48.0689042 -08:00 | 1830301101 | 183031101 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {79DBAB63-5831-4F04-89F2-E6348772FC05}
3191 | 2501 | {36053182-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | KING CITY | Bank 3 | CB 1102 | PGE\ACT0 | 2016-11-23 13:25:31.3248051 -08:00 | 1820301102 | 182031102 | 8 | 3 | 1 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {2B594DC8-F074-47A3-B1BA-EE6EB5A3592B}
3192 | 2535 | {CB6B58C8-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | PETALUMA A (NON-SCADA) | Bank 1 (Non SCADA) | CB 411 (Non-SCADA) | PGE\C8M4 | 2016-10-19 11:42:03.0095384 -07:00 | 042120411 | 042120411 | 4 | 3 | 3 | 1 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | TRUE | 455 | 592 | 546 | 683 | {6CE81945-1F92-4691-9992-8D6B0F51B75D}
3193 | 2501 | {05AC468D-0B42-11E6-9D37-D4BED91EFF1A} | CENTRAL COAST | KING CITY | Bank 3 | CB 1103 | PGE\ACT0 | 2016-10-19 11:43:55.5929199 -07:00 | 1820301103 | 182031103 | 8 | 3 | 1 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {0F7EAE67-1B4B-4026-BB8D-0662217D6496}
3194 | 2535 | {CB6B58D1-0B21-11E6-9D37-D4BED91EFF1A} | SONOMA | PETALUMA A (NON-SCADA) | Bank 1 (Non SCADA) | CB 413 (Non-SCADA) | PGE\C8M4 | 2016-10-19 11:44:33.6393727 -07:00 | 042120413 | 042120413 | 4 | 3 | 3 | 1 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 455 | 592 | 546 | 683 | {75BD18CB-876E-4280-BDDD-A059D22BDDEF}
3195 | 2501 | {FF70C509-0B41-11E6-9D37-D4BED91EFF1A} | CENTRAL COAST | KING CITY | Bank 3 | CB 1104 | PGE\ACT0 | 2016-10-19 11:45:54.4613477 -07:00 | 1820301104 | 182031104 | 8 | 3 | 1 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {D3F9EBB3-5E39-46EE-A99B-275094CE4C42}
3196 | 2569 | {7A8F22A8-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | RIO DELL | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-19 11:50:40.6215515 -07:00 | 1922501101 | 192251101 | 8 | 3 | 3 | 2 | 321 | 7.01 | 6.94 | 321 | 7.01 | 6.94 | 360 | 7.86 | 7.78 | 360 | 7.86 | 7.78 | 358 | 7.81 | 7.73 | 358 | 7.81 | 7.73 | 382 | 8.34 | 8.26 | 382 | 8.34 | 8.26 |  |  | FALSE | TRUE | 481 | 625 | 577 | 721 | {486AA420-2F86-478F-88C6-92B6B13E4D07}
3197 | 2569 | {7A8F22BF-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | RIO DELL | Bank 1 | CB 1102 | PGE\C8M4 | 2016-10-19 11:52:32.6512120 -07:00 | 1922501102 | 192251102 | 8 | 3 | 3 | 2 | 321 | 7.01 | 6.94 | 321 | 7.01 | 6.94 | 360 | 7.86 | 7.78 | 360 | 7.86 | 7.78 | 358 | 7.81 | 7.73 | 358 | 7.81 | 7.73 | 382 | 8.34 | 8.26 | 382 | 8.34 | 8.26 |  |  | FALSE | TRUE | 481 | 625 | 577 | 721 | {AAFB4DD0-1A0C-44C3-98F3-B508E09A2908}
3198 | 2589 | {79E53754-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | PASO ROBLES | Bank 1 | CB 1101 | PGE\ACT0 | 2016-12-01 07:42:29.9409142 -08:00 | 1826101101 | 182611101 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {5AE1285C-91B3-4886-8593-0675DB453B4B}
3199 | 2475 | {6124824F-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | COVELO (NON-SCADA) | Bank 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\C8M4 | 2016-10-19 12:01:21.8623111 -07:00 | 43061101 | 043061101 | 8 | 3 | 3 | 1 | 345 | 7.53 | 7.45 | 263 | 5.74 | 5.68 | 386 | 8.42 | 8.34 | 343 | 7.49 | 7.42 | 443 | 9.67 | 9.57 | 316 | 6.9 | 6.83 | 473 | 10.32 | 10.22 | 385 | 8.4 | 8.32 |  |  | FALSE | TRUE | 263 | 343 | 316 | 385 | {36CA3400-FB6F-4006-89B1-BAC7DBFCABA2}
3200 | 2596 | {8E5DEFEE-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | BRUNSWICK | Bank 2 | CB 1105 | PGE\RVS7 | 2016-10-19 12:34:40.8107311 -07:00 | 1524801105 | 152481105 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | IPAC job - Installed F60 relays and SCADA. Same PMT and GMT, changed CT ratio to 1200/5. *Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. Actual WE = 620 Amps. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {0FF846C4-8ED9-4401-ACE6-B2E29192208A}
3201 | 2596 | {8E5DEFFE-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | BRUNSWICK | Bank 2 | CB 1106 | PGE\RVS7 | 2016-10-19 12:40:49.1598311 -07:00 | 1524801106 | 152481106 | 8 | 3 | 3 | 1 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | *Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. Actual Capabilities: SN = 708A, SE = 740A, WN = 740A, WE = 740A. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {3F48E46D-9A4F-4AFC-BEB5-0C9D483BE86F}
3202 | 2592 | {61248346-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | FAIRHAVEN | Bank 1 | CB 1103 | PGE\C8M4 | 2016-10-19 12:44:24.1392307 -07:00 | 1924501103 | 192451103 | 8 | 3 | 3 | 2 | 572 | 12.48 | 12.36 | 572 | 12.48 | 12.36 | 744 | 16.24 | 16.08 | 744 | 16.24 | 16.08 | 687 | 14.99 | 14.84 | 687 | 14.99 | 14.84 | 859 | 18.75 | 18.56 | 859 | 18.75 | 18.56 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {808B77F5-6525-45AC-B7A9-B388EDDA2422}
3203 | 2592 | {61248356-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | FAIRHAVEN | Bank 1 | CB 1104 | PGE\C8M4 | 2016-10-19 12:45:41.2628138 -07:00 | 1924501104 | 192451104 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 614 | 13.4 | 13.27 | 614 | 13.4 | 13.27 | 623 | 13.6 | 13.46 | 623 | 13.6 | 13.46 | 666 | 14.53 | 14.38 | 666 | 14.53 | 14.38 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {B849D5DE-6AB1-42AC-A866-EE3AE1D38B94}
3204 | 2596 | {8E5DF007-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | BRUNSWICK | Bank 2 | CB 1107 | PGE\RVS7 | 2016-10-19 12:46:53.6055611 -07:00 | 1524801107 | 152481107 | 8 | 3 | 3 | 1 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | *Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. Actual Capabilities: SN = 708A, SE = 740A, WN = 740A, WE = 740A. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {AF6B4AF0-4CC7-45C4-A17B-7D12063954F3}
3205 | 2599 | {946B527D-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | BRUNSWICK | Bank 3 | CB 1110 | PGE\RVS7 | 2016-10-19 12:53:56.9150334 -07:00 | 1524801110 | 152481110 | 8 | 3 | 3 | 1 | 636 | 13.88 | 13.74 | 636 | 13.88 | 13.74 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | *Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. Actual Capabilities: SN = 661, SE = 740A, WN = 717A, WE = 740A. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {5755A7D2-CBBD-49FB-9440-6E80AC075B77}
3206 | 2600 | {612483DD-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | FRUITLAND | Bank 1 | CB 1141 | PGE\DCGa | 2017-04-22 06:11:24.7783866 -07:00 | 1923101141 | 192311141 | 8 | 3 | 3 | 1 | 300 | 6.55 | 6.48 | 229 | 5 | 4.95 | 300 | 6.55 | 6.48 | 285 | 6.22 | 6.16 | 300 | 6.55 | 6.48 | 275 | 6 | 5.94 | 300 | 6.55 | 6.48 | 285 | 6.22 | 6.16 | QA COMPLETED BY DCGA 04/22/17 |  | FALSE | TRUE | 229 | 298 | 275 | 344 | {3E47B5EE-8F73-4123-8B9A-7DC708D15825}
3207 | 2600 | {61248410-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | FRUITLAND | Bank 1 | CB 1142 | PGE\DCGa | 2017-04-22 06:21:02.5822980 -07:00 | 1923101142 | 192311142 | 8 | 3 | 3 | 1 | 300 | 6.55 | 6.48 | 229 | 5 | 4.95 | 300 | 6.55 | 6.48 | 285 | 6.22 | 6.16 | 300 | 6.55 | 6.48 | 275 | 6 | 5.94 | 300 | 6.55 | 6.48 | 285 | 6.22 | 6.16 | QA COMPLETED BY DCGA ON 04/22/2017 |  | FALSE | TRUE | 229 | 298 | 275 | 344 | {08C2A898-FF3F-4EDD-BB44-FE325BED6680}
3208 | 2597 | {8E5DEE6E-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | APPLE HILL | Bank 1 | CB 2102 | PGE\JSKe | 2016-10-19 13:23:54.8871235 -07:00 | 1536602102 | 153662102 | 12 | 3 | 3 | 1 | 423 | 15.99 | 15.83 | 423 | 15.99 | 15.83 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 |  |  | FALSE | FALSE | 423 | 550 | 508 | 635 | {27C6B7B4-055D-405F-AC4C-74E8CD99E72B}
3209 | 2601 | {946B5398-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | COLUMBIA HILL | Bank 1 | CB 1101 | PGE\RVS7 | 2016-10-19 13:08:41.9304104 -07:00 | 1524701101 | 152471101 | 8 | 3 | 3 | 1 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | *Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. |  | FALSE | FALSE | 206 | 268 | 247 | 309 | {46159CD2-7C85-4B5B-933A-DA99C4574175}
3210 | 2590 | {05AC4692-0B42-11E6-9D37-D4BED91EFF1A} | CENTRAL COAST | KING CITY | Bank 4 | CB 1107 (Non-SCADA) | PGE\ACT0 | 2016-10-19 13:09:11.5498392 -07:00 | 1820301107 | 182031107 | 8 | 3 | 3 | 1 | 286 | 6.24 | 6.18 | 286 | 6.24 | 6.18 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 286 | 372 | 343 | 429 | {CB53D3E4-A461-4B63-B614-885799C13F7C}
3211 | 2590 | {0DB7D25D-0B42-11E6-9D37-D4BED91EFF1A} | CENTRAL COAST | KING CITY | Bank 4 | CB 1108 (Non-SCADA) | PGE\ACT0 | 2016-10-19 13:13:26.7436883 -07:00 | 1820301108 | 182031108 | 8 | 3 | 3 | 1 | 286 | 6.24 | 6.18 | 286 | 6.24 | 6.18 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 286 | 372 | 343 | 429 | {8E75D407-0862-4CCD-8A61-6C7BEAC30DEE}
3213 | 2602 | {8E5DEEF9-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | APPLE HILL | Bank 2 | CB 1103 | PGE\JSKe | 2016-10-19 13:39:53.0781376 -07:00 | 1536601103 | 153661103 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | The OCB relay has a LR bypass group selector switch #2. This will lower the phase to 320amp and Grd to 150 amps. |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {65DD4D5C-2C0B-4169-8C85-18FDB888C824}
3214 | 2602 | {8E5DEF09-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | APPLE HILL | Bank 2 | CB 1104 | PGE\JSKe | 2016-10-19 13:47:13.4759636 -07:00 | 1536601104 | 153661104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {BDE0F124-C4D2-4B43-B846-8D7A50187132}
3215 | 2591 | {B8F4804B-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | WILLOW PASS | Bank 3 | CB 2107 | PGE\WCL5 | 2016-11-09 17:24:12.5236280 -08:00 | 0139102107 | 013912107 | 22 | 3 | 3 | 1 | 578 | 20.8 | 20.59 | 578 | 20.8 | 20.59 | 689 | 24.8 | 24.55 | 689 | 24.8 | 24.55 | 627 | 22.57 | 22.34 | 627 | 22.57 | 22.34 | 732 | 26.35 | 26.09 | 732 | 26.35 | 26.09 |  |  | FALSE | FALSE | 833 | 1083 | 1000 | 1250 | {5A943775-8143-4711-9519-B932BCD104E6}
3216 | 2591 | {BF48EF4B-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | WILLOW PASS | Bank 3 | CB 2108 | PGE\WCL5 | 2016-11-09 17:23:54.6767711 -08:00 | 0139102108 | 013912108 | 22 | 3 | 3 | 1 | 578 | 20.8 | 20.59 | 578 | 20.8 | 20.59 | 689 | 24.8 | 24.55 | 689 | 24.8 | 24.55 | 627 | 22.57 | 22.34 | 627 | 22.57 | 22.34 | 732 | 26.35 | 26.09 | 732 | 26.35 | 26.09 |  |  | FALSE | FALSE | 833 | 1083 | 1000 | 1250 | {7C6E7475-D120-4498-BBF4-3D59B122659B}
3217 | 2605 | {360531A3-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | LAURELES | Bank 1 | CB 1111 | PGE\MTDR | 2017-07-11 10:13:46.7413125 -07:00 | 1823701111 | 182371111 | 8 | 3 | 3 | 2 | 316 | 6.9 | 6.83 | 300 | 6.55 | 6.48 | 411 | 8.97 | 8.88 | 390 | 8.51 | 8.42 | 379 | 8.27 | 8.19 | 360 | 7.86 | 7.78 | 474 | 10.34 | 10.24 | 450 | 9.82 | 9.72 |  |  | TRUE | FALSE | 316 | 411 | 379 | 474 | {C53BB2DE-A216-4541-9771-5AFA1E64FF88}
3218 | 2605 | {3C3B437F-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | LAURELES | Bank 1 | CB 1112 | PGE\ACT0 | 2016-11-22 16:09:12.5784995 -08:00 | 1823701112 | 182371112 | 8 | 3 | 3 | 2 | 316 | 6.9 | 6.83 | 300 | 6.55 | 6.48 | 411 | 8.97 | 8.88 | 390 | 8.51 | 8.42 | 379 | 8.27 | 8.19 | 360 | 7.86 | 7.78 | 474 | 10.34 | 10.24 | 450 | 9.82 | 9.72 |  |  | TRUE | FALSE | 316 | 411 | 379 | 474 | {65FF66BD-9053-4EF0-993C-DB792987442D}
3219 | 2607 | {DD06434C-671D-11E5-80CA-005056A729E5} | KERN | COLUMBUS | Bank 3 (Non SCADA) | CB 1109 (Non-SCADA) | PGE\T1SI | 2016-10-19 16:30:52.4300727 -07:00 | 2539501109 | 253951109 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1153 | 1153 | 1153 | 1153 | {DB3C042F-BAF0-476B-8FA4-0FB7CB0C2C82}
3221 | 2603 | {DD064331-671D-11E5-80CA-005056A729E5} | KERN | COLUMBUS | Bank 1 (Non SCADA) | CB 1103 (Non-SCADA) | PGE\KWG0 | 2016-10-19 15:38:01.5338498 -07:00 | 2539501103 | 253951103 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {6A4C8F35-556E-416A-A84E-0095475B3942}
3222 | 2608 | {3C3B439C-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | LOS COCHES | Bank 2 | CB 1101 | PGE\ACT0 | 2016-11-23 10:26:10.6886363 -08:00 | 1821501101 | 182151101 | 8 | 3 | 3 | 1 | 434 | 9.47 | 9.38 | 434 | 9.47 | 9.38 | 486 | 10.61 | 10.5 | 486 | 10.61 | 10.5 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 577 | 750 | 692 | 866 | {E72DFDD6-2E20-49DE-ABED-22DB0CC7E5B5}
3223 | 2607 | {DD064355-671D-11E5-80CA-005056A729E5} | KERN | COLUMBUS | Bank 3 (Non SCADA) | CB 1110 (Non-SCADA) | PGE\BXYD | 2016-10-19 15:44:56.4417297 -07:00 | 2539501110 | 253951110 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1153 | 1153 | 1153 | 1153 | {585744F0-96B0-4641-BB7D-F1108580B5AE}
3224 | 2603 | {DD064334-671D-11E5-80CA-005056A729E5} | KERN | COLUMBUS | Bank 1 (Non SCADA) | CB 1104 (Non-SCADA) | PGE\KWG0 | 2016-10-19 15:37:33.1502484 -07:00 | 2539501104 | 253951104 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {D22B11B6-63BC-4F84-8CF6-3479B4743984}
3225 | 2608 | {3C3B43A4-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | LOS COCHES | Bank 2 | CB 1102 | PGE\MTDR | 2017-07-11 10:28:00.8522625 -07:00 | 1821501102 | 182151102 | 8 | 3 | 3 | 1 | 458 | 10 | 9.9 | 458 | 10 | 9.9 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 458 | 596 | 550 | 687 | {0F100D3A-F5B0-4910-9332-78E0A90F1658}
3226 | 2609 | {DD06433D-671D-11E5-80CA-005056A729E5} | KERN | COLUMBUS | Bank 2 (Non SCADA) | CB 1105 (Non-SCADA) | PGE\KWG0 | 2016-10-19 15:36:54.2899011 -07:00 | 2539501105 | 253951105 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {3E6A8CF5-6D35-4203-9021-A5B9B29F7C31}
3227 | 2609 | {DD064346-671D-11E5-80CA-005056A729E5} | KERN | COLUMBUS | Bank 2 (Non SCADA) | CB 1106 (Non-SCADA) | PGE\KWG0 | 2016-10-19 15:36:23.9463444 -07:00 | 2539501106 | 253951106 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {21399676-2512-41B6-836A-9F2E802BDCC2}
3228 | 2498 | {9ED2E377-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | AMES | Bank 1 | CB 1101 | PGE\MTTA | 2016-12-29 12:36:46.3590496 -08:00 | 0839001101 | 083901101 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {20C3CD90-6C0A-4868-89BB-5483188CF0C5}
3232 | 2611 | {DD0642B3-671D-11E5-80CA-005056A729E5} | KERN | BLACKWELL | Bank 1 | CB 2101 | PGE\APE3 | 2016-10-19 16:25:02.2731564 -07:00 | 2546802101 | 254682101 | 8 | 4 | 4 | 1 | 572 | 12.48 | 12.36 | 572 | 12.48 | 12.36 | 590 | 12.88 | 12.75 | 590 | 12.88 | 12.75 | 590 | 12.88 | 12.75 | 590 | 12.88 | 12.75 | 590 | 12.88 | 12.75 | 590 | 12.88 | 12.75 |  |  | FALSE | FALSE | 572 | 744 | 687 | 842 | {26617EB3-158B-4F6F-93F9-2B77FFE6D7FD}
3233 | 2498 | {9ED2E380-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | AMES | Bank 1 | CB 1102 | PGE\MTTA | 2016-12-29 12:36:55.5788860 -08:00 | 0839001102 | 083901102 | 8 | 4 | 4 | 2 | 534 | 11.65 | 11.53 | 534 | 11.65 | 11.53 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {262D5FDD-8FDC-4547-B2B0-26AFA955513F}
3234 | 2611 | {DD0642A8-671D-11E5-80CA-005056A729E5} | KERN | BLACKWELL | Bank 1 | CB 1102 | PGE\APE3 | 2016-10-19 16:30:49.3253742 -07:00 | 2546801102 | 254681102 | 8 | 4 | 4 | 1 | 572 | 12.48 | 12.36 | 572 | 12.48 | 12.36 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 572 | 744 | 687 | 842 | {FB847111-F076-45E8-BF67-669C59818135}
3236 | 2572 | {DD06424D-671D-11E5-80CA-005056A729E5} | KERN | BAKERSFIELD | Bank 5 (Non SCADA) | CB 1116 | PGE\BXYD | 2016-10-19 16:37:08.6143471 -07:00 | 2533701116 | 253371116 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1603 | 2079 | 1924 | 2079 | {5763D1C2-1ACE-4C5B-B1BA-96FE404E27FF}
3237 | 2572 | {DD064255-671D-11E5-80CA-005056A729E5} | KERN | BAKERSFIELD | Bank 5 (Non SCADA) | CB 1118 | PGE\BXYD | 2016-10-19 16:39:48.7908430 -07:00 | 2533701118 | 253371118 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1603 | 2079 | 1924 | 2079 | {04B742FC-42E8-4D86-9F7B-07FEC682EAEA}
3238 | 2612 | {429753EA-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | LOS OSITOS | Bank 1 | CB 2101 | PGE\ACT0 | 2016-11-23 13:27:08.2319522 -08:00 | 1820802101 | 182082101 | 12 | 3 | 3 | 1 | 330 | 12.47 | 12.35 | 330 | 12.47 | 12.35 | 429 | 16.21 | 16.05 | 429 | 16.21 | 16.05 | 396 | 14.97 | 14.82 | 396 | 14.97 | 14.82 | 496 | 18.75 | 18.56 | 496 | 18.75 | 18.56 |  |  | FALSE | FALSE | 330 | 429 | 396 | 496 | {2EB9D2BC-85AF-439F-AF57-0B7CBECF32DC}
3239 | 2614 | {A4FD4520-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LOS GATOS | Bank 1 | CB 1106 | PGE\MSJ9 | 2016-10-20 09:52:14.5352381 -07:00 | 0820201106 | 082021106 | 8 | 3 | 3 | 2 | 524 | 11.44 | 11.33 | 524 | 11.44 | 11.33 | 591 | 12.9 | 12.77 | 591 | 12.9 | 12.77 | 599 | 13.07 | 12.94 | 599 | 13.07 | 12.94 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 740 | 963 | 888 | 1111 | {5355B032-264A-43EF-8A62-26367CFEF231}
3240 | 2613 | {DD06426F-671D-11E5-80CA-005056A729E5} | KERN | BAKERSFIELD | Bank 6 | CB 1102 | PGE\BXYD | 2016-10-19 17:16:52.7304981 -07:00 | 2533701102 | 253371102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {2F8CCE10-EC9E-4088-B434-A9AA527D29A5}
3241 | 2613 | {DD06427A-671D-11E5-80CA-005056A729E5} | KERN | BAKERSFIELD | Bank 6 | CB 1106 | PGE\BXYD | 2016-10-19 17:19:00.6471284 -07:00 | 2533701106 | 253371106 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {958A291B-5188-4B82-B035-F6D11BDB8E96}
3242 | 2613 | {DD064294-671D-11E5-80CA-005056A729E5} | KERN | BAKERSFIELD | Bank 6 | CB 1110 | PGE\BXYD | 2016-10-19 17:22:35.5339753 -07:00 | 2533701110 | 253371110 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {13AE712C-6AFA-426C-97BC-1CE41AE0C21A}
3243 | 2617 | {48A0FF22-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | LOS OSITOS | Bank 2 | CB 2102 | PGE\ACT0 | 2016-11-23 13:27:40.0257712 -08:00 | 1820802102 | 182082102 | 22 | 3 | 2 | 1 | 400 | 14.4 | 14.26 | 400 | 14.4 | 14.26 | 447 | 16.09 | 15.93 | 447 | 16.09 | 15.93 | 514 | 18.5 | 18.32 | 514 | 18.5 | 18.32 | 549 | 19.76 | 19.56 | 549 | 19.76 | 19.56 |  |  | FALSE | FALSE | 833 | 1083 | 1000 | 1250 | {B6E3AEBE-DB8F-440B-8E4A-3C1B1411940B}
3244 | 2617 | {4F126C14-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | LOS OSITOS | Bank 2 | CB 2103 | PGE\MTDR | 2017-07-11 10:41:15.7604535 -07:00 | 1820802103 | 182082103 | 22 | 3 | 2 | 1 | 345 | 12.42 | 12.3 | 327 | 11.77 | 11.65 | 386 | 13.89 | 13.75 | 366 | 13.17 | 13.04 | 443 | 15.94 | 15.78 | 420 | 15.12 | 14.97 | 473 | 17.02 | 16.85 | 449 | 16.16 | 16 |  |  | FALSE | FALSE | 833 | 1083 | 1000 | 1250 | {A4A2F1EE-A79A-425F-A114-9877080CDA6B}
3245 | 2619 | {67A95033-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | HARRIS | Bank 1 | CB 1109 | PGE\D5LZ | 2017-07-24 14:26:54.0312518 -07:00 | 1924301109 | 192431109 | 8 | 3 | 3 | 2 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | TRUE | 733 | 953 | 879 | 1099 | {7B044DCC-4EA8-4B99-869A-56E973067181}
3246 | 2620 | {67A95062-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | HARRIS | Bank 2 | CB 1108 | PGE\D5LZ | 2017-07-24 16:03:15.1221674 -07:00 | 1924301108 | 192431108 | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 552 | 12.05 | 11.93 | 656 | 14.32 | 14.18 | 623 | 13.6 | 13.46 | 666 | 14.53 | 14.38 | 632 | 13.79 | 13.65 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | TRUE | 572 | 744 | 687 | 842 | {1311A2ED-1FB2-4104-8D23-6D197B4F1339}
3247 | 2606 | {8E5DEF8E-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | BONNIE NOOK | Bank 1 | CB 1101 | PGE\JSKe | 2016-10-20 08:37:34.4496035 -07:00 | 1523001101 | 152301101 | 8 | 4 | 4 | 2 | 79 | 1.72 | 1.7 | 79 | 1.72 | 1.7 | 102 | 2.23 | 2.21 | 102 | 2.23 | 2.21 | 94 | 2.05 | 2.03 | 94 | 2.05 | 2.03 | 118 | 2.58 | 2.55 | 118 | 2.58 | 2.55 |  |  | FALSE | FALSE | 79 | 102 | 94 | 118 | {7AD7A232-75FD-42E5-9BA7-1AF90CF936AA}
3248 | 2606 | {8E5DEF97-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | BONNIE NOOK | Bank 1 | CB 1102 | PGE\JSKe | 2016-10-20 08:39:14.8754073 -07:00 | 1523001102 | 152301102 | 8 | 4 | 4 | 2 | 79 | 1.72 | 1.7 | 79 | 1.72 | 1.7 | 102 | 2.23 | 2.21 | 102 | 2.23 | 2.21 | 94 | 2.05 | 2.03 | 94 | 2.05 | 2.03 | 118 | 2.58 | 2.55 | 118 | 2.58 | 2.55 |  |  | FALSE | FALSE | 79 | 102 | 94 | 118 | {FC13BF49-1A74-44CD-AEE5-A47CDB8378A8}
3249 | 2621 | {67A9508E-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | HARTLEY | Bank 1 | CB 1101 | PGE\DCGa | 2017-01-18 20:38:21.9718984 -08:00 | 0432101101 | 043211101 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {A44C8D8E-FFEE-4EE2-86C2-55FF97091BAD}
3250 | 2622 | {B935D4DF-0E4A-11E6-95F2-D4BED91EFF1A} | CENTRAL COAST | MANZANITA | BANK 2 (Non SCADA) | CB 404 (Non-SCADA) | PGE\ACT0 | 2016-10-20 08:52:19.4428930 -07:00 | 183150404 | 183150404 | 4 | 3 | 2 | 2 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 396 | 3 | 2.97 | 396 | 3 | 2.97 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {5EC3C0A0-0294-457A-93A4-E692B175304A}
3251 | 2624 | {67A950C4-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | HARTLEY | Bank 2 | CB 1102 (Non-SCADA) | PGE\C8M4 | 2016-10-20 08:53:07.4184979 -07:00 | 0432101102 | 043211102 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | TRUE | 572 | 744 | 687 | 842 | {AC059895-3494-48BC-B5FD-0B6BFE65A8A9}
3252 | 2623 | {7B288D36-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACA DIXON | Bank 6 | CB 1101 | PGE\TEJ2 | 2016-11-01 13:02:11.3976686 -07:00 | 0635901101 | 063591101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {438F88E5-AD50-41A9-B3DB-BC3261871B9F}
3253 | 2625 | {56DE9FBA-0E49-11E6-95F2-D4BED91EFF1A} | HUMBOLDT | MIDDLETOWN | BANK 1 | CB 1101 (UNDER CONSTRUCTION) | PGE\C8M4 | 2016-10-20 09:07:10.8438428 -07:00 | 0431401101 | 043141101 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | TRUE | 962 | 1250 | 1154 | 1443 | {DE0A65CF-961A-4F13-B981-8D7C6DFFB4B9}
3254 | 2625 | {5D71B902-0E49-11E6-95F2-D4BED91EFF1A} | HUMBOLDT | MIDDLETOWN | BANK 1 | CB 1103 | PGE\C8M4 | 2016-10-20 09:10:35.8233639 -07:00 | 0431401103 | 043141103 | 8 | 2 | 2 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | TRUE | 962 | 1250 | 1154 | 1443 | {E7F14F2A-C6F3-4C12-84A6-58D5FC1DD2C8}
3255 | 2623 | {7B288D46-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACA DIXON | Bank 6 | CB 1109 | PGE\TEJ2 | 2016-11-01 13:13:15.5439238 -07:00 | 0635901109 | 063591109 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | Note ties to Vaca Dixon 1101 and Vaca Dixon 1102 before 1100 Al UG tie and 600 amp switches. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {A020A370-75B4-47B3-ADAF-3C81E34FE02C}
3258 | 2626 | {742E1156-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | MIDDLETOWN | Bank 2 | CB 1102 | PGE\C8M4 | 2016-10-20 09:19:02.7454433 -07:00 | 0431401102 | 043141102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 572 | 12.48 | 12.36 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | TRUE | 572 | 744 | 687 | 859 | {72815DC3-F987-40FF-85C1-6E880DCCB4D3}
3259 | 2627 | {7B288D60-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACA DIXON | Bank 7 | CB 1102 | PGE\TEJ2 | 2016-10-20 09:35:33.9619747 -07:00 | 0635901102 | 063591102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {46618568-4649-479C-A720-A88381B29464}
3260 | 2630 | {13EDBC82-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BAIR | Bank 2 | CB 1102 | PGE\C7CF | 2017-01-12 11:56:35.7670676 -08:00 | 0242601102 | 024261102 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 592 | 12.92 | 12.79 | 570 | 12.44 | 12.32 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 599 | 13.07 | 12.94 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {1AAE22FA-9971-44E8-A3BD-F7E66FF7C475}
3261 | 2632 | {13EDBC95-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BAIR | Bank 3 | CB 1103 | PGE\C7CF | 2017-01-12 11:56:21.5083934 -08:00 | 0242601103 | 024261103 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 592 | 12.92 | 12.79 | 592 | 12.92 | 12.79 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 599 | 13.07 | 12.94 | 599 | 13.07 | 12.94 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {4CE3E5A3-C0A6-4886-9A50-6A8D859CCAE4}
3262 | 2635 | {742E127C-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | REDBUD | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-20 09:50:00.0220925 -07:00 | 0431901101 | 043191101 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 117 | 2.55 | 2.52 | 578 | 12.61 | 12.48 | 131 | 2.86 | 2.83 | 666 | 14.53 | 14.38 | 163 | 3.56 | 3.52 | 711 | 15.52 | 15.36 | 172 | 3.75 | 3.71 |  |  | FALSE | TRUE | 320 | 416 | 384 | 481 | {D712CA4F-811E-4B44-A958-3BB85350BA79}
3263 | 2614 | {AB2667FE-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LOS GATOS | Bank 1 | CB 1107 | PGE\MSJ9 | 2016-11-15 16:14:46.4211424 -08:00 | 0820201107 | 082021107 | 7 | 3 | 3 | 2 | 468 | 10.11 | 10.01 | 468 | 10.11 | 10.01 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 528 | 11.4 | 11.29 | 528 | 11.4 | 11.29 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | Previous Capability sheet shows 700 Al in 2-way trench (454A capability). Verified only one 6" duct in trench (increasing capability). |  | FALSE | FALSE | 740 | 963 | 888 | 1111 | {6C1CCDBA-5449-4D04-8C95-75C72E21CD16}
3264 | 2629 | {550A6451-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | MONTEREY | Bank 1 | CB 401 (Non-SCADA) | PGE\ACT0 | 2016-11-23 13:29:04.2365110 -08:00 | 182090401 | 182090401 | 3 | 3 | 3 | 2 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 390 | 2.81 | 2.78 | 390 | 2.81 | 2.78 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 450 | 3.24 | 3.21 | 450 | 3.24 | 3.21 |  |  | FALSE | FALSE | 1457 | 1716 | 1716 | 1716 | {AE486A9A-0B37-4DDA-BC40-A800C9B176EA}
3265 | 2632 | {13EDBCA5-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BAIR | Bank 3 | CB 1104 | PGE\C7CF | 2017-01-12 11:58:18.3390401 -08:00 | 0242601104 | 024261104 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {687F41F0-8B3B-466F-88CF-7C627B2CA8F4}
3266 | 2636 | {742E128F-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | REDBUD | Bank 3 | CB 1102 | PGE\DCGa | 2017-05-16 20:04:35.0181746 -07:00 | 0431901102 | 043191102 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 345 | 7.53 | 7.45 | 578 | 12.61 | 12.48 | 386 | 8.42 | 8.34 | 600 | 13.09 | 12.96 | 443 | 9.67 | 9.57 | 600 | 13.09 | 12.96 | 473 | 10.32 | 10.22 |  |  | FALSE | TRUE | 572 | 744 | 687 | 800 | {C2232F7B-EBF6-4457-9371-316D392C8368}
3267 | 2627 | {7B288D69-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACA DIXON | Bank 7 | CB 1103 | PGE\TEJ2 | 2016-10-20 10:21:25.3752263 -07:00 | 0635901103 | 063591103 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {EEB4F255-5270-4F96-8377-A023B21A3E70}
3268 | 2639 | {DD0643B6-671D-11E5-80CA-005056A729E5} | KERN | ELK HILLS | Bank 1 (Non SCADA) | CB 1104 (Non-SCADA) | PGE\BXYD | 2016-10-20 10:24:46.3388343 -07:00 | 2524401104 | 252441104 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {E9FD8C03-948C-4EBF-95BE-E45FF8017824}
3269 | 2639 | {DD0643BF-671D-11E5-80CA-005056A729E5} | KERN | ELK HILLS | Bank 1 (Non SCADA) | CB 1106 (Non-SCADA) | PGE\APE3 | 2017-04-26 07:57:14.4267060 -07:00 | 2524401106 | 252441106 | 8 | 3 | 3 | 1 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {95E0728E-DB26-48EE-96A7-8CF76A42555F}
3270 | 2640 | {742E120B-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | PHILO | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-20 10:28:49.7383198 -07:00 | 0426001101 | 042601101 | 8 | 3 | 3 | 1 | 250 | 5.46 | 5.41 | 229 | 5 | 4.95 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 |  |  | FALSE | TRUE | 229 | 298 | 275 | 344 | {6D776B76-D4ED-47A5-8D35-42DDA5A188D2}
3271 | 2640 | {742E1214-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | PHILO | Bank 1 | CB 1102 | PGE\C8M4 | 2016-10-20 10:30:38.6242598 -07:00 | 0426001102 | 042601102 | 8 | 3 | 3 | 1 | 137 | 2.99 | 2.96 | 137 | 2.99 | 2.96 | 157 | 3.43 | 3.4 | 157 | 3.43 | 3.4 | 198 | 4.32 | 4.28 | 198 | 4.32 | 4.28 | 211 | 4.6 | 4.55 | 211 | 4.6 | 4.55 |  |  | FALSE | FALSE | 229 | 298 | 275 | 344 | {0C42E265-3790-4C74-95AD-429AA351B584}
3272 | 2627 | {7B288D9C-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACA DIXON | Bank 7 | CB 1104 | PGE\TEJ2 | 2016-11-01 13:24:35.4816851 -07:00 | 0635901104 | 063591104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 717 | 15.65 | 15.49 | 717 | 15.65 | 15.49 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 717 | 15.65 | 15.49 | 717 | 15.65 | 15.49 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {1892F12A-CFC9-4C85-8004-16F484047A2D}
3273 | 2641 | {67A94F23-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | GARBERVILLE | Bank 1 | CB 1101 | PGE\DCGa | 2016-10-20 11:34:47.7023441 -07:00 | 1922201101 | 192221101 | 8 | 3 | 3 | 2 | 500 | 10.91 | 10.8 | 263 | 5.74 | 5.68 | 500 | 10.91 | 10.8 | 288 | 6.29 | 6.23 | 500 | 10.91 | 10.8 | 287 | 6.26 | 6.2 | 500 | 10.91 | 10.8 | 303 | 6.61 | 6.54 |  |  | FALSE | TRUE | 962 | 1250 | 1154 | 1443 | {3318A6C3-9ED3-49BE-8B81-3921199A36CF}
3274 | 2642 | {742E122A-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | POINT ARENA | Bank 1 | CB 1101 | PGE\DCGa | 2017-08-15 09:19:26.1737474 -07:00 | 0433801101 | 043381101 | 8 | 3 | 3 | 2 | 150 | 3.27 | 3.24 | 118 | 2.58 | 2.55 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 142 | 3.1 | 3.07 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | QA COMPLETED BY DCGA ON 08/15/17 |  | FALSE | TRUE | 118 | 154 | 142 | 177 | {04C1C0F8-E021-41EB-8F84-6BBCB0F26969}
3278 | 2643 | {7B288DAF-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACA DIXON | Bank 8 | CB 1105 | PGE\TEJ2 | 2016-11-01 13:28:14.5944694 -07:00 | 0635901105 | 063591105 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {DEE5E34E-5ABF-49AC-A95C-583CAEBEFA2C}
3279 | 2644 | {6DFF15DD-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | KONOCTI | Bank 2 | CB 1102 | PGE\C8M4 | 2016-10-20 10:59:37.9774855 -07:00 | 0433101102 | 043311102 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | TRUE | 481 | 625 | 577 | 721 | {DF40B9D2-F851-4A9A-AEB9-C4500CEB6838}
3280 | 2645 | {63A611E2-0E49-11E6-95F2-D4BED91EFF1A} | HUMBOLDT | KONOCTI | BANK 3 | CB 1108 | PGE\C8M4 | 2016-10-20 11:07:17.8242731 -07:00 | 0433101108 | 043311108 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | TRUE | 572 | 722 | 687 | 722 | {8A4A0907-7ADC-4574-8CE6-1727EC834710}
3281 | 2643 | {7B288DCD-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACA DIXON | Bank 8 | CB 1106 | PGE\TEJ2 | 2016-11-01 13:37:11.8212545 -07:00 | 0635901106 | 063591106 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {A5749D87-DC36-4FE8-B95C-F93AEB449AC2}
3283 | 2641 | {51BA7AB5-B5B8-11E6-B077-D4BED91EFF1A} | HUMBOLDT | GARBERVILLE | Bank 1 | CB 1102 | PGE\DCGa | 2016-11-14 11:08:32.5018995 -08:00 | 192221102 | 192221102 | 8 | 3 | 3 | 2 | 500 | 10.91 | 10.8 | 391 | 8.53 | 8.44 | 500 | 10.91 | 10.8 | 440 | 9.6 | 9.5 | 500 | 10.91 | 10.8 | 443 | 9.67 | 9.57 | 500 | 10.91 | 10.8 | 473 | 10.32 | 10.22 |  |  | FALSE | TRUE | 962 | 1250 | 1154 | 1443 | {E6B66E05-3CEE-41BF-A10B-C49D1CA0C5E6}
3284 | 2648 | {742E11B3-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | NEWBURG | Bank 2 | CB 1132 | PGE\C8M4 | 2016-10-20 11:25:27.9138803 -07:00 | 1921501132 | 192151132 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {75EFDA0E-DD4A-4E14-89EC-6CDC3D0AFE80}
3285 | 2647 | {BF18FF2F-671D-11E5-80CA-005056A729E5} | FRESNO | GATES | Bank 3 | CB 1101 | PGE\BXYD | 2017-01-24 09:38:57.2142511 -08:00 | 2539301101 | 253931101 | 8 | 4 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {B826D13D-FF0B-44CB-B3F5-84CEE6264007}
3287 | 2646 | {742E117A-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | NEWBURG | Bank 1 | CB 1131 | PGE\C8M4 | 2016-10-20 11:27:06.1837570 -07:00 | 1921501131 | 192151131 | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 429 | 9.36 | 9.27 | 600 | 13.09 | 12.96 | 558 | 12.18 | 12.06 | 600 | 13.09 | 12.96 | 515 | 11.24 | 11.13 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | TRUE | 429 | 558 | 515 | 601 | {2E204A2E-6DAF-463F-BD89-8291FE4ACF32}
3288 | 2646 | {742E11A0-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | NEWBURG | Bank 1 | CB 1133 | PGE\C8M4 | 2016-10-20 11:27:57.3434267 -07:00 | 1921501133 | 192151133 | 8 | 3 | 3 | 2 | 321 | 7.01 | 6.94 | 321 | 7.01 | 6.94 | 360 | 7.86 | 7.78 | 360 | 7.86 | 7.78 | 358 | 7.81 | 7.73 | 358 | 7.81 | 7.73 | 382 | 8.34 | 8.26 | 382 | 8.34 | 8.26 |  |  | FALSE | TRUE | 429 | 558 | 515 | 601 | {0FD066D4-8C3F-4CDF-998D-540C700E37D3}
3289 | 2643 | {7B288DDD-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACA DIXON | Bank 8 | CB 1107 | PGE\TEJ2 | 2016-11-01 13:41:24.7703493 -07:00 | 0635901107 | 063591107 | 8 | 3 | 3 | 1 | 900 | 19.64 | 19.44 | 600 | 13.09 | 12.96 | 900 | 19.64 | 19.44 | 600 | 13.09 | 12.96 | 900 | 19.64 | 19.44 | 600 | 13.09 | 12.96 | 900 | 19.64 | 19.44 | 600 | 13.09 | 12.96 | parallel 1100 Al. One line ties to the Vaca Dixon 1102 and the other to switch 15624. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {78C0CD6A-D31C-4938-AB64-2FB37929283D}
3291 | 2641 | {67A94FE5-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | GARBERVILLE | Bank 1 | CB 1103 | PGE\DCGa | 2016-11-14 11:09:03.9641339 -08:00 | 192221103 | 192221103 | 8 | 3 | 3 | 2 | 500 | 10.91 | 10.8 | 127 | 2.77 | 2.74 | 500 | 10.91 | 10.8 | 140 | 3.06 | 3.03 | 500 | 10.91 | 10.8 | 163 | 3.56 | 3.52 | 500 | 10.91 | 10.8 | 172 | 3.75 | 3.71 |  |  | FALSE | TRUE | 962 | 1250 | 1154 | 1443 | {B23EC85E-C2C3-4B6F-ADF5-F605B086C627}
3293 | 2647 | {C5113FB7-671D-11E5-80CA-005056A729E5} | FRESNO | GATES | Bank 3 | CB 1102 | PGE\BXYD | 2017-01-24 09:39:36.2145011 -08:00 | 2539301102 | 253931102 | 8 | 4 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {97E0EA10-081D-4563-8270-7E0F8713BEE7}
3295 | 2649 | {742E11EC-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | ORICK | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-20 13:20:37.8026919 -07:00 | 1922601101 | 192261101 | 8 | 3 | 3 | 2 | 200 | 4.36 | 4.32 | 38 | 0.83 | 0.82 | 200 | 4.36 | 4.32 | 49 | 1.07 | 1.06 | 200 | 4.36 | 4.32 | 45 | 0.98 | 0.97 | 200 | 4.36 | 4.32 | 57 | 1.24 | 1.23 |  |  | FALSE | TRUE | 38 | 49 | 45 | 57 | {2B4BB4B0-72D8-4390-BBB2-F6687FE114E1}
3296 | 2649 | {742E11F5-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | ORICK | Bank 1 | CB 1102 | PGE\C8M4 | 2016-10-20 13:22:16.6630293 -07:00 | 1922601102 | 192261102 | 8 | 3 | 3 | 2 | 200 | 4.36 | 4.32 | 38 | 0.83 | 0.82 | 200 | 4.36 | 4.32 | 49 | 1.07 | 1.06 | 200 | 4.36 | 4.32 | 45 | 0.98 | 0.97 | 200 | 4.36 | 4.32 | 57 | 1.24 | 1.23 |  |  | FALSE | TRUE | 38 | 49 | 45 | 57 | {F36B11D7-18E7-4EDB-8675-6EF245D57339}
3297 | 2650 | {67A9500A-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | GUALALA | Bank 1 | CB 1111 | PGE\C8M4 | 2016-10-20 13:34:48.2274446 -07:00 | 0428401111 | 042841111 | 8 | 3 | 3 | 2 | 333 | 7.27 | 7.2 | 263 | 5.74 | 5.68 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 316 | 6.9 | 6.83 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | TRUE | 263 | 343 | 316 | 385 | {616A9656-F8EA-473A-A00B-3F913793CCEF}
3298 | 2651 | {67A9501D-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | GUALALA | Bank 2 | CB 1112 | PGE\C8M4 | 2016-10-20 13:47:05.2552209 -07:00 | 0428401112 | 042841112 | 8 | 3 | 3 | 2 | 333 | 7.27 | 7.2 | 286 | 6.24 | 6.18 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | TRUE | 286 | 372 | 343 | 385 | {704788D7-6D38-4D36-ABCB-A8D198E05C5A}
3299 | 2652 | {6DFF14E6-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | HOOPA | Bank 1 | CB 1101 | PGE\DCGa | 2017-07-17 18:18:12.9502134 -07:00 | 192401101 | 192401101 | 8 | 3 | 3 | 1 | 231 | 5.04 | 4.99 | 219 | 4.78 | 4.73 | 252 | 5.5 | 5.45 | 239 | 5.22 | 5.17 | 287 | 6.26 | 6.2 | 272 | 5.94 | 5.88 | 303 | 6.61 | 6.54 | 287 | 6.26 | 6.2 | QA COMPLETED BY DCGA ON 07/17/2017 |  | FALSE | TRUE | 229 | 298 | 275 | 344 | {DE0C8E45-7677-4988-A1E2-65E9D52D18DD}
3300 | 2653 | {6DFF152D-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | HOPLAND | Bank 1 | CB 1101 | PGE\DCGa | 2016-11-18 16:13:05.6244342 -08:00 | 0422501101 | 042251101 | 8 | 3 | 3 | 1 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 577 | 750 | 692 | 866 | {A1A0E5DB-06AD-461B-92B5-CEFCEFF403D6}
3301 | 2655 | {6DFF1543-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | HUMBOLDT BAY | BK 11 | CB 1101 | PGE\DCGa | 2016-12-13 23:11:15.2061817 -08:00 | 192341101 | 192341101 | 8 | 3 | 3 | 2 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 |  |  | FALSE | TRUE | 481 | 625 | 577 | 721 | {5224CC52-3A42-4584-977A-DD6C3AFAC1C9}
3303 | 2655 | {6DFF1553-0B21-11E6-9D37-D4BED91EFF1A} | HUMBOLDT | HUMBOLDT BAY | BK 11 | CB 1102 | PGE\C8M4 | 2016-10-20 15:09:01.5439013 -07:00 | 192341102 | 192341102 | 8 | 2 | 2 | 2 | 323 | 7.05 | 6.98 | 323 | 7.05 | 6.98 | 443 | 9.67 | 9.57 | 443 | 9.67 | 9.57 | 381 | 8.31 | 8.23 | 381 | 8.31 | 8.23 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 |  |  | FALSE | TRUE | 481 | 625 | 577 | 721 | {66293E2C-B798-490F-BB7A-1D6F73B25821}
3304 | 2656 | {C5113FC8-671D-11E5-80CA-005056A729E5} | FRESNO | GATES | Bank 4 | CB 1104 | PGE\BXYD | 2017-01-24 09:43:28.1255877 -08:00 | 2539301104 | 253931104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F54BDEA2-F19B-43CB-B0D9-BA9A236A5A1F}
3305 | 2656 | {C5113FD9-671D-11E5-80CA-005056A729E5} | FRESNO | GATES | Bank 4 | CB 1105 | PGE\BXYD | 2017-01-24 09:44:25.7991574 -08:00 | 2539301105 | 253931105 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {118D175A-1E4A-400B-802C-92BE12B877E6}
3306 | 2614 | {AB266869-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LOS GATOS | Bank 1 | CB 1108 | PGE\MSJ9 | 2016-10-21 10:33:50.4871230 -07:00 | 0820201108 | 082021108 | 8 | 3 | 3 | 2 | 468 | 10.21 | 10.11 | 468 | 10.21 | 10.11 | 591 | 12.9 | 12.77 | 591 | 12.9 | 12.77 | 528 | 11.52 | 11.4 | 528 | 11.52 | 11.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 740 | 963 | 888 | 1111 | {30044465-261B-40FF-917D-2C7FEB9060D0}
3307 | 2656 | {C5113FE7-671D-11E5-80CA-005056A729E5} | FRESNO | GATES | Bank 4 | CB 1106 | PGE\BXYD | 2017-01-24 09:46:41.8476295 -08:00 | 2539301106 | 253931106 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {5C60439B-AE39-47BB-94B0-4751EBAEA3A5}
3309 | 2659 | {D944BF38-96E6-11E6-841B-D4BED91EFF1A} | HUMBOLDT | POTTER VALLEY P H | Bank 2 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\C8M4 | 2016-10-20 15:39:15.1081615 -07:00 |  | 253931107 | 8 | 3 | 3 | 1 | 100 | 2.18 | 2.16 | 79 | 1.72 | 1.7 | 115 | 2.51 | 2.48 | 102 | 2.23 | 2.21 | 144 | 3.14 | 3.11 | 94 | 2.05 | 2.03 | 153 | 3.34 | 3.31 | 118 | 2.58 | 2.55 |  |  | FALSE | TRUE | 79 | 102 | 94 | 118 | {00000000-0000-0000-0000-000000000000}
3310 | 2654 | {4B85910A-96F5-11E6-841B-D4BED91EFF1A} | HUMBOLDT | POTTER VALLEY P H | Bank 4 (Non SCADA) | CB 1104 (Non-SCADA) | PGE\DCGa | 2016-12-29 17:43:42.1164364 -08:00 |  | 253931108 | 8 | 3 | 3 | 1 | 89 | 1.94 | 1.92 | 89 | 1.94 | 1.92 | 116 | 2.53 | 2.5 | 116 | 2.53 | 2.5 | 107 | 2.34 | 2.32 | 107 | 2.34 | 2.32 | 120 | 2.62 | 2.59 | 120 | 2.62 | 2.59 |  |  | FALSE | FALSE | 89 | 116 | 107 | 120 | {00000000-0000-0000-0000-000000000000}
3311 | 2656 | {C5113FF2-671D-11E5-80CA-005056A729E5} | FRESNO | GATES | Bank 4 | CB 1107 | PGE\BXYD | 2017-01-24 09:48:32.0467359 -08:00 | 2539301107 | 253931109 | 8 | 1 | 1 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {EC90C1C5-59F1-44C0-AE6D-4B8A8DE57516}
3313 | 2511 | {5AA179DF-96F5-11E6-841B-D4BED91EFF1A} | HUMBOLDT | POTTER VALLEY P H | Bank 5 (Non SCADA) | CB 1105 (Non-SCADA) | PGE\DCGa | 2016-12-29 17:37:18.3153956 -08:00 |  | 253871102 | 8 | 3 | 3 | 1 | 190 | 4.15 | 4.11 | 180 | 3.93 | 3.89 | 190 | 4.15 | 4.11 | 190 | 4.15 | 4.11 | 190 | 4.15 | 4.11 | 190 | 4.15 | 4.11 | 190 | 4.15 | 4.11 | 190 | 4.15 | 4.11 |  |  | FALSE | TRUE | 180 | 235 | 217 | 271 | {00000000-0000-0000-0000-000000000000}
3314 | 2656 | {C5113FF7-671D-11E5-80CA-005056A729E5} | FRESNO | GATES | Bank 4 | CB 1108 | PGE\BXYD | 2017-01-24 09:50:41.8083677 -08:00 | 2539301108 | 253871103 | 8 | 1 | 1 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {65E757D5-0F22-4DBB-937D-25309D8306FF}
3315 | 2656 | {C5113FFC-671D-11E5-80CA-005056A729E5} | FRESNO | GATES | Bank 4 | CB 1109 | PGE\BXYD | 2017-01-24 09:52:25.4398320 -08:00 | 2539301109 | 102041101 | 8 | 1 | 1 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {E298FA7E-ED33-4269-96EA-B170A59CEFEE}
3316 | 2665 | {DD064367-671D-11E5-80CA-005056A729E5} | KERN | COPUS | Bank 1 | CB 1102 | PGE\T1SI | 2016-10-20 17:43:39.5547203 -07:00 | 2538701102 | 102041102 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 282 | 6.15 | 6.09 | 500 | 10.91 | 10.8 | 315 | 6.87 | 6.8 | 500 | 10.91 | 10.8 | 358 | 7.81 | 7.73 | 500 | 10.91 | 10.8 | 382 | 8.34 | 8.26 |  |  | FALSE | FALSE | 577 | 750 | 692 | 842 | {125E3E32-7818-47AC-80E9-29B7590F028E}
3317 | 2665 | {DD06436F-671D-11E5-80CA-005056A729E5} | KERN | COPUS | Bank 1 | CB 1103 (Non-SCADA) | PGE\T1SI | 2016-10-20 17:57:29.6042472 -07:00 | 2538701103 | 102041103 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 577 | 750 | 692 | 842 | {CD82F06B-A5FA-4AB1-BB78-573A95C3A4D9}
3318 | 2666 | {9A705D82-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | NOTRE DAME | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-20 19:34:47.6902652 -07:00 | 1020401101 | 102041104 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | TRUE | 2061 | 2680 | 2474 | 3092 | {0848108A-CB59-480F-BBD0-A7A3A7334E0E}
3319 | 2666 | {9A705D8B-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | NOTRE DAME | Bank 1 | CB 1102 | PGE\C8M4 | 2016-10-20 19:45:21.7204286 -07:00 | 1020401102 | 103381101 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | TRUE | 2061 | 2680 | 2474 | 3092 | {40B59C20-634C-49A1-A4B4-EA2559A3C5EA}
3320 | 2666 | {9A705DA9-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | NOTRE DAME | Bank 1 | CB 1103 | PGE\C8M4 | 2016-10-20 19:50:02.5244334 -07:00 | 1020401103 | 103381102 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | TRUE | 2061 | 2680 | 2474 | 3092 | {063282E4-79D7-47E1-AB31-F30577005E1A}
3321 | 2666 | {9A705DB2-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | NOTRE DAME | Bank 1 | CB 1104 | PGE\C8M4 | 2016-10-20 19:52:19.5443310 -07:00 | 1020401104 | 102851101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | TRUE | 2061 | 2680 | 2474 | 3092 | {CADBC70F-F6CE-4DCE-A922-9489C9626C6C}
3322 | 2667 | {8D29892C-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | FRENCH GULCH | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-20 20:06:44.6115959 -07:00 | 1033801101 | 102851102 | 8 | 3 | 3 | 1 | 190 | 4.15 | 4.11 | 91 | 1.99 | 1.97 | 190 | 4.15 | 4.11 | 119 | 2.6 | 2.57 | 190 | 4.15 | 4.11 | 110 | 2.4 | 2.38 | 190 | 4.15 | 4.11 | 137 | 2.99 | 2.96 |  |  | FALSE | TRUE | 91 | 119 | 110 | 137 | {536471AC-3951-47BC-85AE-7F6B17B09882}
3323 | 2667 | {8D298935-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | FRENCH GULCH | Bank 1 | CB 1102 | PGE\C8M4 | 2016-10-20 20:09:56.2628900 -07:00 | 1033801102 | 103142101 | 8 | 3 | 3 | 1 | 150 | 3.27 | 3.24 | 91 | 1.99 | 1.97 | 150 | 3.27 | 3.24 | 119 | 2.6 | 2.57 | 150 | 3.27 | 3.24 | 110 | 2.4 | 2.38 | 150 | 3.27 | 3.24 | 137 | 2.99 | 2.96 |  |  | FALSE | TRUE | 91 | 119 | 110 | 137 | {1F3AECA8-1582-4929-AA6E-AE1CDAC95A12}
3324 | 2668 | {941FA1BB-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | JACINTO | Bank 1 | CB 1101 | PGE\SDK6 | 2017-01-20 15:58:13.6856003 -08:00 | 1028501101 | 103142102 | 8 | 3 | 3 | 1 | 298 | 6.5 | 6.44 | 283 | 6.18 | 6.12 | 333 | 7.27 | 7.2 | 316 | 6.9 | 6.83 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {52DF024D-77E6-4893-AE40-43C7D3F054D7}
3326 | 2668 | {941FA1E7-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | JACINTO | Bank 1 | CB 1102 | PGE\SDK6 | 2017-02-02 15:53:28.9905091 -08:00 | 1028501102 | 102741101 | 8 | 3 | 3 | 1 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {B6186A29-A157-4BB5-B86A-960DEB1ABC74}
3327 | 2669 | {941FA2EF-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | LOGAN CREEK | Bank 1 | CB 2101 | PGE\SDK6 | 2017-01-20 15:56:13.5476900 -08:00 | 1031402101 | 102741103 | 12 | 3 | 3 | 1 | 530 | 20.03 | 19.83 | 530 | 20.03 | 19.83 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {690AA76D-0A3D-42F2-9238-2EF8341D95F1}
3328 | 2669 | {941FA345-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | LOGAN CREEK | Bank 1 | CB 2102 | PGE\SDK6 | 2017-01-20 15:56:47.7903485 -08:00 | 1031402102 | 102741104 | 12 | 3 | 3 | 1 | 530 | 20.03 | 19.83 | 530 | 20.03 | 19.83 | 633 | 23.92 | 23.68 | 633 | 23.92 | 23.68 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 633 | 23.92 | 23.68 | 633 | 23.92 | 23.68 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {81EC3374-457F-4987-9AE8-AEB357A92BC8}
3329 | 2670 | {ACCC4F76-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | WILLOWS A | Bank 1 | CB 1101 | PGE\SDK6 | 2017-01-20 15:51:30.4022450 -08:00 | 1027401101 | 103732101 | 8 | 3 | 3 | 1 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 |  |  | FALSE | FALSE | 641 | 722 | 722 | 722 | {17C551BB-88C8-4199-87E9-BF78B1B1100F}
3330 | 2670 | {ACCC4F7F-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | WILLOWS A | Bank 1 | CB 1103 | PGE\SDK6 | 2017-01-20 15:52:01.7588480 -08:00 | 1027401103 | 103571103 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 641 | 722 | 722 | 722 | {CF5C0383-B1B7-4499-A9C7-A492FAB9FFD9}
3331 | 2670 | {ACCC4F8F-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | WILLOWS A | Bank 1 | CB 1104 | PGE\SDK6 | 2017-01-20 15:53:06.0944852 -08:00 | 1027401104 | 103571104 | 8 | 3 | 3 | 1 | 282 | 6.15 | 6.09 | 267 | 5.83 | 5.77 | 315 | 6.87 | 6.8 | 299 | 6.53 | 6.46 | 358 | 7.81 | 7.73 | 340 | 7.42 | 7.35 | 382 | 8.34 | 8.26 | 362 | 7.9 | 7.82 |  |  | FALSE | FALSE | 641 | 722 | 722 | 722 | {D6896C40-AE80-4EF8-B5A7-B2BA50BA3310}
3332 | 2671 | {A6861C43-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | PIT NO 3 | Bank 2 | CB 2101 | PGE\SDK6 | 2017-01-25 09:14:09.7794167 -08:00 | 1037302101 | 014351110 | 12 | 3 | 3 | 1 | 210 | 7.94 | 7.86 | 210 | 7.94 | 7.86 | 210 | 7.94 | 7.86 | 210 | 7.94 | 7.86 | 210 | 7.94 | 7.86 | 210 | 7.94 | 7.86 | 210 | 7.94 | 7.86 | 210 | 7.94 | 7.86 |  |  | TRUE | FALSE | 277 | 333 | 333 | 333 | {7BA8BC43-2CF2-47DD-8199-09D48A6352D8}
3333 | 2674 | {ACCC4E72-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | TYLER | Bank 1 | CB 1103 | PGE\C8M4 | 2016-10-20 21:28:14.2811623 -07:00 | 1035701103 | 014351111 | 8 | 3 | 3 | 1 | 438 | 9.56 | 9.46 | 160 | 3.49 | 3.46 | 500 | 10.91 | 10.8 | 208 | 4.54 | 4.49 | 500 | 10.91 | 10.8 | 192 | 4.19 | 4.15 | 500 | 10.91 | 10.8 | 240 | 5.24 | 5.19 |  |  | FALSE | TRUE | 160 | 208 | 192 | 240 | {82C63310-5944-4EC7-8F97-1FEC2A5B26B6}
3334 | 2674 | {ACCC4E7B-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | TYLER | Bank 1 | CB 1104 | PGE\C8M4 | 2016-10-20 21:31:25.6829545 -07:00 | 1035701104 | 182090402 | 8 | 3 | 3 | 1 | 438 | 9.56 | 9.46 | 160 | 3.49 | 3.46 | 500 | 10.91 | 10.8 | 208 | 4.54 | 4.49 | 500 | 10.91 | 10.8 | 192 | 4.19 | 4.15 | 500 | 10.91 | 10.8 | 240 | 5.24 | 5.19 |  |  | FALSE | TRUE | 160 | 208 | 192 | 240 | {9C1FB38D-85E0-43F2-B1E4-49FF0A760AC3}
3336 | 2677 | {C3D95808-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | FREMONT | Bank 3 | CB 1110 | PGE\RDR1 | 2017-06-01 10:42:44.1130325 -07:00 | 0143501110 | 014351112 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {3AC1892E-D4FD-4C8F-AC45-7050996D4B95}
3337 | 2677 | {C3D9584C-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | FREMONT | Bank 3 | CB 1111 | PGE\RDR1 | 2017-06-01 10:43:34.9394615 -07:00 | 0143501111 | 182090403 | 7 | 3 | 3 | 2 | 581 | 12.55 | 12.42 | 581 | 12.55 | 12.42 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 598 | 12.92 | 12.79 | 598 | 12.92 | 12.79 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {308AA889-98A5-4357-9974-3FB4645010BD}
3338 | 2629 | {550A645A-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | MONTEREY | Bank 1 | CB 402 (Non-SCADA) | PGE\ACT0 | 2016-11-22 15:31:37.5640065 -08:00 | 182090402 | 182090404 | 3 | 3 | 3 | 2 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 390 | 2.81 | 2.78 | 390 | 2.81 | 2.78 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 450 | 3.24 | 3.21 | 450 | 3.24 | 3.21 |  |  | FALSE | FALSE | 1457 | 1716 | 1716 | 1716 | {E1ABA6A5-06F7-4231-905F-94509F7E1115}
3339 | 2677 | {C3D95855-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | FREMONT | Bank 3 | CB 1112 | PGE\RDR1 | 2017-06-01 10:44:28.5115785 -07:00 | 0143501112 | 182611102 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {A695F9F2-C64C-4230-8867-8DEBAD016090}
3341 | 2629 | {13B44422-0B42-11E6-9D37-D4BED91EFF1A} | CENTRAL COAST | MONTEREY | Bank 1 | CB 403 (Non-SCADA) | PGE\ACT0 | 2016-11-22 16:12:55.1804360 -08:00 | 182090403 | 182611103 | 3 | 3 | 3 | 2 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 390 | 2.81 | 2.78 | 390 | 2.81 | 2.78 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 450 | 3.24 | 3.21 | 450 | 3.24 | 3.21 |  |  | FALSE | FALSE | 1457 | 1716 | 1716 | 1716 | {8E83C5F8-E705-4744-9E9C-B1B14AD438E5}
3342 | 2629 | {550A6460-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | MONTEREY | Bank 1 | CB 404 (Non-SCADA) | PGE\ACT0 | 2016-10-21 08:35:04.7898007 -07:00 | 182090404 | 182090405 | 3 | 3 | 3 | 2 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 390 | 2.81 | 2.78 | 390 | 2.81 | 2.78 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 450 | 3.24 | 3.21 | 450 | 3.24 | 3.21 |  |  | FALSE | FALSE | 1457 | 1716 | 1716 | 1716 | {EA58B1A2-6303-4B94-9F23-B464273980B3}
3343 | 2589 | {79E5375C-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | PASO ROBLES | Bank 1 | CB 1102 | PGE\A9S5 | 2016-11-11 10:20:38.6341609 -08:00 | 1826101102 | 182391102 | 8 | 3 | 3 | 1 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {A29C86A1-5EB1-44D7-993E-878AD369818D}
3344 | 2589 | {8018150F-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | PASO ROBLES | Bank 1 | CB 1103 | PGE\A9S5 | 2016-11-11 10:21:06.6221755 -08:00 | 1826101103 | 163291101 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {69A79113-C551-42B2-8830-54F8E11A5C51}
3345 | 2629 | {550A6463-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | MONTEREY | Bank 1 | CB 405 (Non-SCADA) | PGE\ACT0 | 2016-11-23 13:42:31.5956385 -08:00 | 182090405 | 163291102 | 3 | 3 | 3 | 2 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 375 | 2.7 | 2.67 | 375 | 2.7 | 2.67 | 314 | 2.26 | 2.24 | 314 | 2.26 | 2.24 | 396 | 2.85 | 2.82 | 396 | 2.85 | 2.82 |  |  | FALSE | FALSE | 1457 | 1716 | 1716 | 1716 | {CECD2A0E-BF1D-4ED8-B51E-B89DB93F4991}
3346 | 2678 | {550A646F-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | OILFIELDS | Bank 1 | CB 1102 | PGE\ACT0 | 2016-10-21 09:58:03.5202390 -07:00 | 1823901102 | 163291103 | 8 | 4 | 3 | 1 | 745 | 16.26 | 16.1 | 745 | 16.26 | 16.1 | 838 | 18.29 | 18.11 | 838 | 18.29 | 18.11 | 972 | 21.21 | 21 | 972 | 21.21 | 21 | 1000 | 21.82 | 21.6 | 1000 | 21.82 | 21.6 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {ABFF1B6C-0194-4741-A931-BC099E8BE086}
3347 | 2679 | {3697976B-671D-11E5-80CA-005056A729E5} | STOCKTON | FRENCH CAMP | Bank 1 | CB 1101 | PGE\SZC1 | 2016-10-21 10:17:37.1864300 -07:00 | 1632901101 | 163291104 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {5DF4CCDE-0F51-4562-B413-4B909EB97613}
3348 | 2679 | {36979770-671D-11E5-80CA-005056A729E5} | STOCKTON | FRENCH CAMP | Bank 1 | CB 1102 | PGE\BXYD | 2017-01-12 15:04:54.5298020 -08:00 | 1632901102 | 182391103 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {089E9686-EF20-49EC-8AB3-9909F2E862AB}
3349 | 2681 | {36979781-671D-11E5-80CA-005056A729E5} | STOCKTON | FRENCH CAMP | Bank 2 | CB 1103 | PGE\BXYD | 2017-01-12 15:13:00.0205141 -08:00 | 1632901103 | 182391104 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 489 | 10.67 | 10.56 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {7788FB55-B8A8-4AEC-92F1-BEBAFE5B7211}
3350 | 2681 | {36979786-671D-11E5-80CA-005056A729E5} | STOCKTON | FRENCH CAMP | Bank 2 | CB 1104 | PGE\BXYD | 2017-01-12 15:13:58.4428886 -08:00 | 1632901104 | 083450401 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 633 | 13.81 | 13.67 | 633 | 13.81 | 13.67 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 633 | 13.81 | 13.67 | 633 | 13.81 | 13.67 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {C7C2EEF0-F29D-45CA-BDAC-493D3517AAE7}
3351 | 2680 | {550A6475-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | OILFIELDS | Bank 2 | CB 1103 | PGE\ACT0 | 2016-10-21 10:58:20.0219638 -07:00 | 1823901103 | 083450402 | 8 | 4 | 3 | 1 | 572 | 12.48 | 12.36 | 572 | 12.48 | 12.36 | 744 | 16.24 | 16.08 | 744 | 16.24 | 16.08 | 687 | 14.99 | 14.84 | 687 | 14.99 | 14.84 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {96401F7A-0954-4780-8708-BF1C943849AC}
3352 | 2680 | {5B0C2095-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | OILFIELDS | Bank 2 | CB 1104 | PGE\ACT0 | 2016-11-29 16:07:51.9358075 -08:00 | 1823901104 | 152031101 | 8 | 4 | 4 | 2 | 962 | 20.99 | 20.78 | 913 | 19.93 | 19.73 | 1200 | 26.19 | 25.93 | 1140 | 24.88 | 24.63 | 1154 | 25.18 | 24.93 | 1096 | 23.92 | 23.68 | 1200 | 26.19 | 25.93 | 1140 | 24.88 | 24.63 |  |  | TRUE | FALSE | 962 | 1250 | 1154 | 1443 | {CF6CB6EC-3AB2-4EC8-953F-108553100F67}
3353 | 2683 | {611D1EDF-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | OPAL CLIFFS | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\ACT0 | 2016-11-22 16:15:19.9037858 -08:00 | 083450401 | 152031102 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 450 | 3.41 | 3.38 | 450 | 3.41 | 3.38 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {3A7B87F7-DEDE-435D-A925-5DD8ED417107}
3354 | 2684 | {E8FA3908-0B3F-11E6-9D37-D4BED91EFF1A} | CENTRAL COAST | OPAL CLIFFS | BANK 2 (Non SCADA) | CB 402 (Non-SCADA) | PGE\ACT0 | 2016-10-21 11:23:47.2741685 -07:00 | 083450402 | 152031103 | 4 | 4 | 4 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 455 | 3.44 | 3.41 | 455 | 3.44 | 3.41 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {842761E2-35A8-427C-9995-E6D038B70309}
3357 | 2685 | {A0BFD3C0-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | GRASS VALLEY | Bank 2 | CB 1101 | PGE\RVS7 | 2016-10-21 11:24:37.7060922 -07:00 | 1520301101 | 182941101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | * Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. Actual capabilities: SN = 620 Amps, SE = 620 Amps, WN = 620 Amps, WE = 620 Amps. |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {B2C58DA1-ADCD-4F93-B355-38338BE87BC5}
3358 | 2685 | {A0BFD3C9-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | GRASS VALLEY | Bank 2 | CB 1102 | PGE\RVS7 | 2016-10-21 11:26:32.7229605 -07:00 | 1520301102 | 182941102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | * Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. Actual capabilities: SN = 620 Amps, SE = 620 Amps, WN = 620 Amps, WE = 620 Amps. |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {9BC26505-4391-4C2C-ADCB-1ED6C5C8F359}
3359 | 2685 | {A0BFD3D2-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | GRASS VALLEY | Bank 2 | CB 1103 | PGE\RVS7 | 2016-10-21 11:28:18.8242251 -07:00 | 1520301103 | 102050401 | 8 | 4 | 4 | 2 | 582 | 12.7 | 12.57 | 582 | 12.7 | 12.57 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | * Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. Actual capabilities: WN = 620 Amps, WE = 620 Amps. |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {2653C661-620D-4D78-B885-08274AFE24FA}
3360 | 2686 | {611D1EE8-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | OTTER | Bank 1 | CB 1101 | PGE\MTDR | 2017-07-11 11:17:58.6022947 -07:00 | 1829401101 | 102050402 | 8 | 3 | 3 | 2 | 321 | 7.01 | 6.94 | 304 | 6.63 | 6.56 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 430 | 559 | 516 | 646 | {0C967E01-F271-4C14-8D2B-A7D43B3EA62D}
3361 | 2686 | {611D1EF1-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | OTTER | Bank 1 | CB 1102 | PGE\ACT0 | 2016-11-22 16:18:44.0637696 -08:00 | 1829401102 | 012501102 | 8 | 3 | 3 | 2 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 169 | 3.69 | 3.65 | 169 | 3.69 | 3.65 | 198 | 4.32 | 4.28 | 198 | 4.32 | 4.28 | 211 | 4.6 | 4.55 | 211 | 4.6 | 4.55 |  |  | FALSE | FALSE | 430 | 559 | 516 | 646 | {F075B84F-E310-4F34-AE41-6EE3A5F87EF8}
3367 | 2690 | {80989127-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CHICO A | Bank 1 | CB 401 | PGE\DCGa | 2016-10-21 17:10:46.8345472 -07:00 | 102050401 | 012501105 | 4 | 3 | 3 | 1 | 345 | 2.61 | 2.58 | 345 | 2.61 | 2.58 | 386 | 2.92 | 2.89 | 386 | 2.92 | 2.89 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | TRUE | 660 | 858 | 792 | 990 | {EA5502A3-27DF-4839-9C1D-45B8BF31076C}
3368 | 2690 | {80989130-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CHICO A | Bank 1 | CB 402 | PGE\DCGa | 2016-10-21 17:13:42.8053468 -07:00 | 102050402 | 012501111 | 4 | 3 | 3 | 1 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | TRUE | 660 | 858 | 792 | 990 | {0AEB724E-8454-4F40-8640-F64A705002E2}
3369 | 1075 | {47205EB4-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 2 | CB 1102 (Non-SCADA) | PGE\MUSF | 2017-04-06 14:50:33.9405013 -07:00 | 0125001102 | 012501113 | 7 | 3 | 3 | 2 | 492 | 10.63 | 10.52 | 467 | 10.09 | 9.99 | 554 | 11.97 | 11.85 | 526 | 11.36 | 11.25 | 533 | 11.51 | 11.39 | 532 | 11.49 | 11.38 | 598 | 12.92 | 12.79 | 568 | 12.27 | 12.15 |  |  | FALSE | FALSE | 1541 | 2004 | 1850 | 2312 | {94EE3F0C-E152-4473-8335-E2599C03394D}
3370 | 1075 | {47205EB7-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 2 | CB 1105 (Non-SCADA) | PGE\MUSF | 2017-04-06 15:10:35.6551077 -07:00 | 0125001105 | 012501114 | 7 | 3 | 3 | 2 | 513 | 11.08 | 10.97 | 513 | 11.08 | 10.97 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 528 | 11.4 | 11.29 | 528 | 11.4 | 11.29 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 1541 | 2004 | 1850 | 2312 | {0FD0801A-3CEA-4BBD-B8D0-B849D3661537}
3371 | 1075 | {47205EC6-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 2 | CB 1111 (Non-SCADA) | PGE\MUSF | 2017-04-06 15:35:33.1183057 -07:00 | 0125001111 | 012501101 | 7 | 3 | 3 | 2 | 425 | 9.18 | 9.09 | 425 | 9.18 | 9.09 | 476 | 10.28 | 10.18 | 476 | 10.28 | 10.18 | 438 | 9.46 | 9.37 | 438 | 9.46 | 9.37 | 490 | 10.58 | 10.47 | 490 | 10.58 | 10.47 |  |  | FALSE | FALSE | 1541 | 2004 | 1850 | 2312 | {3F8EB3CE-3D77-4D5E-80B9-CBF593EEA8A6}
3372 | 1075 | {47205EC9-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 2 | CB 1113 (Non-SCADA) | PGE\C7CF | 2016-12-15 20:00:04.0222772 -08:00 | 0125001113 | 012501104 | 7 | 3 | 3 | 2 | 427 | 9.22 | 9.13 | 427 | 9.22 | 9.13 | 474 | 10.24 | 10.14 | 474 | 10.24 | 10.14 | 440 | 9.5 | 9.4 | 440 | 9.5 | 9.4 | 488 | 10.54 | 10.43 | 488 | 10.54 | 10.43 |  |  | FALSE | FALSE | 1541 | 2004 | 1850 | 2312 | {7C7F6133-3411-4F2F-848A-EEF00879E69E}
3373 | 1075 | {47205ED2-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 2 | CB 1114 (Non-SCADA) | PGE\C7CF | 2016-12-12 14:36:14.3508867 -08:00 | 0125001114 | 012501106 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 614 | 13.4 | 13.27 | 614 | 13.4 | 13.27 | 623 | 13.6 | 13.46 | 623 | 13.6 | 13.46 | 666 | 14.53 | 14.38 | 666 | 14.53 | 14.38 |  |  | FALSE | FALSE | 1541 | 2004 | 1850 | 2312 | {C6033767-E244-43B2-9938-57CC2C394732}
3374 | 1076 | {47205EE1-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 4 | CB 1101 (Non-SCADA) | PGE\C7CF | 2016-12-12 14:38:33.1615021 -08:00 | 0125001101 | 253481101 | 8 | 3 | 3 | 2 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 2749 | 3574 | 3299 | 4123 | {7E27C9D1-6349-4497-AC49-06D5E8BC4FE5}
3375 | 1076 | {47205EE7-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 4 | CB 1104 (Non-SCADA) | PGE\C7CF | 2016-12-12 14:40:45.5175355 -08:00 | 0125001104 | 253481102 | 8 | 3 | 3 | 2 | 478 | 10.43 | 10.33 | 478 | 10.43 | 10.33 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 492 | 10.74 | 10.63 | 492 | 10.74 | 10.63 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 2749 | 3574 | 3299 | 4123 | {DCFA1064-A159-474C-8B83-AB3BAE4046ED}
3376 | 1076 | {47205EED-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 4 | CB 1106 (Non-SCADA) | PGE\C7CF | 2016-12-12 14:42:18.2436417 -08:00 | 0125001106 | 253481103 | 8 | 3 | 3 | 2 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 2749 | 3574 | 3299 | 4123 | {6CCAF637-86D6-4325-8349-0628A301C663}
3377 | 2692 | {00138EAE-671E-11E5-80CA-005056A729E5} | KERN | WHEELER RIDGE | Bank 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\BXYD | 2016-10-24 09:35:36.1073365 -07:00 | 2534801101 | 102541101 | 8 | 3 | 3 | 1 | 434 | 9.47 | 9.38 | 434 | 9.47 | 9.38 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 |  |  | FALSE | FALSE | 824 | 1072 | 989 | 1237 | {5700DDD8-552B-48B2-A137-96120C7C6D75}
3378 | 2692 | {00138EC6-671E-11E5-80CA-005056A729E5} | KERN | WHEELER RIDGE | Bank 1 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\BXYD | 2016-10-24 09:31:21.9782998 -07:00 | 2534801102 | 102541102 | 8 | 3 | 3 | 1 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 |  |  | FALSE | FALSE | 824 | 1072 | 989 | 1237 | {60587C78-9C99-4E32-9A9E-B8421F8FE2CE}
3379 | 2692 | {00138EC9-671E-11E5-80CA-005056A729E5} | KERN | WHEELER RIDGE | Bank 1 (Non SCADA) | CB 1103 (Non-SCADA) | PGE\BXYD | 2016-10-24 09:33:09.8763604 -07:00 | 2534801103 | 253701101 | 8 | 3 | 3 | 1 | 282 | 6.15 | 6.09 | 282 | 6.15 | 6.09 | 315 | 6.87 | 6.8 | 315 | 6.87 | 6.8 | 358 | 7.81 | 7.73 | 358 | 7.81 | 7.73 | 382 | 8.34 | 8.26 | 382 | 8.34 | 8.26 |  |  | FALSE | FALSE | 824 | 1072 | 989 | 1237 | {23B833FB-1819-40DE-A28B-98158575D585}
3380 | 2693 | {ACCC4EC8-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | VOLTA | Bank 2 | CB 1101 | PGE\C8M4 | 2016-10-24 09:43:56.0294818 -07:00 | 1025401101 | 253701102 | 8 | 4 | 4 | 1 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 |  |  | FALSE | TRUE | 962 | 1250 | 1154 | 1443 | {DB8FE147-B133-4BF3-9CE3-302B65840A75}
3382 | 2693 | {ACCC4F0A-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | VOLTA | Bank 2 | CB 1102 | PGE\C8M4 | 2016-10-24 09:46:33.0267682 -07:00 | 1025401102 | 253701103 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | TRUE | 962 | 1250 | 1154 | 1443 | {6EF0AAAB-3AB4-4F4A-9AF9-719B66B8EDDD}
3383 | 2694 | {00138E30-671E-11E5-80CA-005056A729E5} | KERN | WESTPARK | Bank 1 | CB 1101 | PGE\BXYD | 2016-10-26 17:08:57.0932856 -07:00 | 2537001101 | 253701104 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1832 | 2382 | 2199 | 2749 | {AECF2F34-6A40-43B5-B042-A793C98D5303}
3384 | 2694 | {00138E38-671E-11E5-80CA-005056A729E5} | KERN | WESTPARK | Bank 1 | CB 1102 | PGE\BXYD | 2016-10-24 09:52:53.3001048 -07:00 | 2537001102 | 253701105 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 539 | 11.76 | 11.64 | 539 | 11.76 | 11.64 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1832 | 2382 | 2199 | 2749 | {A4570D31-6D4C-4CC0-9BEC-89563B7B77DF}
3385 | 2694 | {00138E43-671E-11E5-80CA-005056A729E5} | KERN | WESTPARK | Bank 1 | CB 1103 | PGE\BXYD | 2016-10-24 09:54:51.0136692 -07:00 | 2537001103 | 253701106 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1832 | 2382 | 2199 | 2749 | {3A16ECB9-0295-4A2B-AE9E-3632156746B9}
3386 | 2694 | {00138E4E-671E-11E5-80CA-005056A729E5} | KERN | WESTPARK | Bank 1 | CB 1104 | PGE\BXYD | 2016-10-24 09:58:26.1325691 -07:00 | 2537001104 | 103601101 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1832 | 2382 | 2199 | 2749 | {0756E80F-0695-44B0-A693-1276AB5FA777}
3387 | 2695 | {00138E5C-671E-11E5-80CA-005056A729E5} | KERN | WESTPARK | Bank 2 | CB 1105 | PGE\BXYD | 2016-10-26 17:08:03.2240457 -07:00 | 2537001105 | 253701107 | 8 | 3 | 3 | 1 | 565 | 12.33 | 12.21 | 565 | 12.33 | 12.21 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {6AD64FEB-2358-4564-8AC3-3BC4BE9FA4C4}
3388 | 2695 | {00138E61-671E-11E5-80CA-005056A729E5} | KERN | WESTPARK | Bank 2 | CB 1106 | PGE\BXYD | 2016-10-24 10:06:43.7907374 -07:00 | 2537001106 | 253701108 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 639 | 13.95 | 13.81 | 639 | 13.95 | 13.81 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {221FEEA9-3545-4D07-B811-224F208AE5C1}
3389 | 2696 | {ACCC4F3C-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | WHITMORE | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-24 10:06:54.1029323 -07:00 | 1036001101 | 253701109 | 8 | 3 | 3 | 2 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 |  |  | FALSE | TRUE | 274 | 357 | 329 | 385 | {F836C07F-7D74-4BC0-90C4-72EBBB5B9641}
3391 | 2695 | {00138E66-671E-11E5-80CA-005056A729E5} | KERN | WESTPARK | Bank 2 | CB 1107 | PGE\BXYD | 2016-10-26 17:06:44.7483414 -07:00 | 2537001107 | 103611101 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {BB090CD8-4E68-44B5-91C9-104EF3C220ED}
3392 | 2695 | {00138E6E-671E-11E5-80CA-005056A729E5} | KERN | WESTPARK | Bank 2 | CB 1108 | PGE\BXYD | 2016-10-24 10:11:15.2254087 -07:00 | 2537001108 | 253701110 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {1CFCB525-752A-4109-BB44-24E567CAA4B4}
3393 | 2697 | {00138E7F-671E-11E5-80CA-005056A729E5} | KERN | WESTPARK | Bank 3 | CB 1109 | PGE\BXYD | 2016-10-26 17:04:40.9633380 -07:00 | 2537001109 | 253701111 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {83446329-3C93-4B75-914D-792EE8B702DF}
3394 | 2698 | {ACCC4F60-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | WILDWOOD | Bank 1 | CB 1101 | PGE\SDK6 | 2017-01-25 13:07:40.1821130 -08:00 | 103611101 | 253701112 | 8 | 3 | 3 | 1 | 137 | 2.99 | 2.96 | 137 | 2.99 | 2.96 | 173 | 3.78 | 3.74 | 164 | 3.58 | 3.54 | 164 | 3.58 | 3.54 | 164 | 3.58 | 3.54 | 206 | 4.5 | 4.46 | 206 | 4.5 | 4.46 | Same capability for the 1100 feeder |  | FALSE | FALSE | 137 | 178 | 164 | 206 | {E8192D2E-5171-4958-ACA5-6EE1F5CD4CFA}
3395 | 2697 | {00138E90-671E-11E5-80CA-005056A729E5} | KERN | WESTPARK | Bank 3 | CB 1110 | PGE\BXYD | 2016-10-24 10:20:50.9233492 -07:00 | 2537001110 | 103551101 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {0E3DD6FA-AF7C-4886-B780-3FBF505820F6}
3396 | 2697 | {00138E9B-671E-11E5-80CA-005056A729E5} | KERN | WESTPARK | Bank 3 | CB 1111 | PGE\BXYD | 2016-10-24 10:23:34.0505497 -07:00 | 2537001111 | 254291103 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {B61F648C-4E2A-4D25-90EC-66C5C5CD441E}
3397 | 2697 | {00138EA0-671E-11E5-80CA-005056A729E5} | KERN | WESTPARK | Bank 3 | CB 1112 | PGE\BXYD | 2016-10-24 10:27:50.0164879 -07:00 | 2537001112 | 254291104 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {56152037-E665-4A9B-BCC4-9E2D4F91E4E6}
3398 | 2699 | {A6861D21-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | RISING RIVER | Bank 1 | CB 1101 | PGE\C8M4 | 2016-10-24 10:28:51.9882991 -07:00 | 1035501101 | 254291102 | 8 | 3 | 3 | 2 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 |  |  | FALSE | TRUE | 481 | 625 | 577 | 721 | {D125DBA5-2AF9-4ADF-ADC0-6476DC2073C5}
3399 | 2700 | {00138E13-671E-11E5-80CA-005056A729E5} | KERN | WELLFIELD | Bank 1 | CB 1103 (Non-SCADA) | PGE\BXYD | 2016-10-24 10:42:40.8612281 -07:00 | 2542901103 | 182611104 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 842 | 842 | 842 | {FA8F2EA0-394F-4B2B-8BF1-3E6A9EBA2D7A}
3400 | 2700 | {00138E16-671E-11E5-80CA-005056A729E5} | KERN | WELLFIELD | Bank 1 | CB 1104 (Non-SCADA) | PGE\BXYD | 2016-10-24 10:45:18.7603946 -07:00 | 2542901104 | 252971101 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 842 | 842 | 842 | {07AC18ED-03BC-4E46-8E2F-1D8BD609860C}
3401 | 2701 | {00138E1F-671E-11E5-80CA-005056A729E5} | KERN | WELLFIELD | Bank 2 | CB 1102 | PGE\BXYD | 2016-10-24 10:55:57.3532631 -07:00 | 2542901102 | 252971102 | 8 | 3 | 3 | 1 | 143 | 3.12 | 3.09 | 143 | 3.12 | 3.09 | 186 | 4.06 | 4.02 | 186 | 4.06 | 4.02 | 171 | 3.73 | 3.69 | 171 | 3.73 | 3.69 | 214 | 4.67 | 4.62 | 214 | 4.67 | 4.62 |  |  | FALSE | FALSE | 143 | 186 | 171 | 214 | {C6357E73-CDAB-4300-A828-130505E51CF8}
3402 | 1118 | {80181538-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | PASO ROBLES | Bank 2 | CB 1104 | PGE\A9S5 | 2016-11-11 10:22:42.0680151 -08:00 | 1826101104 | 252971103 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2060 | {29062981-D9D8-4AC0-ACC0-6E33D7A9930F}
3403 | 2702 | {00138DD8-671E-11E5-80CA-005056A729E5} | KERN | WEEDPATCH | Bank 1 | CB 1101 | PGE\BXYD | 2016-10-24 11:17:35.4840858 -07:00 | 2529701101 | 182611106 | 8 | 3 | 3 | 1 | 376 | 8.21 | 8.13 | 376 | 8.21 | 8.13 | 420 | 9.17 | 9.08 | 420 | 9.17 | 9.08 | 482 | 10.52 | 10.41 | 482 | 10.52 | 10.41 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {C017F543-A8FA-452E-BBEB-CB224142815C}
3404 | 2702 | {00138DE3-671E-11E5-80CA-005056A729E5} | KERN | WEEDPATCH | Bank 1 | CB 1102 | PGE\BXYD | 2016-10-24 11:20:42.1977988 -07:00 | 2529701102 | 252971105 | 8 | 4 | 4 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {748F5BB3-2E0C-40EF-B229-3BDE1D4E8A01}
3405 | 2702 | {00138DEB-671E-11E5-80CA-005056A729E5} | KERN | WEEDPATCH | Bank 1 | CB 1103 | PGE\BXYD | 2016-10-24 11:23:55.5253301 -07:00 | 2529701103 | 012501107 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {1DF7D22E-E78B-4BA8-9982-4D3CF4C44247}
3406 | 1118 | {8624F4B5-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | PASO ROBLES | Bank 2 | CB 1106 | PGE\A9S5 | 2016-11-11 10:23:42.0814935 -08:00 | 1826101106 | 012501110 | 8 | 3 | 3 | 1 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2060 | {A244B199-64FD-4DA3-B8B3-8D783C37CE6B}
3407 | 2702 | {359918FC-0B43-11E6-9D37-D4BED91EFF1A} | KERN | WEEDPATCH | Bank 1 | CB 1105 (Non-SCADA) | PGE\BXYD | 2016-10-24 11:27:25.5818508 -07:00 | 2529701105 | 012501201 | 8 | 3 | 3 | 1 | 282 | 6.15 | 6.09 | 282 | 6.15 | 6.09 | 315 | 6.87 | 6.8 | 315 | 6.87 | 6.8 | 358 | 7.81 | 7.73 | 358 | 7.81 | 7.73 | 382 | 8.34 | 8.26 | 382 | 8.34 | 8.26 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {5CFD1F6D-6ABC-4CAE-902D-37B99943965C}
3409 | 1076 | {4D5B0499-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 4 | CB 1107 | PGE\C7CF | 2016-12-12 14:43:24.5716986 -08:00 | 0125001107 | 012501202 | 8 | 3 | 3 | 2 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 2749 | 3574 | 3299 | 4123 | {DAEA6EA6-EDDD-455F-952F-8C23AD7CB48C}
3410 | 1076 | {4D5B04A1-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 4 | CB 1110 (Non-SCADA) | PGE\MUSF | 2017-05-25 10:20:23.1763523 -07:00 | 0125001110 | 012501203 | 7 | 3 | 3 | 2 | 478 | 10.32 | 10.22 | 478 | 10.32 | 10.22 | 531 | 11.47 | 11.36 | 531 | 11.47 | 11.36 | 492 | 10.63 | 10.52 | 492 | 10.63 | 10.52 | 546 | 11.79 | 11.67 | 546 | 11.79 | 11.67 |  |  | FALSE | FALSE | 2777 | 3611 | 3333 | 4166 | {2FC76C73-C64A-4F73-B20B-71547BC894B4}
3411 | 1076 | {4D5B04AD-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 4 | CB FG-1 | PGE\C7CF | 2016-11-18 15:35:25.9118889 -08:00 | 012501201 | 012501204 | 8 | 3 | 3 | 2 | 505 | 11.02 | 10.91 | 505 | 11.02 | 10.91 | 586 | 12.79 | 12.66 | 586 | 12.79 | 12.66 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 |  |  | FALSE | FALSE | 2749 | 3574 | 3299 | 4123 | {31421644-A9A0-4142-A2E8-C32923BF206C}
3412 | 1076 | {4D5B04B0-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 4 | CB FG-2 | PGE\C7CF | 2016-11-18 15:35:48.2362044 -08:00 | 012501202 | 182611107 | 8 | 3 | 3 | 2 | 505 | 11.02 | 10.91 | 505 | 11.02 | 10.91 | 586 | 12.79 | 12.66 | 586 | 12.79 | 12.66 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 |  |  | FALSE | FALSE | 2749 | 3574 | 3299 | 4123 | {6C9447A6-11BD-415F-B256-09645F535265}
3413 | 1076 | {4D5B04B3-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 4 | CB FG-3 | PGE\C7CF | 2016-11-18 15:36:10.0145024 -08:00 | 012501203 | 102051101 | 8 | 3 | 3 | 2 | 505 | 11.02 | 10.91 | 505 | 11.02 | 10.91 | 586 | 12.79 | 12.66 | 586 | 12.79 | 12.66 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 |  |  | FALSE | FALSE | 2749 | 3574 | 3299 | 4123 | {4E5F1611-08E4-4A3E-B21F-CC7C321BFF4D}
3414 | 1076 | {4D5B04B6-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 4 | CB FG-4 | PGE\C7CF | 2016-11-18 15:36:25.5635950 -08:00 | 012501204 | 252971106 | 8 | 3 | 3 | 2 | 505 | 11.02 | 10.91 | 505 | 11.02 | 10.91 | 586 | 12.79 | 12.66 | 586 | 12.79 | 12.66 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 |  |  | FALSE | FALSE | 2749 | 3574 | 3299 | 4123 | {1A924500-1F18-4D9E-A78D-A1D0438E99B4}
3415 | 1044 | {8C3C5B5E-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | PASO ROBLES | Bank 3 | CB 1107 | PGE\A9S5 | 2016-11-11 10:29:08.0824721 -08:00 | 1826101107 | 102051102 | 8 | 3 | 3 | 1 | 636 | 13.88 | 13.74 | 636 | 13.88 | 13.74 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 717 | 15.65 | 15.49 | 717 | 15.65 | 15.49 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {1D946968-AB42-4F82-83A8-C95D507315FB}
3418 | 2687 | {80989143-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CHICO A | Bank 2 | CB 1101 | PGE\C8M4 | 2016-10-24 12:23:49.0357157 -07:00 | 1020501101 | 102051103 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | TRUE | 962 | 1250 | 1154 | 1443 | {6398CC69-F5D8-41BC-9FF4-FBAF9FB55BBD}
3419 | 2702 | {00138DFC-671E-11E5-80CA-005056A729E5} | KERN | WEEDPATCH | Bank 1 | CB 1106 | PGE\BXYD | 2016-10-24 12:23:28.5400865 -07:00 | 2529701106 | 252961101 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {87480E21-143C-437C-8187-0F0830EF554E}
3420 | 2687 | {8098915A-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CHICO A | Bank 2 | CB 1102 | PGE\C8M4 | 2016-10-24 12:23:30.4110065 -07:00 | 1020501102 | 252961102 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | TRUE | 962 | 1250 | 1154 | 1443 | {119DAB36-1354-48B1-AD5F-5B99212A71DC}
3422 | 2687 | {80989178-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CHICO A | Bank 2 | CB 1103 | PGE\C8M4 | 2016-10-24 12:28:39.9476262 -07:00 | 1020501103 | 252961104 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | TRUE | 962 | 1250 | 1154 | 1443 | {BBFD28E3-3E41-4550-BF10-8565F081EC88}
3425 | 2703 | {F9A7A3F9-671D-11E5-80CA-005056A729E5} | KERN | WASCO | Bank 1 | CB 1101 | PGE\BXYD | 2016-10-24 12:37:27.4176988 -07:00 | 2529601101 | 183071101 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {A19B84B9-118C-41BE-AF01-3B5989FBAE75}
3426 | 2703 | {F9A7A401-671D-11E5-80CA-005056A729E5} | KERN | WASCO | Bank 1 | CB 1102 | PGE\BXYD | 2016-10-24 12:40:04.9084730 -07:00 | 2529601102 | 254401102 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {B2C8662D-E5C8-4F45-B8AA-1E4764AE0245}
3427 | 2703 | {F9A7A406-671D-11E5-80CA-005056A729E5} | KERN | WASCO | Bank 1 | CB 1104 | PGE\BXYD | 2016-10-24 12:41:35.9923394 -07:00 | 2529601104 | 254402105 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {800915B4-BE61-4474-9978-8AD9E11407D7}
3428 | 2704 | {92955E83-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | PERRY | Bank 2 | CB 1101 | PGE\A9S5 | 2016-11-11 10:33:03.6947570 -08:00 | 1830701101 | 254561103 | 8 | 3 | 3 | 1 | 240 | 5.24 | 5.19 | 240 | 5.24 | 5.19 | 312 | 6.81 | 6.74 | 312 | 6.81 | 6.74 | 288 | 6.29 | 6.23 | 288 | 6.29 | 6.23 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 240 | 312 | 288 | 360 | {0D3CC19B-CD82-4A5E-8725-ACC4CA831A43}
3429 | 2705 | {F9A7A3E4-671D-11E5-80CA-005056A729E5} | KERN | TWISSELMAN | Bank 1 | CB 1102 (Non-SCADA) | PGE\BXYD | 2016-10-24 12:55:10.7091999 -07:00 | 2544001102 | 254561104 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {1FD53010-FB8F-44CC-9B42-57F1D9D961C7}
3430 | 2706 | {F9A7A3EA-671D-11E5-80CA-005056A729E5} | KERN | TWISSELMAN | Bank 2 | CB 2105 (Non-SCADA) | PGE\BXYD | 2016-10-24 13:03:50.6076867 -07:00 | 2544002105 | 254561105 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {18079410-11BA-4410-91BA-486B24A2C1B4}
3431 | 2708 | {F9A7A3A8-671D-11E5-80CA-005056A729E5} | KERN | TUPMAN | Bank 1 | CB 1103 (Non-SCADA) | PGE\BXYD | 2016-10-24 13:15:47.5776589 -07:00 | 2545601103 | 254561106 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {D874EF9F-5685-41F4-8C41-698AD931269A}
3432 | 2708 | {F9A7A3B7-671D-11E5-80CA-005056A729E5} | KERN | TUPMAN | Bank 1 | CB 1104 | PGE\BXYD | 2016-10-24 13:19:02.2048755 -07:00 | 2545601104 | 255322101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {0701118C-CD7C-44EB-97F3-646E5FC4D3E3}
3433 | 2709 | {F9A7A3CB-671D-11E5-80CA-005056A729E5} | KERN | TUPMAN | Bank 2 | CB 1105 | PGE\BXYD | 2016-10-24 13:22:56.9160153 -07:00 | 2545601105 | 255322102 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1153 | 1153 | 1153 | 1153 | {983FBF72-6EC9-46D9-A923-B9BF1E4D76A5}
3434 | 2709 | {F9A7A3D0-671D-11E5-80CA-005056A729E5} | KERN | TUPMAN | Bank 2 | CB 1106 | PGE\BXYD | 2016-10-24 13:24:37.3580901 -07:00 | 2545601106 | 255322103 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1153 | 1153 | 1153 | 1153 | {9A06A17E-EEA1-488B-8078-F90883A6965B}
3435 | 2710 | {F9A7A33E-671D-11E5-80CA-005056A729E5} | KERN | TEVIS | Bank 1 | CB 2101 | PGE\BXYD | 2016-11-28 17:12:21.7943375 -08:00 | 2553202101 | 255322104 | 12 | 3 | 3 | 1 | 515 | 19.46 | 19.27 | 515 | 19.46 | 19.27 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 666 | 25.17 | 24.92 | 666 | 25.17 | 24.92 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {6534BB62-4EA7-4B6D-9331-54A05919EA22}
3436 | 2710 | {F9A7A35B-671D-11E5-80CA-005056A729E5} | KERN | TEVIS | Bank 1 | CB 2102 | PGE\BXYD | 2016-11-29 08:17:54.3026523 -08:00 | 2553202102 | 255322105 | 12 | 3 | 3 | 1 | 515 | 19.46 | 19.27 | 515 | 19.46 | 19.27 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 666 | 25.17 | 24.92 | 666 | 25.17 | 24.92 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {D643CCD7-D80F-42CA-9876-E84C1331395E}
3437 | 2710 | {F9A7A36F-671D-11E5-80CA-005056A729E5} | KERN | TEVIS | Bank 1 | CB 2103 | PGE\BXYD | 2016-11-07 08:53:50.9750651 -08:00 | 2553202103 | 252551104 | 12 | 3 | 3 | 1 | 515 | 19.46 | 19.27 | 515 | 19.46 | 19.27 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 634 | 23.96 | 23.72 | 634 | 23.96 | 23.72 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {888E6EFD-C148-4758-9755-8243DE94D937}
3438 | 2711 | {F9A7A37D-671D-11E5-80CA-005056A729E5} | KERN | TEVIS | Bank 2 | CB 2104 | PGE\BXYD | 2016-11-07 08:54:52.8233409 -08:00 | 2553202104 | 252552103 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {4E174404-2ADD-4F1B-8E69-B2EB31384D94}
3439 | 2711 | {F9A7A38B-671D-11E5-80CA-005056A729E5} | KERN | TEVIS | Bank 2 | CB 2105 | PGE\BXYD | 2016-11-07 08:55:18.8780129 -08:00 | 2553202105 | 252931102 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {366BCB62-C1B2-4C71-B16A-0A32D94BA7D5}
3440 | 2712 | {F9A7A323-671D-11E5-80CA-005056A729E5} | KERN | TEMBLOR | Bank 1 | CB 1104 (Non-SCADA) | PGE\BXYD | 2016-10-24 15:04:20.8566444 -07:00 | 2525501104 | 252931103 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {DED98EBC-C931-4BA0-8614-31A3C75D2046}
3441 | 2712 | {F9A7A332-671D-11E5-80CA-005056A729E5} | KERN | TEMBLOR | Bank 1 | CB 2103 (Non-SCADA) | PGE\BXYD | 2016-10-24 15:08:38.4091614 -07:00 | 2525502103 | 252931105 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {1EA47633-6FC9-47D6-BDEA-BF96ADD047AB}
3442 | 2713 | {F9A7A2EF-671D-11E5-80CA-005056A729E5} | KERN | TEJON | Bank 1 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\BXYD | 2016-10-24 15:42:30.4928466 -07:00 | 2529301102 | 252931106 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {46A66D07-2FBA-46A6-BB1F-224E4FAD0FE2}
3443 | 2713 | {F9A7A304-671D-11E5-80CA-005056A729E5} | KERN | TEJON | Bank 1 (Non SCADA) | CB 1103 (Non-SCADA) | PGE\BXYD | 2016-10-24 15:46:30.1683609 -07:00 | 2529301103 | 162421101 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {1ED8E4AB-3E5D-4492-BD4E-322B55A09269}
3444 | 2714 | {F9A7A30D-671D-11E5-80CA-005056A729E5} | KERN | TEJON | Bank 2 | CB 1105 | PGE\BXYD | 2016-10-24 16:00:31.3229060 -07:00 | 2529301105 | 162421106 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {0EE798DA-F121-4AF7-B10C-CB60A8E4018E}
3445 | 2714 | {F9A7A312-671D-11E5-80CA-005056A729E5} | KERN | TEJON | Bank 2 | CB 1106 | PGE\BXYD | 2016-10-24 16:02:11.7948980 -07:00 | 2529301106 | 162422103 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {C67D6F74-57D7-4AB7-8DC6-7373E608B9A4}
3446 | 2715 | {464AAFA0-671D-11E5-80CA-005056A729E5} | STOCKTON | STAGG | Bank 2 | CB 1101 | PGE\BXYD | 2017-01-11 10:38:36.4766943 -08:00 | 1624201101 | 162422104 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {63784D22-95D0-4FC5-9781-D2AEB80D3317}
3447 | 2715 | {464AAFAE-671D-11E5-80CA-005056A729E5} | STOCKTON | STAGG | Bank 2 | CB 1106 | PGE\DHN4 | 2016-10-25 07:56:40.3302025 -07:00 | 1624201106 | 162422105 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {3B26170A-5369-4D90-8A35-043B223BACAC}
3448 | 2717 | {464AAFCF-671D-11E5-80CA-005056A729E5} | STOCKTON | STAGG | Bank 5 | CB 2103 | PGE\BXYD | 2017-01-11 10:51:30.1636538 -08:00 | 1624202103 | 162701701 | 12 | 3 | 3 | 1 | 540 | 20.41 | 20.21 | 540 | 20.41 | 20.21 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 598 | 22.6 | 22.37 | 598 | 22.6 | 22.37 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {4FEF4DE9-F1BF-4FB0-BDD0-5E52572EBD99}
3449 | 2717 | {464AAFD4-671D-11E5-80CA-005056A729E5} | STOCKTON | STAGG | Bank 5 | CB 2104 | PGE\BXYD | 2017-01-11 11:15:30.7236881 -08:00 | 1624202104 | 162701702 | 12 | 3 | 3 | 1 | 573 | 21.66 | 21.44 | 573 | 21.66 | 21.44 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {CD0BEC57-0B82-4453-8B92-A8F23BEFA639}
3450 | 2717 | {464AAFDF-671D-11E5-80CA-005056A729E5} | STOCKTON | STAGG | Bank 5 | CB 2105 | PGE\BXYD | 2017-01-11 11:16:08.2887289 -08:00 | 1624202105 | 162701703 | 12 | 3 | 3 | 1 | 573 | 21.66 | 21.44 | 573 | 21.66 | 21.44 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {8DA12673-E56F-4560-AB24-AE0D4F203593}
3452 | 2716 | {4C486E48-671D-11E5-80CA-005056A729E5} | STOCKTON | VIERRA | Bank 1 | CB 1701 | PGE\BXYD | 2017-01-10 17:03:15.4771067 -08:00 | 1627001701 | 182440421 | 10 | 3 | 3 | 1 | 578 | 17.87 | 17.69 | 578 | 17.87 | 17.69 | 689 | 21.3 | 21.09 | 689 | 21.3 | 21.09 | 627 | 19.39 | 19.2 | 627 | 19.39 | 19.2 | 700 | 21.64 | 21.42 | 700 | 21.64 | 21.42 |  |  | FALSE | FALSE | 1455 | 1892 | 1746 | 2183 | {21A89678-3BA0-4223-9FF6-67EAB8CB1090}
3453 | 2716 | {4C486E62-671D-11E5-80CA-005056A729E5} | STOCKTON | VIERRA | Bank 1 | CB 1702 | PGE\BXYD | 2017-01-10 17:03:53.1679147 -08:00 | 1627001702 | 182440423 | 10 | 3 | 3 | 1 | 578 | 17.87 | 17.69 | 578 | 17.87 | 17.69 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 | 627 | 19.39 | 19.2 | 627 | 19.39 | 19.2 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 |  |  | FALSE | FALSE | 1455 | 1892 | 1746 | 2183 | {070CE46A-08DB-4F3F-A989-23C8FC3AA7C3}
3454 | 2716 | {4C486E6D-671D-11E5-80CA-005056A729E5} | STOCKTON | VIERRA | Bank 1 | CB 1703 | PGE\BXYD | 2017-01-10 17:04:36.0068877 -08:00 | 1627001703 | 163571701 | 10 | 3 | 3 | 1 | 636 | 19.66 | 19.46 | 636 | 19.66 | 19.46 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 |  |  | FALSE | FALSE | 1455 | 1892 | 1746 | 2183 | {8F4AE8CB-B620-4609-B6C0-15C484E62D3E}
3455 | 2691 | {611D1F0C-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | PACIFIC GROVE | Bank 1 (Non SCADA) | CB 421 (Non-SCADA) | PGE\ACT0 | 2016-11-23 10:29:34.1462439 -08:00 | 182440421 | 163571702 | 4 | 3 | 3 | 2 | 545 | 4.13 | 4.09 | 545 | 4.13 | 4.09 | 614 | 4.65 | 4.6 | 614 | 4.65 | 4.6 | 600 | 4.54 | 4.49 | 600 | 4.54 | 4.49 | 666 | 5.04 | 4.99 | 666 | 5.04 | 4.99 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {25466D2A-ED7C-431B-B621-751CE84748F1}
3456 | 2691 | {611D1F12-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | PACIFIC GROVE | Bank 1 (Non SCADA) | CB 423 (Non-SCADA) | PGE\ACT0 | 2016-11-23 14:21:38.9170732 -08:00 | 182440423 | 042031122 | 4 | 3 | 3 | 2 | 425 | 3.22 | 3.19 | 425 | 3.22 | 3.19 | 523 | 3.96 | 3.92 | 523 | 3.96 | 3.92 | 438 | 3.32 | 3.29 | 438 | 3.32 | 3.29 | 530 | 4.01 | 3.97 | 530 | 4.01 | 3.97 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {9B7CACCF-3CF2-4946-8279-DEAD52248520}
3457 | 2718 | {2FE3CAC7-671D-11E5-80CA-005056A729E5} | STOCKTON | AVENA | Bank 1 | CB 1701 | PGE\JCD5 | 2017-05-18 15:05:05.1335956 -07:00 | 1635701701 | 042031123 | 9 | 1 | 1 | 1 | 495 | 14.58 | 14.43 | 470 | 13.84 | 13.7 | 500 | 14.72 | 14.57 | 500 | 14.72 | 14.57 | 500 | 14.72 | 14.57 | 500 | 14.72 | 14.57 | 500 | 14.72 | 14.57 | 500 | 14.72 | 14.57 |  |  | FALSE | FALSE | 543 | 706 | 652 | 815 | {ABC3F7F6-30E1-47D7-8B6F-643DB147D6DD}
3460 | 2718 | {2FE3CAD2-671D-11E5-80CA-005056A729E5} | STOCKTON | AVENA | Bank 1 | CB 1702 | PGE\BXYD | 2017-01-17 10:36:49.2504356 -08:00 | 1635701702 | 252081101 | 9 | 1 | 1 | 1 | 475 | 13.99 | 13.85 | 470 | 13.84 | 13.7 | 500 | 14.72 | 14.57 | 500 | 14.72 | 14.57 | 500 | 14.72 | 14.57 | 500 | 14.72 | 14.57 | 500 | 14.72 | 14.57 | 500 | 14.72 | 14.57 |  |  | FALSE | FALSE | 475 | 618 | 570 | 713 | {4AEBF409-4EE7-4400-BC48-9F3B6CFF9D2B}
3461 | 2637 | {B1F47D64-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | ALTO | Bank 1 | CB 1122 | PGE\C7CF | 2016-12-19 12:53:16.6680697 -08:00 | 0420301122 | 252081103 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 592 | 12.92 | 12.79 | 592 | 12.92 | 12.79 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {26C6EB80-0665-4ADD-B4D7-F1A8C3EC837E}
3462 | 2637 | {B1F47D75-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | ALTO | Bank 1 | CB 1123 | PGE\C7CF | 2016-12-19 12:53:44.5773152 -08:00 | 0420301123 | 252081104 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 592 | 12.92 | 12.79 | 592 | 12.92 | 12.79 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {0FB9D1F8-1D04-4593-96E9-991FB6DB55D7}
3463 | 2720 | {F9A7A2B9-671D-11E5-80CA-005056A729E5} | KERN | TAFT | Bank 3 | CB 1101 (Non-SCADA) | PGE\BXYD | 2016-10-25 10:39:38.2918038 -07:00 | 2520801101 | 042031124 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {85BACA38-D4ED-44F6-9D79-DAC773015091}
3464 | 2720 | {F9A7A2C8-671D-11E5-80CA-005056A729E5} | KERN | TAFT | Bank 3 | CB 1103 (Non-SCADA) | PGE\BXYD | 2016-10-25 10:41:31.2333725 -07:00 | 2520801103 | 252081106 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {1A849A6E-2107-4941-9164-40354680E834}
3465 | 2721 | {F9A7A2D1-671D-11E5-80CA-005056A729E5} | KERN | TAFT | Bank 4 | CB 1104 (Non-SCADA) | PGE\BXYD | 2016-10-25 10:45:25.3177207 -07:00 | 2520801104 | 252081108 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {70BBB55A-6709-48B8-B821-17F0FB218A95}
3466 | 2637 | {B868F762-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | ALTO | Bank 1 | CB 1124 | PGE\C7CF | 2016-12-19 12:53:59.7556120 -08:00 | 0420301124 | 042031120 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 592 | 12.92 | 12.79 | 592 | 12.92 | 12.79 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {B9DF9219-AB74-40EB-AA0B-E61FCE712E9A}
3467 | 2721 | {F9A7A2D7-671D-11E5-80CA-005056A729E5} | KERN | TAFT | Bank 4 | CB 1106 (Non-SCADA) | PGE\BXYD | 2016-10-25 10:46:47.0971507 -07:00 | 2520801106 | 254071109 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {42D8D959-BEC2-43A6-BF7D-9BAD00D7632D}
3468 | 2721 | {F9A7A2E3-671D-11E5-80CA-005056A729E5} | KERN | TAFT | Bank 4 | CB 1108 (Non-SCADA) | PGE\BXYD | 2016-10-25 10:48:26.3128436 -07:00 | 2520801108 | 042031121 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {686DEE86-523E-4D2D-950A-9C87EA5D0884}
3469 | 2719 | {B868F776-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | ALTO | Bank 3 | CB 1120 | PGE\C7CF | 2016-12-19 12:54:45.8963220 -08:00 | 0420301120 | 254071110 | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 582 | 12.7 | 12.57 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {E58721EB-53E2-4BCC-BF40-E7F224C98157}
3470 | 2722 | {EEFC7527-671D-11E5-80CA-005056A729E5} | KERN | STOCKDALE | Bank 1 | CB 1109 | PGE\BXYD | 2016-10-26 17:02:57.2681318 -07:00 | 2540701109 | 254071111 | 8 | 3 | 3 | 1 | 618 | 13.49 | 13.36 | 618 | 13.49 | 13.36 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {E6557AA8-8894-47A9-873C-182EC87457CF}
3471 | 2719 | {BE68DEEE-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | ALTO | Bank 3 | CB 1121 | PGE\C7CF | 2016-12-19 12:55:00.8433254 -08:00 | 0420301121 | 042031125 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 592 | 12.92 | 12.79 | 592 | 12.92 | 12.79 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {7ED790F1-4C4A-453C-ACC5-B10B0EF81026}
3472 | 2722 | {EEFC753B-671D-11E5-80CA-005056A729E5} | KERN | STOCKDALE | Bank 1 | CB 1110 | PGE\BXYD | 2016-10-26 17:03:14.4916670 -07:00 | 2540701110 | 162701706 | 8 | 3 | 3 | 1 | 618 | 13.49 | 13.36 | 618 | 13.49 | 13.36 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {E0355647-F778-47AC-B670-A0A7B7CE3846}
3473 | 2722 | {EEFC7540-671D-11E5-80CA-005056A729E5} | KERN | STOCKDALE | Bank 1 | CB 1111 | PGE\BXYD | 2016-10-26 17:03:31.2467114 -07:00 | 2540701111 | 162701707 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 639 | 13.95 | 13.81 | 639 | 13.95 | 13.81 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {316D34F8-B825-4247-86B2-22DB341BB61D}
3474 | 2719 | {C4771DF4-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | ALTO | Bank 3 | CB 1125 | PGE\C7CF | 2016-12-19 12:55:20.5022234 -08:00 | 0420301125 | 042461101 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 592 | 12.92 | 12.79 | 592 | 12.92 | 12.79 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 599 | 13.07 | 12.94 | 599 | 13.07 | 12.94 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {7DA8AB96-1728-4629-BCEA-884F5ED2D452}
3476 | 2723 | {4C486E78-671D-11E5-80CA-005056A729E5} | STOCKTON | VIERRA | Bank 2 | CB 1706 | PGE\BXYD | 2017-01-10 17:10:20.3219430 -08:00 | 1627001706 | 042461104 | 10 | 3 | 3 | 1 | 573 | 17.72 | 17.54 | 573 | 17.72 | 17.54 | 689 | 21.3 | 21.09 | 689 | 21.3 | 21.09 | 627 | 19.39 | 19.2 | 627 | 19.39 | 19.2 | 700 | 21.64 | 21.42 | 700 | 21.64 | 21.42 |  |  | FALSE | FALSE | 1455 | 1892 | 1746 | 2183 | {E570A288-40A3-4029-AB96-BE9AAF69966F}
3477 | 2723 | {4C486E83-671D-11E5-80CA-005056A729E5} | STOCKTON | VIERRA | Bank 2 | CB 1707 | PGE\BXYD | 2017-01-10 17:11:18.1054542 -08:00 | 1627001707 | 042461105 | 10 | 3 | 3 | 1 | 578 | 17.87 | 17.69 | 578 | 17.87 | 17.69 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 | 627 | 19.39 | 19.2 | 627 | 19.39 | 19.2 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 |  |  | FALSE | FALSE | 1455 | 1892 | 1746 | 2183 | {181444D5-189D-4649-AE5F-0A650B58F397}
3478 | 2725 | {D530E937-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | BASALT | Bank 1 | CB 1101 | PGE\C7CF | 2016-12-19 13:20:49.1631707 -08:00 | 0424601101 | 042461106 | 8 | 3 | 3 | 1 | 429 | 9.36 | 9.27 | 429 | 9.36 | 9.27 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 429 | 558 | 515 | 644 | {008C47EF-B541-4FBA-BC40-C6FC03C18287}
3479 | 2726 | {DBE57907-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | BASALT | Bank 2 | CB 1104 | PGE\C7CF | 2016-12-19 13:21:31.8970487 -08:00 | 0424601104 | 042261101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {2E072EE4-2985-4DC2-A6B3-E799945C34AB}
3480 | 2726 | {DBE5790C-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | BASALT | Bank 2 | CB 1105 | PGE\C7CF | 2016-12-19 13:21:53.8953362 -08:00 | 0424601105 | 042711101 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {DCEB20CD-6275-4C8B-919A-B1025F5FE3EA}
3481 | 2726 | {DBE57911-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | BASALT | Bank 2 | CB 1106 | PGE\C7CF | 2016-12-19 13:22:14.0056697 -08:00 | 0424601106 | 042711102 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {59A19A3C-BEB1-4295-8C6E-27DDBAD7B17F}
3482 | 2728 | {DBE57925-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | BOLINAS | Bank 1 | CB 1101 | PGE\C7CF | 2016-12-19 13:23:39.6527224 -08:00 | 0422601101 | 043281103 | 8 | 3 | 3 | 2 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {17FB3060-F24A-4BB2-BEFF-0B5C539ACE34}
3483 | 2729 | {E251B606-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | CALISTOGA | Bank 1 | CB 1101 | PGE\C7CF | 2016-12-19 13:24:36.4311561 -08:00 | 0427101101 | 043281104 | 8 | 3 | 3 | 1 | 345 | 7.53 | 7.45 | 345 | 7.53 | 7.45 | 386 | 8.42 | 8.34 | 386 | 8.42 | 8.34 | 443 | 9.67 | 9.57 | 443 | 9.67 | 9.57 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {E207C74B-813F-458A-968E-DA80BBFFF872}
3484 | 2729 | {E8571B84-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | CALISTOGA | Bank 1 | CB 1102 | PGE\C7CF | 2016-12-19 13:25:01.3177299 -08:00 | 0427101102 | 043281105 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {C4EA8079-300F-4482-AB75-9A355CED689D}
3485 | 2730 | {E8571BA1-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | CARQUINEZ | Bank 1 | CB 1103 | PGE\C7CF | 2016-10-25 12:34:53.6212764 -07:00 | 0432801103 | 043091101 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {6CD5FEC4-6F6F-4CDD-B6DF-1B032143B4D5}
3486 | 2730 | {EF304A33-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | CARQUINEZ | Bank 1 | CB 1104 | PGE\C7CF | 2016-12-19 13:28:38.5380073 -08:00 | 0432801104 | 043091102 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {ABF39C80-4BED-4446-A000-40270E30C21A}
3487 | 2731 | {EF304A3E-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | CARQUINEZ | Bank 2 | CB 1105 | PGE\C7CF | 2016-10-25 12:42:54.8069826 -07:00 | 0432801105 | 062701112 | 8 | 3 | 3 | 2 | 572 | 12.48 | 12.36 | 572 | 12.48 | 12.36 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {9FD0CAFE-CEF7-48F7-900B-C4737490CAE0}
3488 | 2732 | {F56AC911-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | GREENBRAE | Bank 1 | CB 1101 | PGE\C7CF | 2016-12-19 13:31:50.7452707 -08:00 | 0430901101 | 254072108 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {819FFD93-1B6A-42AC-AD69-A6753EABCB20}
3489 | 2732 | {F56AC919-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | GREENBRAE | Bank 1 | CB 1102 | PGE\C7CF | 2016-12-19 13:32:21.5880523 -08:00 | 0430901102 | 254072109 | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 582 | 12.7 | 12.57 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {1871A669-7663-4CB9-AC08-51DB3FD6FBE8}
3490 | 2546 | {02750711-2F59-11E6-B38D-D4BED91EFF1A} | SACRAMENTO | CORDELIA | BANK 3 | CB 1112 | PGE\TEJ2 | 2016-10-25 13:41:01.5265746 -07:00 | 0627001112 | 254072110 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 397 Al past switch 40315 |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {06654BFC-9459-4BA4-AEC5-3D4C02CC7353}
3491 | 2727 | {EEFC754B-671D-11E5-80CA-005056A729E5} | KERN | STOCKDALE | Bank 2 | CB 2108 | PGE\BXYD | 2016-11-07 08:45:18.4201164 -08:00 | 2540702108 | 254072111 | 12 | 3 | 3 | 1 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {F36C77F9-A315-48D4-8C69-E0B25CDB36E4}
3492 | 2727 | {EEFC755F-671D-11E5-80CA-005056A729E5} | KERN | STOCKDALE | Bank 2 | CB 2109 | PGE\BXYD | 2016-11-29 08:22:34.9026684 -08:00 | 2540702109 | 043091103 | 12 | 3 | 3 | 1 | 618 | 23.36 | 23.13 | 618 | 23.36 | 23.13 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {A3668B2A-6E1C-4539-87D7-AC4F2227DD46}
3493 | 2727 | {EEFC7573-671D-11E5-80CA-005056A729E5} | KERN | STOCKDALE | Bank 2 | CB 2110 | PGE\BXYD | 2016-11-29 08:23:11.6108797 -08:00 | 2540702110 | 254072112 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {B97240E7-0DB8-4B5C-8C96-CD8A37A3D650}
3494 | 2727 | {EEFC759F-671D-11E5-80CA-005056A729E5} | KERN | STOCKDALE | Bank 2 | CB 2111 | PGE\BXYD | 2016-11-29 08:23:41.6728505 -08:00 | 2540702111 | 254072113 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {7218D517-D57C-4789-97E0-915B257B1086}
3495 | 2733 | {F56AC92A-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | GREENBRAE | Bank 2 | CB 1103 | PGE\C7CF | 2016-12-19 13:33:17.1586119 -08:00 | 0430901103 | 062881103 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {DFBA9BF5-5DAE-41AC-BE0C-0A2392A6491F}
3496 | 2734 | {F9A7A1D3-671D-11E5-80CA-005056A729E5} | KERN | STOCKDALE | Bank 3 | CB 2112 | PGE\BXYD | 2016-11-07 08:47:03.8038072 -08:00 | 2540702112 | 254072114 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {3289D882-1D19-4F00-99DC-B5CAB08B3F73}
3497 | 2734 | {F9A7A1EA-671D-11E5-80CA-005056A729E5} | KERN | STOCKDALE | Bank 3 | CB 2113 | PGE\BXYD | 2016-11-29 08:53:57.9011240 -08:00 | 2540702113 | 254072115 | 12 | 3 | 3 | 1 | 618 | 23.36 | 23.13 | 618 | 23.36 | 23.13 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {75B23B91-A23B-4D64-8607-597483C8C0A9}
3498 | 2573 | {620DC9CB-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | MAXWELL | Bank 2 | CB 1103 | PGE\TEJ2 | 2016-10-25 13:50:16.3846845 -07:00 | 62881103 | 043091104 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {77AD102B-CE59-4A5C-AB0B-BB1F9EFB15FA}
3499 | 2734 | {F9A7A1FB-671D-11E5-80CA-005056A729E5} | KERN | STOCKDALE | Bank 3 | CB 2114 | PGE\BXYD | 2016-11-29 08:26:44.2514085 -08:00 | 2540702114 | 254071105 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {10AE2158-5E9E-4037-97D7-8314F05F9E3F}
3500 | 2734 | {F9A7A21B-671D-11E5-80CA-005056A729E5} | KERN | STOCKDALE | Bank 3 | CB 2115 | PGE\BXYD | 2016-11-29 08:27:52.1790834 -08:00 | 2540702115 | 254071106 | 12 | 3 | 3 | 1 | 612 | 23.13 | 22.9 | 612 | 23.13 | 22.9 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {DEC074A3-D548-4EBE-BAB4-1EA73B9CD2FA}
3501 | 2733 | {F56AC935-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | GREENBRAE | Bank 2 | CB 1104 | PGE\C7CF | 2016-12-19 13:33:54.7253759 -08:00 | 0430901104 | 182440422 | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 582 | 12.7 | 12.57 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {8D27B0F6-E6ED-4FB7-9FC6-297A1E28DDD8}
3502 | 2736 | {F9A7A238-671D-11E5-80CA-005056A729E5} | KERN | STOCKDALE | Bank 5 | CB 1105 | PGE\BXYD | 2016-10-25 14:39:11.2538251 -07:00 | 2540701105 | 254072105 | 8 | 3 | 3 | 1 | 636 | 13.88 | 13.74 | 636 | 13.88 | 13.74 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {1FAD343B-7ADF-4FC7-9ED3-1FA5C7DA1B3F}
3503 | 2736 | {F9A7A24C-671D-11E5-80CA-005056A729E5} | KERN | STOCKDALE | Bank 5 | CB 1106 | PGE\BXYD | 2016-10-25 14:36:59.9117379 -07:00 | 2540701106 | 182440424 | 8 | 3 | 3 | 1 | 573 | 12.51 | 12.38 | 573 | 12.51 | 12.38 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {75390A4A-E4EA-4FE0-81FD-CDB57B03F608}
3504 | 2738 | {611D1F18-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | PACIFIC GROVE | Bank 2 (Non SCADA) | CB 422 (Non-SCADA) | PGE\ACT0 | 2016-11-23 14:22:59.6765490 -08:00 | 182440422 | 254072106 | 4 | 3 | 3 | 2 | 492 | 3.72 | 3.68 | 492 | 3.72 | 3.68 | 554 | 4.19 | 4.15 | 554 | 4.19 | 4.15 | 560 | 4.24 | 4.2 | 560 | 4.24 | 4.2 | 598 | 4.53 | 4.48 | 598 | 4.53 | 4.48 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {CB03BE0A-6B9F-4EA9-AF38-03D33B0FC1B1}
3505 | 2739 | {F9A7A26E-671D-11E5-80CA-005056A729E5} | KERN | STOCKDALE | Bank 6 | CB 2105 | PGE\BXYD | 2016-11-07 08:49:24.4946308 -08:00 | 2540702105 | 254072107 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {4CFCAAAC-5F79-40FB-8D43-AD93C756E20C}
3506 | 2738 | {611D1F1B-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | PACIFIC GROVE | Bank 2 (Non SCADA) | CB 424 (Non-SCADA) | PGE\ACT0 | 2016-10-25 14:51:34.9782155 -07:00 | 182440424 | 083252101 | 4 | 3 | 3 | 2 | 480 | 3.63 | 3.59 | 480 | 3.63 | 3.59 | 518 | 3.92 | 3.88 | 518 | 3.92 | 3.88 | 494 | 3.74 | 3.7 | 494 | 3.74 | 3.7 | 534 | 4.04 | 4 | 534 | 4.04 | 4 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {BE450F51-CD50-4C05-8A9E-24D3BD0B5CDE}
3507 | 2739 | {F9A7A285-671D-11E5-80CA-005056A729E5} | KERN | STOCKDALE | Bank 6 | CB 2106 | PGE\BXYD | 2016-11-29 08:32:45.9807066 -08:00 | 2540702106 | 083252102 | 12 | 3 | 3 | 1 | 618 | 23.36 | 23.13 | 618 | 23.36 | 23.13 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {BF703278-3FAE-4EDD-992C-F33A052540E0}
3508 | 2739 | {F9A7A299-671D-11E5-80CA-005056A729E5} | KERN | STOCKDALE | Bank 6 | CB 2107 | PGE\BXYD | 2016-11-29 08:38:06.9974296 -08:00 | 2540702107 | 063601102 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {4C14E5DE-67C0-44E9-984F-49A52E9E62C7}
3509 | 2741 | {67BC0450-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | PAUL SWEET | Bank 1 | CB 2101 | PGE\ACT0 | 2016-10-25 15:20:56.5741769 -07:00 | 0832502101 | 083252103 | 12 | 3 | 3 | 2 | 582 | 22 | 21.78 | 582 | 22 | 21.78 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | * Missing CB Drop: 2-500 KCMIL Cu |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {4189431C-B67B-4015-B83C-6B74C79DB76A}
3510 | 2741 | {67BC0467-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | PAUL SWEET | Bank 1 | CB 2102 | PGE\ACT0 | 2016-10-25 15:50:53.3827954 -07:00 | 0832502102 | 063601103 | 12 | 3 | 3 | 2 | 564 | 21.32 | 21.11 | 564 | 21.32 | 21.11 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {0F5208A4-F0B3-41A0-A8BD-B309FB7F1B37}
3511 | 2661 | {812C0458-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACAVILLE | Bank 1 | CB 1102 | PGE\TEJ2 | 2016-10-25 15:57:08.7386849 -07:00 | 0636001102 | 083252104 | 8 | 4 | 4 | 2 | 553 | 12.07 | 11.95 | 553 | 12.07 | 11.95 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {33221A7A-F298-4DA6-B3A0-1AB19795B967}
3512 | 2741 | {6E6DD53B-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | PAUL SWEET | Bank 1 | CB 2103 | PGE\ACT0 | 2016-10-25 15:58:52.2484216 -07:00 | 0832502103 | 063601104 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {19975AED-DB3F-43DA-AA7C-04F2D3B4D363}
3513 | 2661 | {812C0461-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACAVILLE | Bank 1 | CB 1103 | PGE\TEJ2 | 2016-10-25 16:05:27.3480775 -07:00 | 0636001103 | 253551101 | 8 | 3 | 3 | 1 | 573 | 12.51 | 12.38 | 573 | 12.51 | 12.38 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note: Tie to Vacaville 1108 not limited to 1000 Al XLP Conc PVC UG cable. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {5A948316-3AF6-481B-AA42-46879DA1A2E4}
3514 | 2742 | {6E6DD552-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | PAUL SWEET | Bank 2 | CB 2104 | PGE\ACT0 | 2016-10-25 16:08:38.1362478 -07:00 | 0832502104 | 253551102 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | *Missing OH Conductor 6-4/0 Cu. |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1773 | {AC8AFA4D-3AE9-4613-98E2-58D177AC2888}
3515 | 2661 | {812C0471-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACAVILLE | Bank 1 | CB 1104 | PGE\TEJ2 | 2016-10-25 16:20:41.1343795 -07:00 | 0636001104 | 253551103 | 8 | 3 | 3 | 1 | 584 | 12.75 | 12.62 | 584 | 12.75 | 12.62 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {07532585-CA34-4574-B40B-288EA0865561}
3516 | 2743 | {EEFC74E1-671D-11E5-80CA-005056A729E5} | KERN | SMYRNA | Bank 1 | CB 1101 (Non-SCADA) | PGE\BXYD | 2016-10-25 16:28:25.0597269 -07:00 | 2535501101 | 253551104 | 8 | 3 | 3 | 1 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {B136BDF9-A2D1-4AEC-96BB-022188C23A41}
3517 | 2743 | {EEFC74E7-671D-11E5-80CA-005056A729E5} | KERN | SMYRNA | Bank 1 | CB 1102 (Non-SCADA) | PGE\BXYD | 2016-10-25 16:32:28.9168702 -07:00 | 2535501102 | 253551105 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {40954348-88CC-4C81-A41D-CAF8646464A5}
3518 | 2743 | {EEFC74ED-671D-11E5-80CA-005056A729E5} | KERN | SMYRNA | Bank 1 | CB 1103 (Non-SCADA) | PGE\BXYD | 2016-10-25 16:33:43.1696017 -07:00 | 2535501103 | 253651101 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {B4183366-15F7-4A19-8502-C218971ED378}
3519 | 2744 | {EEFC74FF-671D-11E5-80CA-005056A729E5} | KERN | SMYRNA | Bank 2 | CB 1104 | PGE\BXYD | 2016-10-25 17:13:11.9645914 -07:00 | 2535501104 | 042651102 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {92B7ED6E-9FBB-4E01-B6B3-969FB4584006}
3520 | 2744 | {EEFC750D-671D-11E5-80CA-005056A729E5} | KERN | SMYRNA | Bank 2 | CB 1105 | PGE\BXYD | 2016-10-25 17:13:20.4988854 -07:00 | 2535501105 | 042651104 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {0AE135D7-DE9D-48A1-B1F1-3833AE09DD49}
3521 | 2746 | {EEFC74A0-671D-11E5-80CA-005056A729E5} | KERN | SHAFTER | Bank 1 | CB 1101 | PGE\BXYD | 2016-10-25 17:12:16.2607242 -07:00 | 2536501101 | 042651106 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1223 | 1590 | 1468 | 1835 | {832A75A1-8BE4-43A0-BFEA-7600B5AC19C2}
3522 | 2737 | {FF749816-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | HIGHWAY | Bank 1 | CB 1102 | PGE\C7CF | 2016-12-19 13:35:31.1179833 -08:00 | 0426501102 | 042651101 | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 582 | 12.7 | 12.57 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {90C6AB6C-3B40-47EA-A9BE-00C5549ABDB6}
3523 | 2737 | {FF74981B-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | HIGHWAY | Bank 1 | CB 1104 | PGE\C7CF | 2016-12-19 13:37:05.8318562 -08:00 | 0426501104 | 042651103 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {70314C53-1111-4886-819E-A6514DA2C314}
3524 | 2737 | {06048940-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | HIGHWAY | Bank 1 | CB 1106 | PGE\C7CF | 2016-10-25 17:55:10.8883051 -07:00 | 0426501106 | 042651105 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {D279DC6F-3095-4D81-88A6-63C681E3AF3C}
3525 | 2740 | {0604894B-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | HIGHWAY | Bank 2 | CB 1101 | PGE\C7CF | 2016-12-19 13:40:05.2033966 -08:00 | 0426501101 | 083252105 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {DEF35237-868D-455E-8FA1-5EC024EA2B13}
3526 | 2740 | {06048950-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | HIGHWAY | Bank 2 | CB 1103 | PGE\C7CF | 2016-10-25 18:07:11.0758520 -07:00 | 0426501103 | 083252106 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B6F7A676-1047-478A-AC94-A42812393179}
3527 | 2740 | {06048955-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | HIGHWAY | Bank 2 | CB 1105 | PGE\C7CF | 2016-10-25 18:14:51.2135524 -07:00 | 0426501105 | 253651102 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {284C96E1-4C68-420C-A3B2-BE7655F4EEE5}
3528 | 2742 | {7543F6AD-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | PAUL SWEET | Bank 2 | CB 2105 | PGE\ACT0 | 2016-10-26 07:56:25.9847406 -07:00 | 0832502105 | 253651103 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1773 | {EA0B319A-9751-42FF-8D00-6683DB73D47A}
3529 | 2742 | {7BCFC95D-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | PAUL SWEET | Bank 2 | CB 2106 | PGE\ACT0 | 2016-10-26 08:00:40.9901448 -07:00 | 0832502106 | 253651104 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1773 | {7E4761F3-ED23-4A90-B861-23DE3EA1558C}
3530 | 2746 | {EEFC74AB-671D-11E5-80CA-005056A729E5} | KERN | SHAFTER | Bank 1 | CB 1102 | PGE\BXYD | 2016-10-26 08:06:44.9383679 -07:00 | 2536501102 | 163801702 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1223 | 1590 | 1468 | 1835 | {274904F6-A4B0-448F-8851-557937AC87DB}
3531 | 2746 | {EEFC74BC-671D-11E5-80CA-005056A729E5} | KERN | SHAFTER | Bank 1 | CB 1103 | PGE\BXYD | 2016-10-26 08:09:30.1809745 -07:00 | 2536501103 | 163801704 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1223 | 1590 | 1468 | 1835 | {A2767D36-02EF-40E0-A3E3-BE303FF84C62}
3532 | 2746 | {EEFC74C7-671D-11E5-80CA-005056A729E5} | KERN | SHAFTER | Bank 1 | CB 1104 | PGE\BXYD | 2016-10-26 08:10:33.9949175 -07:00 | 2536501104 | 182971101 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1223 | 1590 | 1468 | 1835 | {348CED5B-B839-4B41-BEB2-CF439644FA9E}
3533 | 2752 | {464AAF49-671D-11E5-80CA-005056A729E5} | STOCKTON | RIPON | Bank 2 | CB 1702 | PGE\JCD5 | 2017-05-22 12:38:46.7207541 -07:00 | 1638001702 | 253191101 | 10 | 1 | 1 | 1 | 530 | 16.39 | 16.23 | 530 | 16.39 | 16.23 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 |  |  | FALSE | FALSE | 905 | 1177 | 1086 | 1358 | {7B8F8D26-36E1-4ECF-B9BF-B84FD2F3E67C}
3534 | 2752 | {464AAF5A-671D-11E5-80CA-005056A729E5} | STOCKTON | RIPON | Bank 2 | CB 1704 | PGE\JCD5 | 2017-05-22 13:09:11.7998450 -07:00 | 1638001704 | 253191102 | 10 | 3 | 3 | 1 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 667 | 20.62 | 20.41 | 667 | 20.62 | 20.41 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 667 | 20.62 | 20.41 | 667 | 20.62 | 20.41 |  |  | FALSE | FALSE | 905 | 1177 | 1086 | 1358 | {E76D36A1-D5EA-4514-9595-45B34F6E7BB3}
3535 | 2707 | {98AB3EC9-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | PURISIMA | Bank 2 | CB 1101 | PGE\ACT0 | 2016-12-01 07:43:25.1205901 -08:00 | 1829701101 | 253191104 | 8 | 3 | 3 | 2 | 468 | 10.21 | 10.11 | 468 | 10.21 | 10.11 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {729C3318-F286-4B6A-8D1F-A77EE44DB731}
3537 | 2754 | {EEFC742E-671D-11E5-80CA-005056A729E5} | KERN | SAN BERNARD | Bank 1 (Non SCADA) | CB 1101 | PGE\BXYD | 2016-10-26 08:46:13.2641083 -07:00 | 2531901101 | 254761101 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {83C47851-5FB2-4A63-B201-32A389DBD211}
3539 | 2754 | {EEFC7436-671D-11E5-80CA-005056A729E5} | KERN | SAN BERNARD | Bank 1 (Non SCADA) | CB 1102 | PGE\BXYD | 2016-10-26 08:48:29.0812906 -07:00 | 2531901102 | 254761102 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {7145671F-F6A9-4DF1-BC04-F7DD0F577BE9}
3540 | 2754 | {EEFC743B-671D-11E5-80CA-005056A729E5} | KERN | SAN BERNARD | Bank 1 (Non SCADA) | CB 1104 | PGE\BXYD | 2016-10-26 08:51:15.9055942 -07:00 | 2531901104 | 252861102 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {7055FDA0-F563-4EF1-8855-FE8FEB285CD3}
3541 | 2756 | {E8FE8F9F-671D-11E5-80CA-005056A729E5} | KERN | ROSEDALE | Bank 1 | CB 1101 | PGE\BXYD | 2016-10-26 09:10:36.9672718 -07:00 | 2547601101 | 252861106 | 8 | 3 | 3 | 1 | 745 | 16.26 | 16.1 | 745 | 16.26 | 16.1 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {21CB2EA1-2C8B-4A58-8E5A-95CAE1C993F8}
3542 | 2756 | {EEFC7414-671D-11E5-80CA-005056A729E5} | KERN | ROSEDALE | Bank 1 | CB 2102 | PGE\BXYD | 2016-10-26 09:14:46.2073519 -07:00 | 254761102 | 252861101 | 8 | 3 | 3 | 1 | 817 | 17.83 | 17.65 | 817 | 17.83 | 17.65 | 817 | 17.83 | 17.65 | 817 | 17.83 | 17.65 | 817 | 17.83 | 17.65 | 817 | 17.83 | 17.65 | 817 | 17.83 | 17.65 | 817 | 17.83 | 17.65 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {45CAF3A6-9EBB-49CE-A549-9C51AD5029B5}
3543 | 2758 | {E8FE8F7B-671D-11E5-80CA-005056A729E5} | KERN | RIO BRAVO | Bank 2 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\BXYD | 2016-10-26 09:24:38.4157870 -07:00 | 2528601102 | 252861103 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {AB80045A-FC33-4919-BB5A-6383A7D475F9}
3544 | 2758 | {E8FE8F81-671D-11E5-80CA-005056A729E5} | KERN | RIO BRAVO | Bank 2 (Non SCADA) | CB 1106 (Non-SCADA) | PGE\BXYD | 2016-10-26 09:25:56.6465908 -07:00 | 2528601106 | 042481103 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F7C4CDAF-AB4E-4DE3-BA3A-62E25795D611}
3545 | 2759 | {E8FE8F8A-671D-11E5-80CA-005056A729E5} | KERN | RIO BRAVO | Bank 3 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\BXYD | 2016-10-26 09:34:39.2817210 -07:00 | 2528601101 | 042481104 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {8D7BABC4-3455-4A66-9423-19335004C4DE}
3546 | 2759 | {E8FE8F93-671D-11E5-80CA-005056A729E5} | KERN | RIO BRAVO | Bank 3 (Non SCADA) | CB 1103 (Non-SCADA) | PGE\BXYD | 2016-10-26 09:35:59.1503354 -07:00 | 2528601103 | 254572101 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {295A39FA-4662-4B2B-ACEC-1B083ACF19A8}
3547 | 2757 | {0C6D6AD8-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | IGNACIO | Bank 5 (Non SCADA) | CB 1103 | PGE\C7CF | 2016-10-26 09:37:57.7498496 -07:00 | 0424801103 | 254572102 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {B95EE0F7-D102-4395-A7CD-8A21B6A9AD1C}
3548 | 2757 | {0C6D6AE0-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | IGNACIO | Bank 5 (Non SCADA) | CB 1104 | PGE\C7CF | 2016-12-19 13:44:58.7067749 -08:00 | 0424801104 | 254572103 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {FFA4A62E-49A2-47F6-AE52-4475EBE038C7}
3549 | 2761 | {E8FE8F2C-671D-11E5-80CA-005056A729E5} | KERN | RENFRO | Bank 1 | CB 2101 | PGE\BXYD | 2016-11-07 08:40:28.9545149 -08:00 | 2545702101 | 254572105 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1773 | {4D1118B4-029E-4222-8421-D4E1D306E8F2}
3550 | 2761 | {E8FE8F40-671D-11E5-80CA-005056A729E5} | KERN | RENFRO | Bank 1 | CB 2102 | PGE\BXYD | 2016-11-07 08:40:49.3764664 -08:00 | 2545702102 | 254572107 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1773 | {72FD8341-43DB-4B28-A251-47CDD353617D}
3551 | 2761 | {E8FE8F4B-671D-11E5-80CA-005056A729E5} | KERN | RENFRO | Bank 1 | CB 2103 | PGE\BXYD | 2016-11-07 08:41:14.0730077 -08:00 | 2545702103 | 083252107 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1773 | {C8530FCE-E108-494C-BF72-0D9B9B5A5936}
3552 | 2764 | {E8FE8F5C-671D-11E5-80CA-005056A729E5} | KERN | RENFRO | Bank 2 | CB 2105 | PGE\BXYD | 2016-11-07 08:41:41.2497676 -08:00 | 2545702105 | 042991103 | 12 | 3 | 3 | 1 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1773 | {7549EA59-15EA-4D1B-8CEC-976B74E95BCC}
3553 | 2764 | {E8FE8F6A-671D-11E5-80CA-005056A729E5} | KERN | RENFRO | Bank 2 | CB 2107 | PGE\BXYD | 2016-11-07 08:42:02.3103076 -08:00 | 2545702107 | 042991104 | 12 | 3 | 3 | 1 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1773 | {822EE947-863E-4CB0-8CD8-73DAD5435A95}
3554 | 2753 | {84977DB8-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | PAUL SWEET | Bank 3 | CB 2107 | PGE\ACT0 | 2016-10-26 10:03:21.2393594 -07:00 | 0832502107 | 083252108 | 12 | 3 | 3 | 2 | 657 | 24.83 | 24.58 | 657 | 24.83 | 24.58 | 881 | 33.3 | 32.97 | 881 | 33.3 | 32.97 | 737 | 27.85 | 27.57 | 737 | 27.85 | 27.57 | 900 | 34.01 | 33.67 | 900 | 34.01 | 33.67 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {E75A2CF7-AA8D-4CEC-958E-4E1EBC866B95}
3555 | 2760 | {12E05E6E-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | LAS GALLINAS A | Bank 1 | CB 1103 | PGE\C7CF | 2016-10-26 10:05:54.6960417 -07:00 | 0429901103 | 042991105 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {EC46F1D5-DB1D-4FA5-87B5-2C2073B3C9D2}
3556 | 2760 | {12E05E73-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | LAS GALLINAS A | Bank 1 | CB 1104 | PGE\C7CF | 2016-12-19 13:46:31.8118624 -08:00 | 0429901104 | 083252109 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {19EA080C-1733-484F-B102-4AAE2E085531}
3557 | 2753 | {8A9987F1-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | PAUL SWEET | Bank 3 | CB 2108 | PGE\ACT0 | 2016-10-26 10:13:43.1799836 -07:00 | 0832502108 | 042991106 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {0FD92B09-1ED9-4159-9BAB-9FDC1A1F195F}
3559 | 2762 | {12E05E84-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | LAS GALLINAS A | Bank 2 | CB 1105 | PGE\C7CF | 2016-12-19 13:48:42.7514666 -08:00 | 0429901105 | 042991107 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1153 | 1153 | 1153 | 1153 | {21F5FA7C-E4C8-4CFD-8B5F-3D876113F9B4}
3560 | 2753 | {90974C5E-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | PAUL SWEET | Bank 3 | CB 2109 | PGE\ACT0 | 2016-10-26 10:21:53.7637605 -07:00 | 0832502109 | 253642101 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {4851072B-C8D7-40D7-B1BF-30527792E32D}
3561 | 2762 | {196F1724-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | LAS GALLINAS A | Bank 2 | CB 1106 | PGE\C7CF | 2016-12-19 13:48:59.6617180 -08:00 | 0429901106 | 082931101 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1153 | 1153 | 1153 | 1153 | {4B021A42-FACB-4F5A-9D7D-D676CA46E2F6}
3562 | 2763 | {196F172F-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | LAS GALLINAS A | Bank 3 | CB 1107 | PGE\C7CF | 2016-12-19 13:51:17.3911962 -08:00 | 0429901107 | 182961107 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {709D6AA2-BFA1-459F-AABF-28A30DD6DC0B}
3563 | 2766 | {A3C3D642-5FFE-11E6-9BE4-80000BC6CD8D} | KERN | POSO MOUNTAIN | Bank 1 | CB 2101 | PGE\BXYD | 2016-11-07 08:38:33.1704846 -08:00 | 253642101 | 042021105 | 12 | 3 | 3 | 1 | 529 | 19.99 | 19.79 | 529 | 19.99 | 19.79 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 529 | 687 | 635 | 793 | {87616806-0B5C-407A-AB14-17F69D6C41DA}
3564 | 2765 | {90974C81-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | POINT MORETTI | Bank 1 | CB 1101 (Non-SCADA) | PGE\MTDR | 2017-07-11 16:36:58.9996501 -07:00 | 082931101 | 182961110 | 8 | 3 | 3 | 2 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | *Alt 1 MTT of 600A can be used if needed for capacity. |  | FALSE | FALSE | 481 | 481 | 481 | 481 | {00000000-0000-0000-0000-000000000000}
3565 | 2768 | {9DF1DC42-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | PRUNEDALE | Bank 2 | CB 1107 | PGE\ACT0 | 2016-10-26 10:49:18.7472489 -07:00 | 1829601107 | 253422101 | 8 | 3 | 2 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {CF3B28B6-F39F-48AD-BEE1-B611BCB9C0B0}
3566 | 2770 | {1FE69EAE-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | NAPA | Bank 2 (Non SCADA) | CB 1105 | PGE\C7CF | 2016-10-26 10:59:33.0249473 -07:00 | 0420201105 | 253422102 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {7DC6FDEF-F219-45BC-80D1-E899202640FA}
3567 | 2772 | {A3EB5BAF-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | PRUNEDALE | Bank 3 | CB 1110 | PGE\C7CF | 2017-07-03 12:06:04.4435041 -07:00 | 1829601110 | 022590401 | 8 | 3 | 3 | 2 | 468 | 10.21 | 10.11 | 468 | 10.21 | 10.11 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 528 | 11.52 | 11.4 | 528 | 11.52 | 11.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {C689C032-0CDE-46C9-921D-C8CB5CC85D39}
3569 | 2773 | {E8FE8EBB-671D-11E5-80CA-005056A729E5} | KERN | PANAMA | Bank 1 | CB 2101 | PGE\BXYD | 2016-11-29 08:42:12.7482167 -08:00 | 2534202101 | 042021106 | 12 | 3 | 3 | 1 | 618 | 23.36 | 23.13 | 618 | 23.36 | 23.13 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {26311C0B-6BAA-40CD-9806-85383104DFF1}
3570 | 2773 | {E8FE8EDE-671D-11E5-80CA-005056A729E5} | KERN | PANAMA | Bank 1 | CB 2102 | PGE\BXYD | 2016-11-07 08:36:12.4699210 -08:00 | 2534202102 | 182631101 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {0138A375-F466-4999-B69D-9E6FEDED568B}
3571 | 2774 | {9E2F7BF4-3D5A-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | RANDOLPH | BANK 401 (Non SCADA) | CB 401 (Non-SCADA) | PGE\DMAL | 2017-05-12 18:49:30.2647618 -07:00 | 022590401 | 252821103 | 3 | 3 | 3 | 2 | 277 | 2 | 1.98 | 277 | 2 | 1.98 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 277 | 360 | 333 | 416 | {B9A06A1B-4A35-4E63-9E41-5577AFD3FAFA}
3572 | 2770 | {1FE69EB3-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | NAPA | Bank 2 (Non SCADA) | CB 1106 | PGE\C7CF | 2016-12-19 14:01:31.4031612 -08:00 | 0420201106 | 252821104 | 8 | 3 | 3 | 2 | 475 | 10.37 | 10.27 | 475 | 10.37 | 10.27 | 584 | 12.75 | 12.62 | 584 | 12.75 | 12.62 | 489 | 10.67 | 10.56 | 489 | 10.67 | 10.56 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {B531ED92-8395-49FA-9408-0C1FCB7D26FC}
3573 | 2755 | {9EED5EAC-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SAN LUIS OBISPO | Bank 4 | CB 1101 | PGE\A9S5 | 2016-11-11 10:42:53.8883935 -08:00 | 1826301101 | 182631102 | 8 | 3 | 3 | 2 | 454 | 9.91 | 9.81 | 454 | 9.91 | 9.81 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 468 | 10.21 | 10.11 | 468 | 10.21 | 10.11 | 566 | 12.35 | 12.23 | 566 | 12.35 | 12.23 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3071 | {36D51663-D69D-4B36-BE5D-3F7FF460B776}
3574 | 2775 | {E8FE8E80-671D-11E5-80CA-005056A729E5} | KERN | OLD RIVER | Bank 1 | CB 1103 | PGE\BXYD | 2016-10-26 11:45:27.2574671 -07:00 | 2528201103 | 252821101 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1123 | 1123 | 1123 | 1123 | {90C4C257-B65C-4F8C-B005-CC03A4183E60}
3575 | 2775 | {E8FE8E8E-671D-11E5-80CA-005056A729E5} | KERN | OLD RIVER | Bank 1 | CB 1104 | PGE\BXYD | 2016-10-26 11:47:09.0898022 -07:00 | 2528201104 | 182631103 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1123 | 1123 | 1123 | 1123 | {A082EF56-BEA6-4FDD-8F32-BED26A4D3C54}
3576 | 2755 | {9EED5EB7-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SAN LUIS OBISPO | Bank 4 | CB 1102 | PGE\A9S5 | 2016-11-11 10:43:22.7963053 -08:00 | 1826301102 | 252821102 | 8 | 3 | 3 | 2 | 454 | 9.91 | 9.81 | 454 | 9.91 | 9.81 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 468 | 10.21 | 10.11 | 468 | 10.21 | 10.11 | 566 | 12.35 | 12.23 | 566 | 12.35 | 12.23 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3071 | {8CD0FA9D-D37B-4DF7-8384-5E1F950B3254}
3578 | 2777 | {E8FE8E9F-671D-11E5-80CA-005056A729E5} | KERN | OLD RIVER | Bank 2 | CB 1101 | PGE\BXYD | 2016-10-26 11:56:36.8585636 -07:00 | 2528201101 | 042041102 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {33366E55-56C8-4EC0-B9DE-F0CFA5390D56}
3579 | 2755 | {9EED5EC2-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SAN LUIS OBISPO | Bank 4 | CB 1103 | PGE\A9S5 | 2016-11-11 10:41:21.0019141 -08:00 | 1826301103 | 042041103 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3071 | {ADC93D67-8E88-47F6-8C2A-F05FB9D2A016}
3580 | 2777 | {E8FE8EA7-671D-11E5-80CA-005056A729E5} | KERN | OLD RIVER | Bank 2 | CB 1102 | PGE\BXYD | 2016-10-26 12:01:29.2160620 -07:00 | 2528201102 | 042041104 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {0D494026-C25A-4E6E-A321-BB48C418270F}
3581 | 2776 | {262737DD-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | NORTH TOWER | Bank 1 | CB 1102 | PGE\C7CF | 2016-10-26 12:20:40.6623725 -07:00 | 0420401102 | 042041108 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {692CCEC1-69A4-494E-8330-DFCB14232C4D}
3582 | 2776 | {2CD474E3-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | NORTH TOWER | Bank 1 | CB 1103 | PGE\C7CF | 2016-10-26 12:25:51.0017848 -07:00 | 0420401103 | 042211101 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {544A5BCC-55B9-46BE-8055-9780D39E87C5}
3583 | 2776 | {2CD474E6-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | NORTH TOWER | Bank 1 | CB 1104 | PGE\C7CF | 2016-10-26 12:31:00.9058387 -07:00 | 0420401104 | 042211102 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {4ACF88A6-F90C-47C6-97F1-E957C147BC37}
3584 | 2778 | {32CD5768-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | NORTH TOWER | Bank 4 | CB 1108 | PGE\C7CF | 2016-10-26 12:35:29.0906717 -07:00 | 0420401108 | 042211103 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {8D3884D0-1CC1-4FCF-98BF-936C1B810AB7}
3585 | 2780 | {32CD5785-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | NOVATO | Bank 1 | CB 1101 | PGE\C7CF | 2016-10-26 12:51:57.3500696 -07:00 | 0422101101 | 042211104 | 8 | 3 | 3 | 2 | 307 | 6.7 | 6.63 | 307 | 6.7 | 6.63 | 399 | 8.71 | 8.62 | 399 | 8.71 | 8.62 | 368 | 8.03 | 7.95 | 368 | 8.03 | 7.95 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 307 | 399 | 368 | 460 | {6015C431-0B66-4D00-8AAB-55098F2173CC}
3586 | 2780 | {32CD578A-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | NOVATO | Bank 1 | CB 1102 | PGE\C7CF | 2016-12-19 14:37:09.5693744 -08:00 | 0422101102 | 042291101 | 8 | 3 | 3 | 2 | 307 | 6.7 | 6.63 | 307 | 6.7 | 6.63 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 307 | 399 | 368 | 460 | {849CA9C8-E5FA-4CE1-86A3-D9027D1A00B0}
3587 | 2781 | {32CD5795-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | NOVATO | Bank 2 | CB 1103 | PGE\C7CF | 2016-12-19 14:39:23.4237268 -08:00 | 0422101103 | 042051101 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {41DECF73-F6ED-43B0-BC25-6840135BDEED}
3588 | 2781 | {392AEE5D-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | NOVATO | Bank 2 | CB 1104 | PGE\C7CF | 2016-12-19 14:38:41.8311334 -08:00 | 0422101104 | 042051102 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {4E96D533-4C1E-4065-B5FA-0BE066836FFF}
3589 | 2783 | {392AEE74-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | OLEMA | Bank 1 (Non Scada) | CB 1101 | PGE\C7CF | 2016-12-19 14:40:46.8149665 -08:00 | 0422901101 | 042051103 | 8 | 3 | 3 | 2 | 229 | 5 | 4.95 | 229 | 5 | 4.95 | 298 | 6.5 | 6.44 | 298 | 6.5 | 6.44 | 275 | 6 | 5.94 | 275 | 6 | 5.94 | 344 | 7.51 | 7.43 | 344 | 7.51 | 7.43 |  |  | FALSE | FALSE | 229 | 298 | 275 | 344 | {E213466F-06D4-4388-869B-4A613F20B033}
3591 | 2784 | {4528E85B-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | PARKWAY | Bank 1 | CB 1101 | PGE\C7CF | 2016-10-26 13:38:31.6030255 -07:00 | 0420501101 | 043292101 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {AADD45D8-AA2B-423E-8042-CD7E87B22D18}
3592 | 2784 | {4528E860-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | PARKWAY | Bank 1 | CB 1102 | PGE\C7CF | 2016-10-26 13:41:53.2299063 -07:00 | 0420501102 | 252721110 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {D082E3E3-64D1-44F3-A4AB-69A681DA465A}
3593 | 2784 | {4528E877-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | PARKWAY | Bank 1 | CB 1103 | PGE\C7CF | 2016-10-26 13:45:32.6266991 -07:00 | 0420501103 | 043292102 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {68B4C491-17AD-4FF7-908D-91414800EEB9}
3594 | 2787 | {4B3AF806-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | PUEBLO | Bank 1 | CB 2101 | PGE\C7CF | 2016-12-19 14:49:01.5735610 -08:00 | 0432902101 | 252721112 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {C3FBE1F5-A3CC-4723-BDC7-650B7073EA27}
3595 | 2785 | {E3005911-671D-11E5-80CA-005056A729E5} | KERN | KERN OIL | Bank 2 | CB 1110 | PGE\BXYD | 2016-11-29 08:48:29.7654535 -08:00 | 2527201110 | 043292103 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {3BC9CA19-87A3-4428-9867-2A5DF0F26BB7}
3596 | 2787 | {4B3AF81A-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | PUEBLO | Bank 1 | CB 2102 | PGE\C7CF | 2016-12-19 14:49:26.7221666 -08:00 | 0432902102 | 043291102 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {693BF29E-32D8-43A7-8923-7F0802AF1A06}
3597 | 2785 | {2717D552-A5BE-11E5-A1F0-D4BED91EFF1A} | KERN | KERN OIL | Bank 2 | CB 1112 | PGE\BXYD | 2016-11-29 08:48:44.6797227 -08:00 | 2527201112 | 252721114 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {89864714-185E-4291-A440-6E064FF773FF}
3598 | 2787 | {517D6621-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | PUEBLO | Bank 1 | CB 2103 | PGE\C7CF | 2016-12-19 14:50:11.5721304 -08:00 | 0432902103 | 043291103 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {313F8BA3-B387-4C77-9DBD-A803D92CED2E}
3599 | 2788 | {57F22E7C-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | PUEBLO | Bank 2 | CB 1102 | PGE\C7CF | 2016-12-19 14:52:51.4908336 -08:00 | 0432901102 | 043291104 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F6B4A5F9-951B-49B7-8E44-99E360672CE6}
3600 | 2785 | {E300591C-671D-11E5-80CA-005056A729E5} | KERN | KERN OIL | Bank 2 | CB 1114 | PGE\BXYD | 2016-11-29 08:49:00.2491961 -08:00 | 2527201114 | 043291105 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {EC41D2E5-4E3B-4D26-A8B9-E593DEFAC94E}
3601 | 2788 | {57F22E84-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | PUEBLO | Bank 2 | CB 1103 | PGE\C7CF | 2016-12-19 14:53:06.8418240 -08:00 | 0432901103 | 252721104 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B4FD6CE4-F1E9-4760-9AA8-1F38EB1B9D2F}
3602 | 2788 | {5E190498-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | PUEBLO | Bank 2 | CB 1104 | PGE\C7CF | 2016-10-26 14:18:33.4550362 -07:00 | 0432901104 | 252721106 | 8 | 3 | 3 | 1 | 573 | 12.51 | 12.38 | 573 | 12.51 | 12.38 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {72B9B43B-7321-46B4-B9A4-075678A38143}
3603 | 2788 | {643E26EC-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | PUEBLO | Bank 2 | CB 1105 | PGE\C7CF | 2016-12-19 14:53:42.3799372 -08:00 | 0432901105 | 252721108 | 8 | 3 | 3 | 1 | 573 | 12.51 | 12.38 | 573 | 12.51 | 12.38 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {BC44C413-E921-4BA4-87A5-A6E09234DE60}
3612 | 2790 | {E300592F-671D-11E5-80CA-005056A729E5} | KERN | KERN OIL | Bank 3 | CB 1104 | PGE\APE3 | 2016-10-26 14:58:32.2381699 -07:00 | 2527201104 | 022590403 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B4496ED9-6088-4AEC-ADEE-A01DBF681104}
3613 | 2790 | {E300593D-671D-11E5-80CA-005056A729E5} | KERN | KERN OIL | Bank 3 | CB 1106 | PGE\APE3 | 2016-10-26 15:01:54.1715068 -07:00 | 2527201106 | 042011103 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {48409A22-1CFD-45F2-AAC8-90804C9856DA}
3614 | 2790 | {E300594B-671D-11E5-80CA-005056A729E5} | KERN | KERN OIL | Bank 3 | CB 1108 | PGE\APE3 | 2016-10-26 15:05:16.7173523 -07:00 | 2527201108 | 042011104 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {85A1C4C9-AE63-4C27-93F8-0073CA0D972C}
3615 | 2791 | {959A7E77-3D5A-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | RANDOLPH | BANK 403 (Non SCADA) | CB 403 (Non-SCADA) | PGE\DMAL | 2017-05-12 18:55:10.0792092 -07:00 | 022590403 | 042011106 | 3 | 3 | 3 | 2 | 319 | 2.3 | 2.28 | 319 | 2.3 | 2.28 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 383 | 2.76 | 2.73 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 319 | 414 | 383 | 478 | {67356BF4-67AA-4F91-BED7-E496F5D7CB47}
3616 | 2792 | {6A37096C-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | SAN RAFAEL | Bank 1 | CB 1103 | PGE\C7CF | 2016-12-19 14:56:22.1992214 -08:00 | 0420101103 | 042011101 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1370 | 1781 | 1644 | 2055 | {8FAB91FA-FDA0-4EEC-9400-5BC2581C3094}
3617 | 2792 | {6A370977-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | SAN RAFAEL | Bank 1 | CB 1104 | PGE\C7CF | 2016-12-19 14:56:57.0992390 -08:00 | 0420101104 | 042011102 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1370 | 1781 | 1644 | 2055 | {3D1AF3DA-C828-470A-91D1-A721ED46D339}
3618 | 2792 | {6A370985-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | SAN RAFAEL | Bank 1 | CB 1106 | PGE\C7CF | 2016-10-26 15:40:50.2156280 -07:00 | 0420101106 | 014422109 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1370 | 1781 | 1644 | 2055 | {AA982CD8-2E6C-45C9-85AD-948F60918F7D}
3619 | 2793 | {70CBB59D-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | SAN RAFAEL | Bank 2 | CB 1101 | PGE\C7CF | 2016-10-26 15:44:39.2588751 -07:00 | 0420101101 | 014422111 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {53B27CC0-1A60-4254-B5EA-D54D5A3E1F4B}
3620 | 2793 | {778E281D-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | SAN RAFAEL | Bank 2 | CB 1102 | PGE\C7CF | 2016-10-26 16:04:08.5965933 -07:00 | 0420101102 | 014402103 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {115214F2-AA7F-4884-A72A-F41E448AD457}
3621 | 2795 | {B7382B97-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | CAYETANO | Bank 3 | CB 2109 | PGE\RDR1 | 2017-05-19 14:48:02.7821144 -07:00 | 0144202109 | 014402104 | 11 | 3 | 3 | 1 | 636 | 23.79 | 23.55 | 636 | 23.79 | 23.55 | 792 | 29.63 | 29.33 | 792 | 29.63 | 29.33 | 691 | 25.85 | 25.59 | 691 | 25.85 | 25.59 | 800 | 29.93 | 29.63 | 800 | 29.93 | 29.63 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {04C5EAF8-59E3-434A-A5EE-DE1E5842F2BA}
3622 | 2795 | {B7382BB5-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | CAYETANO | Bank 3 | CB 2111 | PGE\RDR1 | 2017-05-20 17:19:12.4552797 -07:00 | 0144202111 | 042011107 | 11 | 3 | 3 | 1 | 636 | 23.79 | 23.55 | 636 | 23.79 | 23.55 | 792 | 29.63 | 29.33 | 792 | 29.63 | 29.33 | 691 | 25.85 | 25.59 | 691 | 25.85 | 25.59 | 800 | 29.93 | 29.63 | 800 | 29.93 | 29.63 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {B82B1E05-7494-4204-9EA0-CBD193B3F209}
3623 | 2796 | {C3D95A0A-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | LAS POSITAS | Bank 1 | CB 2103 | PGE\E2Ma | 2016-10-26 16:33:01.0512512 -07:00 | 0144002103 | 042011108 | 11 | 3 | 3 | 1 | 530 | 19.83 | 19.63 | 530 | 19.83 | 19.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {192B6DE6-6B23-4EAA-911B-1B6B6590673C}
3625 | 2796 | {C3D95A22-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | LAS POSITAS | Bank 1 | CB 2104 | PGE\E2Ma | 2016-10-26 16:39:20.5492490 -07:00 | 0144002104 | 014402105 | 11 | 3 | 3 | 1 | 530 | 19.83 | 19.63 | 530 | 19.83 | 19.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {039CE43B-DAE4-4153-8611-AA5A797F4FB3}
3626 | 2793 | {778E2825-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | SAN RAFAEL | Bank 2 | CB 1107 | PGE\C7CF | 2016-12-19 14:58:40.0160654 -08:00 | 0420101107 | 014402106 | 8 | 3 | 3 | 2 | 524 | 11.44 | 11.33 | 524 | 11.44 | 11.33 | 591 | 12.9 | 12.77 | 591 | 12.9 | 12.77 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {E26D5245-8FC9-489F-A635-3D61E20ED675}
3627 | 2793 | {778E2830-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | SAN RAFAEL | Bank 2 | CB 1108 | PGE\C7CF | 2016-12-19 14:59:02.7426262 -08:00 | 0420101108 | 042011105 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {BCB2D865-28A8-4D00-8B8B-415DF50E1E09}
3628 | 2797 | {C3D95A54-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | LAS POSITAS | Bank 2 | CB 2105 | PGE\E2Ma | 2016-10-26 16:51:26.6314332 -07:00 | 0144002105 | 014402107 | 11 | 3 | 3 | 1 | 151 | 5.65 | 5.59 | 151 | 5.65 | 5.59 | 166 | 6.21 | 6.15 | 166 | 6.21 | 6.15 | 156 | 5.84 | 5.78 | 156 | 5.84 | 5.78 | 171 | 6.4 | 6.34 | 171 | 6.4 | 6.34 |  |  | FALSE | FALSE | 2004 | 2606 | 2405 | 3007 | {DB2CCD5C-7145-43C1-AA16-8ABAD34607B9}
3629 | 2797 | {C3D95A5D-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | LAS POSITAS | Bank 2 | CB 2106 | PGE\E2Ma | 2016-10-26 16:51:01.7301814 -07:00 | 0144002106 | 014402108 | 11 | 3 | 3 | 1 | 573 | 21.44 | 21.23 | 573 | 21.44 | 21.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 2004 | 2606 | 2405 | 3007 | {730E76C4-6A2B-45F5-87A4-674442AE1ED8}
3630 | 2794 | {84E98C7D-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | SAN RAFAEL | Bank 3 | CB 1105 | PGE\C7CF | 2016-10-26 16:52:07.1334464 -07:00 | 0420101105 | 014402109 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {256DF8B2-9599-4486-9DE1-3A90705E7848}
3631 | 2797 | {C3D95A89-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | LAS POSITAS | Bank 2 | CB 2107 | PGE\E2Ma | 2016-10-26 16:55:48.8223128 -07:00 | 0144002107 | 014402110 | 11 | 3 | 3 | 1 | 578 | 21.62 | 21.4 | 578 | 21.62 | 21.4 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 2004 | 2606 | 2405 | 3007 | {7D7555F5-D267-4F64-8226-0E6A6FE13906}
3632 | 2797 | {C3D95AB5-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | LAS POSITAS | Bank 2 | CB 2108 | PGE\E2Ma | 2016-10-26 16:58:09.9953649 -07:00 | 0144002108 | 042011109 | 11 | 3 | 3 | 1 | 573 | 21.44 | 21.23 | 573 | 21.44 | 21.23 | 667 | 24.95 | 24.7 | 667 | 24.95 | 24.7 | 627 | 23.46 | 23.23 | 627 | 23.46 | 23.23 | 667 | 24.95 | 24.7 | 667 | 24.95 | 24.7 |  |  | FALSE | FALSE | 2004 | 2606 | 2405 | 3007 | {D24D6855-00FE-4A40-AFE9-A8E01EE01518}
3633 | 2798 | {C3D95ADD-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | LAS POSITAS | Bank 3 | CB 2109 | PGE\E2Ma | 2016-10-26 17:02:25.5508922 -07:00 | 0144002109 | 042011110 | 11 | 3 | 3 | 1 | 530 | 19.83 | 19.63 | 530 | 19.83 | 19.63 | 667 | 24.95 | 24.7 | 667 | 24.95 | 24.7 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 667 | 24.95 | 24.7 | 667 | 24.95 | 24.7 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {FEDD32CF-7FEE-4BAB-BEC4-EC21C5F811C9}
3634 | 2798 | {C3D95B13-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | LAS POSITAS | Bank 3 | CB 2110 | PGE\E2Ma | 2016-10-26 17:06:43.2661894 -07:00 | 0144002110 | 012141101 | 11 | 3 | 3 | 1 | 578 | 21.62 | 21.4 | 578 | 21.62 | 21.4 | 667 | 24.95 | 24.7 | 667 | 24.95 | 24.7 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 667 | 24.95 | 24.7 | 667 | 24.95 | 24.7 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {B834A3EB-A0CC-4F27-A654-CC396E32B0F1}
3635 | 2794 | {8B20FE1B-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | SAN RAFAEL | Bank 3 | CB 1109 | PGE\C7CF | 2016-10-26 17:16:40.9928116 -07:00 | 0420101109 | 012141103 | 8 | 3 | 3 | 2 | 384 | 8.38 | 8.3 | 384 | 8.38 | 8.3 | 472 | 10.3 | 10.2 | 472 | 10.3 | 10.2 | 396 | 8.64 | 8.55 | 396 | 8.64 | 8.55 | 479 | 10.45 | 10.35 | 479 | 10.45 | 10.35 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {71F3337C-1E97-4331-A5C1-5929AE1C9283}
3636 | 2794 | {8B20FE23-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | SAN RAFAEL | Bank 3 | CB 1110 | PGE\C7CF | 2016-10-26 17:20:10.8689409 -07:00 | 0420101110 | 012141102 | 8 | 3 | 3 | 2 | 258 | 5.63 | 5.57 | 258 | 5.63 | 5.57 | 286 | 6.24 | 6.18 | 286 | 6.24 | 6.18 | 266 | 5.81 | 5.75 | 266 | 5.81 | 5.75 | 295 | 6.44 | 6.38 | 295 | 6.44 | 6.38 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {17C512BB-36FF-4F90-939B-2596BA433678}
3637 | 2799 | {C3D95B30-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | LIVERMORE | Bank 1 | CB 1101 | PGE\E2Ma | 2016-10-27 13:32:03.3413602 -07:00 | 0121401101 | 014452103 | 8 | 3 | 3 | 1 | 477 | 10.41 | 10.31 | 453 | 9.89 | 9.79 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 528 | 11.52 | 11.4 | 501 | 10.93 | 10.82 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | TRUE | FALSE | 577 | 750 | 692 | 866 | {CC678B9C-A9F7-4B54-974A-0A012FD5C2BD}
3638 | 2799 | {C3D95B40-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | LIVERMORE | Bank 1 | CB 1103 | PGE\E2Ma | 2016-10-27 13:32:18.0592642 -07:00 | 0121401103 | 014452104 | 8 | 3 | 3 | 1 | 151 | 3.3 | 3.27 | 143 | 3.12 | 3.09 | 166 | 3.62 | 3.58 | 157 | 3.43 | 3.4 | 156 | 3.4 | 3.37 | 148 | 3.23 | 3.2 | 171 | 3.73 | 3.69 | 162 | 3.54 | 3.5 |  |  | TRUE | FALSE | 577 | 750 | 692 | 866 | {B46B08A5-681F-4606-85AF-B7E9F155997D}
3639 | 2804 | {C3D95B5A-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | LIVERMORE | Bank 2 | CB 1102 | PGE\E2Ma | 2016-10-27 13:32:27.5752610 -07:00 | 0121401102 | 012141104 | 8 | 3 | 3 | 1 | 440 | 9.6 | 9.5 | 418 | 9.12 | 9.03 | 566 | 12.35 | 12.23 | 537 | 11.72 | 11.6 | 525 | 11.46 | 11.35 | 498 | 10.87 | 10.76 | 583 | 12.72 | 12.59 | 553 | 12.07 | 11.95 | metal riser isn't correct, picked the closest |  | TRUE | FALSE | 577 | 750 | 692 | 866 | {3B0A6D42-FB91-4C6F-A2F5-45410D8C1BD7}
3640 | 2800 | {ECBA774D-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | KIRKER | Bank 1 | CB 2103 | PGE\WCL5 | 2016-11-09 17:21:24.9579998 -08:00 | 0144502103 | 042490401 | 22 | 3 | 3 | 1 | 940 | 33.83 | 33.49 | 940 | 33.83 | 33.49 | 1000 | 35.99 | 35.63 | 1000 | 35.99 | 35.63 | 1000 | 35.99 | 35.63 | 1000 | 35.99 | 35.63 | 1000 | 35.99 | 35.63 | 1000 | 35.99 | 35.63 | The capabilities in the Capability Report shown above are for the entire circuit including the split (east and west). This circuit splits out of the station east and west. The limitation of the east side is 1100Al UG Cable @ 75 % LF (1W), Summer Normal=661A, Summer Emg=792A, Winter Normal=717A, Winter Emg= 842A. The limitation of the west side is Interrupter 17411 Phase MTT (600A), 600A*0.833=500A, Summer Normal=500A, Summer Emg=500A, Winter Normal=500A, Winter Emg=500A. |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {2494F303-249E-45FE-8D87-E1B1AD7DFC9D}
3642 | 2800 | {ECBA7755-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | KIRKER | Bank 1 | CB 2104 | PGE\WCL5 | 2016-11-09 17:21:11.8069469 -08:00 | 0144502104 | 042490402 | 22 | 3 | 3 | 1 | 578 | 20.8 | 20.59 | 578 | 20.8 | 20.59 | 689 | 24.8 | 24.55 | 689 | 24.8 | 24.55 | 627 | 22.57 | 22.34 | 627 | 22.57 | 22.34 | 700 | 25.19 | 24.94 | 700 | 25.19 | 24.94 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {161F4631-8D30-4164-AFDD-F06AD5792A27}
3644 | 2804 | {C3D95B63-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | LIVERMORE | Bank 2 | CB 1104 | PGE\E2Ma | 2016-10-27 13:32:36.3127170 -07:00 | 0121401104 | 042491101 | 8 | 3 | 3 | 1 | 430 | 9.38 | 9.29 | 408 | 8.9 | 8.81 | 430 | 9.38 | 9.29 | 408 | 8.9 | 8.81 | 430 | 9.38 | 9.29 | 408 | 8.9 | 8.81 | 430 | 9.38 | 9.29 | 408 | 8.9 | 8.81 | circuit splits to 2 major load areas at SW 884, original capability sheet designated a load limit on each section. refer to original for more details. |  | TRUE | FALSE | 577 | 750 | 692 | 866 | {303A014C-19EC-47EE-9551-52A53B07B63F}
4615 | 3792 | {8B20FE31-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | SAUSALITO | Bank 1 | CB 401 | PGE\C7CF | 2017-05-30 13:58:34.9156403 -07:00 | 042490401 | 042491102 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 285 | 2.16 | 2.14 | 333 | 2.52 | 2.49 | 333 | 2.52 | 2.49 | 333 | 2.52 | 2.49 | 333 | 2.52 | 2.49 | 333 | 2.52 | 2.49 | 333 | 2.52 | 2.49 | 3-1p Reglator 72kVA |  | FALSE | FALSE | 594 | 772 | 713 | 891 | {22A1D1D3-81ED-45C5-A198-366815AABF2D}
4616 | 3792 | {8B20FE36-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | SAUSALITO | Bank 1 | CB 402 | PGE\C7CF | 2017-05-30 13:58:12.5601238 -07:00 | 042490402 | 043432102 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 285 | 2.16 | 2.14 | 390 | 2.95 | 2.92 | 370 | 2.8 | 2.77 | 360 | 2.72 | 2.69 | 342 | 2.59 | 2.56 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 |  |  | FALSE | FALSE | 594 | 772 | 713 | 891 | {2E80C202-C15C-4784-B8BD-54F9B76E70EA}
4617 | 3793 | {8B20FE41-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | SAUSALITO | Bank 2 | CB 1101 | PGE\C7CF | 2016-12-19 15:10:54.0273047 -08:00 | 0424901101 | 043432103 | 8 | 3 | 3 | 2 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {135351D6-7B02-47B6-897C-6332DE2AD02F}
4618 | 3793 | {8B20FE4C-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | SAUSALITO | Bank 2 | CB 1102 | PGE\C7CF | 2016-12-19 15:11:21.7836185 -08:00 | 0424901102 | 043432104 | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 582 | 12.7 | 12.57 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {707B17A4-9446-4B06-A625-68B909EEEBFD}
4619 | 3795 | {911FFB2C-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | SILVERADO | Bank 1 | CB 2102 | PGE\C7CF | 2016-12-19 15:15:07.9495234 -08:00 | 0434302102 | 043432105 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {568EB709-AE59-40FA-9128-05E5A637B66A}
4620 | 3795 | {972E3A38-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | SILVERADO | Bank 1 | CB 2103 | PGE\C7CF | 2016-10-27 08:52:23.1299313 -07:00 | 0434302103 | 254691101 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {DC5F6CBC-DBAD-4136-81F6-8C28E80D9E31}
4622 | 3796 | {A0456D8E-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | SILVERADO | Bank 2 | CB 2104 | PGE\C7CF | 2016-12-19 15:17:30.6125740 -08:00 | 0434302104 | 254691102 | 12 | 3 | 3 | 1 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {34A8F2BB-B413-4836-91FB-28962CBF6D7C}
4623 | 3796 | {A0456DA5-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | SILVERADO | Bank 2 | CB 2105 | PGE\C7CF | 2016-10-27 08:51:52.9845640 -07:00 | 0434302105 | 252611101 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {FB5DCEE0-3A92-43E2-8000-5BBE405BA2AD}
4624 | 2380 | {E8FE8E6E-671D-11E5-80CA-005056A729E5} | KERN | NORCO | Bank 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\BXYD | 2016-10-27 09:00:35.9851381 -07:00 | 2546901101 | 252611103 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {E322A105-BACE-4AF5-B30B-C63975CAAF04}
4625 | 2380 | {E8FE8E77-671D-11E5-80CA-005056A729E5} | KERN | NORCO | Bank 1 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\BXYD | 2016-10-27 09:02:03.2111281 -07:00 | 2546901102 | 043201101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {7DE053C4-5148-4296-8EC0-D53F371EC75D}
4626 | 3798 | {E8FE8E4A-671D-11E5-80CA-005056A729E5} | KERN | MIDWAY | Bank 7 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\BXYD | 2016-10-27 09:16:52.0812638 -07:00 | 2526101101 | 043201102 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {11862262-CCE0-4968-A04B-88F76C4B60D2}
4627 | 3798 | {E8FE8E50-671D-11E5-80CA-005056A729E5} | KERN | MIDWAY | Bank 7 (Non SCADA) | CB 1103 (Non-SCADA) | PGE\BXYD | 2016-10-27 09:17:54.1627955 -07:00 | 2526101103 | 252611102 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {9CA7207E-DBE4-4388-AA1B-D4FEF3A26C11}
4628 | 3799 | {A659C73A-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | STAFFORD | Bank 1 | CB 1101 | PGE\C7CF | 2016-12-19 15:22:05.8931113 -08:00 | 0432001101 | 252611104 | 8 | 3 | 3 | 2 | 572 | 12.48 | 12.36 | 572 | 12.48 | 12.36 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {03EF5D9C-1678-4DEA-8637-E3A66D6C892D}
4629 | 3800 | {A659C74E-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | STAFFORD | Bank 2 | CB 1102 | PGE\C7CF | 2016-12-19 15:22:20.8543744 -08:00 | 0432001102 | 042301101 | 8 | 3 | 3 | 2 | 572 | 12.48 | 12.36 | 572 | 12.48 | 12.36 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {963B6837-8833-4A84-8197-67412D9AF868}
4630 | 3801 | {E8FE8E59-671D-11E5-80CA-005056A729E5} | KERN | MIDWAY | Bank 8 (Non Scada) | CB 1102 (Non-SCADA) | PGE\BXYD | 2016-10-27 09:30:16.3520593 -07:00 | 2526101102 | 013151101 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {3BB4392F-85C3-40D3-AF0C-67F79C9385F1}
4631 | 3801 | {E8FE8E62-671D-11E5-80CA-005056A729E5} | KERN | MIDWAY | Bank 8 (Non Scada) | CB 1104 (Non-SCADA) | PGE\BXYD | 2016-10-27 09:31:34.9452754 -07:00 | 2526101104 | 013151102 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {50DC9025-7E09-4CED-B922-8B8631EF845D}
4632 | 3803 | {AC6A2947-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | TULUCAY | Bank 2 (Non SCADA) | CB 1101 | PGE\C7CF | 2016-12-19 15:24:46.4420863 -08:00 | 0423001101 | 013151105 | 8 | 3 | 3 | 1 | 745 | 16.26 | 16.1 | 745 | 16.26 | 16.1 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {4D3D3866-3A1B-4C6F-95C8-032CB32FB44F}
4633 | 3804 | {C9E29CA6-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | RADUM | Bank 1 | CB 1101 | PGE\E2Ma | 2016-10-27 13:29:57.0289989 -07:00 | 0131501101 | 014241101 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 477 | 10.41 | 10.31 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 529 | 11.54 | 11.42 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | TRUE | FALSE | 577 | 750 | 692 | 866 | {238ACF48-2E1E-45B6-8A31-5E2ED08C7503}
4634 | 3804 | {C9E29CAF-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | RADUM | Bank 1 | CB 1102 | PGE\E2Ma | 2016-10-27 13:29:46.1707029 -07:00 | 0131501102 | 013751102 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 477 | 10.41 | 10.31 | 639 | 13.95 | 13.81 | 607 | 13.25 | 13.12 | 557 | 12.16 | 12.04 | 529 | 11.54 | 11.42 | 674 | 14.71 | 14.56 | 640 | 13.97 | 13.83 |  |  | TRUE | FALSE | 577 | 750 | 692 | 866 | {8E39B800-4690-4297-9E80-E518C14E41D3}
4635 | 3805 | {C9E29CC2-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | RADUM | Bank 2 | CB 1105 | PGE\E2Ma | 2016-10-27 13:29:38.5886169 -07:00 | 0131501105 | 013751101 | 8 | 3 | 3 | 1 | 566 | 12.35 | 12.23 | 537 | 11.72 | 11.6 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | TRUE | FALSE | 577 | 750 | 692 | 866 | {BE5F33DE-1FA9-40A2-BDE9-C9283F39D9B5}
4636 | 3806 | {D5F1743D-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SUNOL | Bank 1 | CB 1101 | PGE\E2Ma | 2016-10-27 13:51:05.3438313 -07:00 | 0142401101 | 013751103 | 8 | 3 | 3 | 1 | 572 | 12.48 | 12.36 | 572 | 12.48 | 12.36 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {2239A795-0012-4A7C-AC20-A45C6695C1F1}
4637 | 3807 | {D5F17480-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | VASCO | Bank 1 | CB 1102 | PGE\E2Ma | 2016-10-27 14:03:49.2434872 -07:00 | 0137501102 | 082021101 | 8 | 3 | 3 | 1 | 384 | 8.38 | 8.3 | 364 | 7.94 | 7.86 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 461 | 10.06 | 9.96 | 437 | 9.54 | 9.44 | 577 | 12.59 | 12.46 | 548 | 11.96 | 11.84 |  |  | TRUE | FALSE | 384 | 500 | 461 | 577 | {6E63D9B7-BF66-4F77-B913-73583C52BAA5}
4638 | 3808 | {D5F174A8-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | VASCO | Bank 2 | CB 1101 | PGE\E2Ma | 2016-10-27 14:13:16.0674630 -07:00 | 0137501101 | 162471101 | 8 | 3 | 3 | 1 | 429 | 9.36 | 9.27 | 407 | 8.88 | 8.79 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 |  |  | TRUE | FALSE | 429 | 558 | 515 | 644 | {273E8AAF-B0A6-4CD6-A673-8EFAF5E42CDE}
4639 | 3808 | {D5F174C2-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | VASCO | Bank 2 | CB 1103 | PGE\E2Ma | 2016-10-27 14:19:59.1876091 -07:00 | 0137501103 | 162471102 | 8 | 3 | 3 | 1 | 429 | 9.36 | 9.27 | 407 | 8.88 | 8.79 | 558 | 12.18 | 12.06 | 530 | 11.57 | 11.45 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | TRUE | FALSE | 429 | 558 | 515 | 644 | {5FEC5DE5-ED2F-44D3-B744-1235B0E1FAD8}
4640 | 2747 | {AB26687C-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LOS GATOS | Bank 2 | CB 1101 | PGE\MSJ9 | 2016-11-15 13:09:10.8325275 -08:00 | 0820201101 | 083260401 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 722 | 722 | 722 | 722 | {42FC8484-5C3B-4819-8306-9239107DC7D7}
4641 | 3809 | {2FE3CADD-671D-11E5-80CA-005056A729E5} | STOCKTON | BANTA | Bank 1 | CB 1101 | PGE\DET3 | 2016-10-27 15:32:58.0715844 -07:00 | 1624701101 | 083260402 | 8 | 3 | 3 | 1 | 343 | 7.49 | 7.42 | 343 | 7.49 | 7.42 | 446 | 9.73 | 9.63 | 446 | 9.73 | 9.63 | 412 | 8.99 | 8.9 | 412 | 8.99 | 8.9 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 |  |  | FALSE | FALSE | 343 | 446 | 412 | 515 | {7BF95CE4-238E-4203-B6D6-E8D9BD676EBC}
4642 | 3809 | {2FE3CAE5-671D-11E5-80CA-005056A729E5} | STOCKTON | BANTA | Bank 1 | CB 1102 | PGE\DET3 | 2016-10-27 15:32:40.2999952 -07:00 | 1624701102 | 022680401 | 8 | 3 | 3 | 1 | 343 | 7.49 | 7.42 | 343 | 7.49 | 7.42 | 446 | 9.73 | 9.63 | 446 | 9.73 | 9.63 | 412 | 8.99 | 8.9 | 412 | 8.99 | 8.9 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 |  |  | FALSE | FALSE | 343 | 446 | 412 | 515 | {DD63B180-465E-4DE3-B414-9CD796395327}
4646 | 3810 | {AA29C2FE-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | RIO DEL MAR | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\ACT0 | 2016-10-27 15:11:23.6078238 -07:00 | 083260401 | 162471103 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 455 | 3.44 | 3.41 | 455 | 3.44 | 3.41 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {BE2DBE3C-1ED4-4449-B125-D25A80DEEBB8}
4647 | 3812 | {AA29C304-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | RIO DEL MAR | Bank 2 (Non SCADA) | CB 402 (Non-SCADA) | PGE\ACT0 | 2016-10-27 15:18:05.9792924 -07:00 | 083260402 | 082021102 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 455 | 3.44 | 3.41 | 455 | 3.44 | 3.41 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {0658C3A8-8A0D-481A-80EE-BF76D9DB8B2A}
4648 | 4753 | {C15E84B9-3D5A-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | PLYMOUTH | BANK 401 (Non SCADA) | CB 401 (Non-SCADA) | PGE\DMAL | 2017-05-12 21:15:10.5257354 -07:00 | 022680401 | 083692104 | 3 | 3 | 3 | 2 | 319 | 2.3 | 2.28 | 319 | 2.3 | 2.28 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 383 | 2.76 | 2.73 | 383 | 2.76 | 2.73 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 319 | 414 | 383 | 478 | {70044DD3-531E-4AAC-AD24-ED3974058DF9}
4649 | 3809 | {2FE3CAEA-671D-11E5-80CA-005056A729E5} | STOCKTON | BANTA | Bank 1 | CB 1103 | PGE\DET3 | 2016-10-27 15:33:31.6011137 -07:00 | 1624701103 | 163741102 | 8 | 3 | 3 | 1 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 |  |  | FALSE | FALSE | 343 | 446 | 412 | 515 | {CD767225-6346-4F27-A6F9-59CD12C05D19}
4650 | 2747 | {AB26689A-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LOS GATOS | Bank 2 | CB 1102 | PGE\MSJ9 | 2016-11-15 16:05:14.2972462 -08:00 | 0820201102 | 163741103 | 8 | 3 | 3 | 2 | 492 | 10.74 | 10.63 | 492 | 10.74 | 10.63 | 554 | 12.09 | 11.97 | 554 | 12.09 | 11.97 | 560 | 12.22 | 12.1 | 560 | 12.22 | 12.1 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 | Previous Capability Sheet used 1/0 Cu way load to get capability of 455A |  | FALSE | FALSE | 722 | 722 | 722 | 722 | {15472822-DE28-4D73-88EC-578F97C9CBDA}
4654 | 3813 | {AA29C30D-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | ROB ROY | Bank 1 | CB 2104 | PGE\ACT0 | 2016-10-31 08:41:37.3675450 -07:00 | 0836902104 | 163220401 | 12 | 3 | 3 | 2 | 541 | 20.45 | 20.25 | 541 | 20.45 | 20.25 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 595 | 773 | 714 | 893 | {B780AC5B-8A3F-47C6-80B7-8DB1FA3C54E9}
4655 | 3815 | {36979821-671D-11E5-80CA-005056A729E5} | STOCKTON | HERDLYN | Bank 1 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\BXYD | 2017-01-25 17:17:53.4272237 -08:00 | 1637401102 | 163220402 | 8 | 3 | 3 | 1 | 330 | 7.2 | 7.13 | 330 | 7.2 | 7.13 | 330 | 7.2 | 7.13 | 330 | 7.2 | 7.13 | 330 | 7.2 | 7.13 | 330 | 7.2 | 7.13 | 330 | 7.2 | 7.13 | 330 | 7.2 | 7.13 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {99E7AC41-6713-45ED-9A6F-B843F42A80F9}
4657 | 3815 | {36979824-671D-11E5-80CA-005056A729E5} | STOCKTON | HERDLYN | Bank 1 (Non SCADA) | CB 1103 (Non-SCADA) | PGE\BXYD | 2017-01-12 11:56:18.7944657 -08:00 | 1637401103 | 163081102 | 8 | 3 | 3 | 1 | 183 | 3.99 | 3.95 | 173 | 3.78 | 3.74 | 211 | 4.6 | 4.55 | 200 | 4.36 | 4.32 | 266 | 5.81 | 5.75 | 252 | 5.5 | 5.45 | 284 | 6.2 | 6.14 | 269 | 5.87 | 5.81 |  |  | FALSE | FALSE | 343 | 446 | 412 | 515 | {098AB999-2E46-4E94-A4B4-404F2853D41C}
4660 | 3818 | {464AB076-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON ACRES | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\DET3 | 2016-10-27 17:51:55.9530831 -07:00 | 163220401 | 013111102 | 3 | 3 | 3 | 1 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 520 | 676 | 624 | 780 | {62081F46-266E-46DC-8211-E496DF9B4BF1}
4662 | 3818 | {464AB079-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON ACRES | Bank 1 (Non SCADA) | CB 402 (Non-SCADA) | PGE\DET3 | 2016-10-27 17:56:12.9088123 -07:00 | 163220402 | 013111103 | 3 | 3 | 3 | 1 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 520 | 676 | 624 | 780 | {A78CA728-5D4F-45A5-96D2-2B189720EC5D}
4664 | 3821 | {464AAF6E-671D-11E5-80CA-005056A729E5} | STOCKTON | ROUGH AND READY ISLA | Bank 1 | CB 1102 | PGE\SZC1 | 2016-10-28 10:06:33.1822452 -07:00 | 1630801102 | 013111104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 626 | 626 | 626 | 626 | {0D2F70FA-0FED-49D9-96CA-78AAB20759CB}
4666 | 2410 | {C9E29CEF-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN LEANDRO | Bank 1 | CB 1102 | PGE\RDR1 | 2017-05-11 10:40:29.9549506 -07:00 | 0131101102 | 162370406 | 7 | 3 | 3 | 2 | 492 | 10.63 | 10.52 | 492 | 10.63 | 10.52 | 554 | 11.97 | 11.85 | 554 | 11.97 | 11.85 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 598 | 12.92 | 12.79 | 598 | 12.92 | 12.79 | The UG cable & riser from the inside of the substation will be replaced with 1100Al EPR cable in 2016/2017 under PM# 30866455 |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {71EC68C7-53DA-4E16-B853-D9A9840F103C}
4668 | 2410 | {CFDD35A9-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN LEANDRO | Bank 1 | CB 1103 | PGE\RDR1 | 2017-05-11 07:52:42.2701450 -07:00 | 0131101103 | 162370407 | 7 | 3 | 3 | 2 | 446 | 9.63 | 9.53 | 446 | 9.63 | 9.53 | 549 | 11.86 | 11.74 | 549 | 11.86 | 11.74 | 459 | 9.91 | 9.81 | 459 | 9.91 | 9.81 | 556 | 12.01 | 11.89 | 556 | 12.01 | 11.89 | Missing Metal Riser for 750Cu P&L. U1103 & U1113 will swap customers in 2017/2018 under capacity project 30866455 & 30866456 |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {32C0AF4D-1E99-4997-A028-A292253CE0B8}
4669 | 2410 | {CFDD35B9-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN LEANDRO | Bank 1 | CB 1104 | PGE\RDR1 | 2017-05-11 08:11:20.9520577 -07:00 | 0131101104 | 162370409 | 7 | 3 | 3 | 2 | 383 | 8.27 | 8.19 | 383 | 8.27 | 8.19 | 429 | 9.27 | 9.18 | 429 | 9.27 | 9.18 | 394 | 8.51 | 8.42 | 394 | 8.51 | 8.42 | 442 | 9.55 | 9.45 | 442 | 9.55 | 9.45 | 750Cu P&L cable will be replaced with 1100 Al EPR cable & reuse the existing 1000Al XLP cable (from U1115) in 2016/2017 on PM# 30866455 & 30866456 |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {BE9C9815-0352-493D-8954-35A9859A86B0}
4670 | 3823 | {464AB082-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 1 (Non SCADA) | CB A406 (Non-SCADA) | PGE\SZC1 | 2017-03-07 14:12:06.1567174 -08:00 | 162370406 | 013111110 | 3 | 3 | 3 | 1 | 223 | 1.61 | 1.59 | 211 | 1.52 | 1.5 | 248 | 1.79 | 1.77 | 235 | 1.69 | 1.67 | 283 | 2.04 | 2.02 | 268 | 1.93 | 1.91 | 300 | 2.16 | 2.14 | 285 | 2.05 | 2.03 |  |  | TRUE | FALSE | 1553 | 2018 | 1863 | 2329 | {C09B055C-9E8E-4B87-9C9D-53EB50A02A20}
4671 | 3823 | {464AB085-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 1 (Non SCADA) | CB A407 (Non-SCADA) | PGE\SZC1 | 2016-10-28 11:38:59.6509999 -07:00 | 162370407 | 162370410 | 3 | 3 | 3 | 1 | 300 | 2.16 | 2.14 | 285 | 2.05 | 2.03 | 378 | 2.72 | 2.69 | 359 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 342 | 2.46 | 2.44 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | TRUE | FALSE | 1553 | 2018 | 1863 | 2329 | {DFC5BADE-3FD3-4BC3-B076-FA4BA7BF177B}
4672 | 3823 | {464AB088-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 1 (Non SCADA) | CB A409 (Non-SCADA) | PGE\SZC1 | 2017-03-07 14:22:30.0439150 -08:00 | 162370409 | 163701109 | 3 | 3 | 3 | 1 | 300 | 2.16 | 2.14 | 285 | 2.05 | 2.03 | 378 | 2.72 | 2.69 | 370 | 2.67 | 2.64 | 360 | 2.59 | 2.56 | 342 | 2.46 | 2.44 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | TRUE | FALSE | 1553 | 2018 | 1863 | 2329 | {A7DC39EC-9678-4AD2-B64A-ABB0A7A0D123}
4673 | 2410 | {CFDD35C2-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN LEANDRO | Bank 1 | CB 1110 | PGE\RDR1 | 2017-05-11 08:43:15.1088677 -07:00 | 0131101110 | 162370411 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | U1110 outlet change was initiated by PM# 30866456 & has been completed under PM# 31109438 |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {E9489F4E-A787-4140-B997-9434E2FEB64F}
4674 | 3823 | {464AB08B-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 1 (Non SCADA) | CB A410 (Non-SCADA) | PGE\SZC1 | 2017-03-07 14:23:59.2308301 -08:00 | 162370410 | 163701110 | 3 | 3 | 3 | 1 | 300 | 2.16 | 2.14 | 285 | 2.05 | 2.03 | 326 | 2.35 | 2.33 | 326 | 2.35 | 2.33 | 311 | 2.24 | 2.22 | 311 | 2.24 | 2.22 | 336 | 2.42 | 2.4 | 336 | 2.42 | 2.4 |  |  | TRUE | FALSE | 1553 | 2018 | 1863 | 2329 | {CD0B4A48-C070-4552-9670-0710AB002D5E}
4675 | 3824 | {3C91ADB3-671D-11E5-80CA-005056A729E5} | STOCKTON | METTLER | Bank 3 (Non SCADA) | CB 1109 (Non-SCADA) | PGE\BXYD | 2017-01-11 17:25:38.4539632 -08:00 | 1637001109 | 163021102 | 8 | 3 | 3 | 1 | 417 | 9.1 | 9.01 | 396 | 8.64 | 8.55 | 417 | 9.1 | 9.01 | 396 | 8.64 | 8.55 | 417 | 9.1 | 9.01 | 396 | 8.64 | 8.55 | 417 | 9.1 | 9.01 | 396 | 8.64 | 8.55 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {7AC18777-E353-4C92-BFE6-501805F14E3C}
4676 | 3823 | {464AB08E-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 1 (Non SCADA) | CB A411 (Non-SCADA) | PGE\SZC1 | 2017-03-07 14:25:36.2802964 -08:00 | 162370411 | 163021103 | 3 | 3 | 3 | 1 | 233 | 1.68 | 1.66 | 233 | 1.68 | 1.66 | 252 | 1.82 | 1.8 | 252 | 1.82 | 1.8 | 240 | 1.73 | 1.71 | 240 | 1.73 | 1.71 | 259 | 1.87 | 1.85 | 259 | 1.87 | 1.85 |  |  | TRUE | FALSE | 1553 | 2018 | 1863 | 2329 | {50470C52-1E45-467D-B17C-A659D2152766}
4678 | 3824 | {3C91ADB6-671D-11E5-80CA-005056A729E5} | STOCKTON | METTLER | Bank 3 (Non SCADA) | CB 1110 (Non-SCADA) | PGE\BXYD | 2017-01-11 17:26:31.5105835 -08:00 | 1637001110 | 013111105 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {54157DD1-6489-4A33-B4D8-5BA43C161FC6}
4679 | 3826 | {464AB0F7-671D-11E5-80CA-005056A729E5} | STOCKTON | TERMINOUS | Bank 1 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\BXYD | 2017-01-11 09:21:15.3533437 -08:00 | 1630201102 | 013111106 | 8 | 3 | 3 | 1 | 263 | 5.74 | 5.68 | 263 | 5.74 | 5.68 | 343 | 7.49 | 7.42 | 343 | 7.49 | 7.42 | 316 | 6.9 | 6.83 | 316 | 6.9 | 6.83 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 |  |  | FALSE | FALSE | 263 | 343 | 316 | 395 | {D8AE4496-9444-4A19-9C7F-CF960C7A0A0D}
4681 | 3826 | {464AB0FD-671D-11E5-80CA-005056A729E5} | STOCKTON | TERMINOUS | Bank 1 (Non SCADA) | CB 1103 (Non-SCADA) | PGE\TxY6 | 2016-10-28 14:17:20.8686084 -07:00 | 1630201103 | 013111107 | 8 | 3 | 3 | 1 | 263 | 5.74 | 5.68 | 263 | 5.74 | 5.68 | 343 | 7.49 | 7.42 | 343 | 7.49 | 7.42 | 316 | 6.9 | 6.83 | 316 | 6.9 | 6.83 | 395 | 8.62 | 8.53 | 395 | 8.62 | 8.53 |  |  | FALSE | FALSE | 263 | 343 | 316 | 395 | {0CBAD509-D870-49FF-9F66-847E440896AE}
4683 | 3827 | {CFDD35E9-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN LEANDRO | Bank 2 | CB 1105 | PGE\RDR1 | 2017-05-11 12:38:43.4348360 -07:00 | 0131101105 | 022721101 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 665 | 14.36 | 14.22 | 665 | 14.36 | 14.22 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 674 | 14.56 | 14.41 | 674 | 14.56 | 14.41 | Relay is Microprocessor? Need to confirm..\\hayward01\omc\Hayward_Engr\Hayward\Relay Settings\San Leandro\1105. Rule 20 (30616108) will UG all of 3/0Cu & 715Al on E 14th. with 1100Al EPR |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {5EE5BA3D-6382-478E-B80C-CF8B202E5141}
4684 | 3827 | {CFDD35F2-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN LEANDRO | Bank 2 | CB 1106 | PGE\RDR1 | 2017-05-11 13:28:57.6312002 -07:00 | 0131101106 | 022721102 | 7 | 3 | 3 | 2 | 435 | 9.4 | 9.31 | 435 | 9.4 | 9.31 | 496 | 10.71 | 10.6 | 496 | 10.71 | 10.6 | 492 | 10.63 | 10.52 | 492 | 10.63 | 10.52 | 546 | 11.79 | 11.67 | 546 | 11.79 | 11.67 | 750Cu P&L cable will be replaced in 2017/2018 under PM# 30866456 |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {E749E088-5D64-4247-9605-9CBB6FA746D7}
4685 | 3827 | {CFDD3602-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN LEANDRO | Bank 2 | CB 1107 | PGE\RDR1 | 2017-05-11 14:24:17.7182468 -07:00 | 0131101107 | 022721106 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 750 | 16.2 | 16.04 | 750 | 16.2 | 16.04 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 750 | 16.2 | 16.04 | 750 | 16.2 | 16.04 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {1886286A-1997-4332-891B-41388C5AA76F}
4806 | 3868 | {2C77CAB3-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SNEATH LANE | Bank 1 | CB 1101 | PGE\C7CF | 2016-11-01 14:52:43.4146865 -07:00 | 0227201101 | 063131105 | 8 | 3 | 3 | 2 | 429 | 9.36 | 9.27 | 429 | 9.36 | 9.27 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 429 | 558 | 515 | 644 | {99A5FCBD-F076-43DF-A38C-95D3D6CCADDA}
4807 | 3868 | {2C77CACB-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SNEATH LANE | Bank 1 | CB 1102 | PGE\C7CF | 2016-11-01 14:53:56.0794711 -07:00 | 0227201102 | 022580401 | 8 | 3 | 3 | 2 | 429 | 9.36 | 9.27 | 429 | 9.36 | 9.27 | 554 | 12.09 | 11.97 | 554 | 12.09 | 11.97 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 |  |  | FALSE | FALSE | 429 | 558 | 515 | 644 | {4B7AA85E-3225-4348-B8FB-C80B00181C3B}
4808 | 3871 | {2C77CAFA-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SNEATH LANE | Bank 2 | CB 1106 | PGE\C7CF | 2016-11-01 15:48:43.4908125 -07:00 | 0227201106 | 253411101 | 8 | 3 | 3 | 2 | 429 | 9.36 | 9.27 | 429 | 9.36 | 9.27 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 429 | 558 | 515 | 644 | {B4739688-B516-42FD-8ECF-CE07E2427903}
4809 | 3866 | {812C0580-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WEST SACRAMENTO | Bank 1 | CB 1105 | PGE\TEJ2 | 2016-11-01 14:59:29.4242135 -07:00 | 0631301105 | 253411102 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 634 | 13.84 | 13.7 | 634 | 13.84 | 13.7 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {392723EE-2F7F-46AA-A8F8-26166CC54D9F}
4810 | 3872 | {8D6E923E-3D5A-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | OCEAN | BANK 401 (Non SCADA) | CB 401 (Non-SCADA) | PGE\DMAL | 2017-05-16 08:57:06.9058725 -07:00 | 022580401 | 253411103 | 3 | 3 | 3 | 2 | 319 | 2.3 | 2.28 | 319 | 2.3 | 2.28 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 383 | 2.76 | 2.73 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 319 | 400 | 383 | 400 | {DC3EBE13-8E89-4931-8CDC-C174CA57E4B1}
4812 | 3873 | {E30059BA-671D-11E5-80CA-005056A729E5} | KERN | LAKEVIEW | Bank 1 (Non SCADA) | CB 1101 | PGE\BXYD | 2016-11-01 15:01:45.6712671 -07:00 | 2534101101 | 063131106 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {4C2FA3E0-9D28-426F-B7F5-42463151E270}
4813 | 3873 | {E30059BF-671D-11E5-80CA-005056A729E5} | KERN | LAKEVIEW | Bank 1 (Non SCADA) | CB 1102 | PGE\BXYD | 2016-11-01 15:04:18.0967283 -07:00 | 2534101102 | 063131107 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {CF3861A5-9576-48B2-8915-E45FA2E220B3}
4814 | 3873 | {E30059CD-671D-11E5-80CA-005056A729E5} | KERN | LAKEVIEW | Bank 1 (Non SCADA) | CB 1103 | PGE\BXYD | 2016-11-01 15:06:42.9992483 -07:00 | 2534101103 | 022580402 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {1197865B-5127-486B-B862-89F8BCC9BBFD}
4815 | 3866 | {812C0589-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WEST SACRAMENTO | Bank 1 | CB 1106 | PGE\JMB4 | 2017-03-30 12:48:34.4542308 -07:00 | 0631301106 | 255262101 | 8 | 3 | 3 | 1 | 566 | 12.35 | 12.23 | 566 | 12.35 | 12.23 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {D4F8C384-B3A0-41AB-B73A-6CB0CD7685F6}
4817 | 3867 | {812C059C-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WEST SACRAMENTO | Bank 2 | CB 1107 | PGE\TEJ2 | 2016-11-01 15:24:10.5088425 -07:00 | 0631301107 | 255262103 | 8 | 3 | 3 | 1 | 745 | 16.26 | 16.1 | 745 | 16.26 | 16.1 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {70B138FB-1922-4CA9-B54F-090A6C3DA4A1}
4818 | 3874 | {8D6E9241-3D5A-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | OCEAN | BANK 402 (Non SCADA) | CB 402 (Non-SCADA) | PGE\DMAL | 2017-05-16 08:58:59.2621139 -07:00 | 022580402 | 255262104 | 3 | 3 | 3 | 2 | 319 | 2.3 | 2.28 | 319 | 2.3 | 2.28 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 383 | 2.76 | 2.73 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 319 | 400 | 383 | 400 | {D7B4A46C-3A5F-4D58-A78C-2EF732B60632}
4819 | 3877 | {E3005959-671D-11E5-80CA-005056A729E5} | KERN | KERN POWER | Bank 6 | CB 2101 | PGE\BXYD | 2016-11-07 08:26:22.6341072 -08:00 | 2552602101 | 255262105 | 12 | 3 | 3 | 1 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {D7CA96CD-1362-4F51-8AC7-1876FCCAB6D8}
4820 | 3877 | {E300596A-671D-11E5-80CA-005056A729E5} | KERN | KERN POWER | Bank 6 | CB 2103 | PGE\BXYD | 2016-11-07 08:26:37.0649338 -08:00 | 2552602103 | 022721107 | 12 | 3 | 3 | 1 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {B9D67A14-9275-4A35-B327-DEB1E25F1C99}
4821 | 3878 | {E3005983-671D-11E5-80CA-005056A729E5} | KERN | KERN POWER | Bank 7 | CB 2104 | PGE\BXYD | 2016-11-07 08:27:26.9400520 -08:00 | 2552602104 | 063131108 | 12 | 3 | 3 | 1 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {EE582D02-88F3-4513-A4D6-7D752A0A933B}
4822 | 3878 | {E3005994-671D-11E5-80CA-005056A729E5} | KERN | KERN POWER | Bank 7 | CB 2105 | PGE\BXYD | 2016-11-07 08:27:50.4034645 -08:00 | 2552602105 | 022861103 | 12 | 3 | 3 | 1 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {0510724E-7145-4B02-B0E8-1C41310676CA}
4823 | 3871 | {2C77CB1F-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SNEATH LANE | Bank 2 | CB 1107 | PGE\C7CF | 2016-11-01 15:48:09.7403245 -07:00 | 0227201107 | 022861104 | 8 | 3 | 3 | 2 | 429 | 9.36 | 9.27 | 429 | 9.36 | 9.27 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 429 | 558 | 515 | 644 | {5F67DB92-AEA6-49BF-9CD8-5DDA40952109}
4824 | 3867 | {812C05B3-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WEST SACRAMENTO | Bank 2 | CB 1108 | PGE\TEJ2 | 2016-11-01 15:57:46.4750512 -07:00 | 0631301108 | 063131109 | 8 | 3 | 3 | 1 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {6BA8DBA2-242C-4E76-B08B-8C2311D20A43}
4825 | 3879 | {2C77CA4C-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SERRAMONTE | Bank 1 | CB 1103 | PGE\C7CF | 2016-11-01 16:00:55.0289226 -07:00 | 0228601103 | 182742104 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {4C27B9BB-77A3-43E4-9B09-9805E26C8D7A}
4826 | 3879 | {2C77CA71-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SERRAMONTE | Bank 1 | CB 1104 | PGE\C7CF | 2016-11-01 16:02:05.7565282 -07:00 | 0228601104 | 083500401 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {2FA3CB02-832A-41EF-84D3-1705594D70DC}
4827 | 3870 | {812C05DB-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WEST SACRAMENTO | Bank 3 | CB 1109 | PGE\DCGa | 2016-11-01 19:39:32.2570838 -07:00 | 0631301109 | 024190404 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {3E44210B-EFDE-4B3A-9C60-21F06099BDDA}
4828 | 3845 | {EA1DF6B4-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SAN BENITO | Bank 1 | CB 2104 | PGE\ACT0 | 2016-11-01 16:17:50.5834737 -07:00 | 1827402104 | 024190407 | 12 | 3 | 3 | 2 | 369 | 13.95 | 13.81 | 369 | 13.95 | 13.81 | 414 | 15.65 | 15.49 | 414 | 15.65 | 15.49 | 415 | 15.68 | 15.52 | 415 | 15.68 | 15.52 | 443 | 16.74 | 16.57 | 443 | 16.74 | 16.57 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {723BD509-D6D8-4C92-B92C-9815323009EB}
4829 | 3881 | {EA1DF6C5-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SEACLIFF | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\ACT0 | 2016-11-03 08:10:48.7729457 -07:00 | 083500401 | 024190408 | 4 | 3 | 3 | 2 | 340 | 2.57 | 2.54 | 340 | 2.57 | 2.54 | 443 | 3.35 | 3.32 | 443 | 3.35 | 3.32 | 409 | 3.1 | 3.07 | 409 | 3.1 | 3.07 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 |  |  | FALSE | FALSE | 340 | 443 | 409 | 511 | {BE15BBFD-8D94-4666-90D4-D05D52757939}
4830 | 3880 | {2C77C962-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SAN MATEO | Bank 4 | CB 404 | PGE\C7CF | 2016-11-01 16:51:43.4422824 -07:00 | 024190404 | 254501102 | 4 | 3 | 3 | 2 | 582 | 4.41 | 4.37 | 582 | 4.41 | 4.37 | 600 | 4.54 | 4.49 | 600 | 4.54 | 4.49 | 600 | 4.54 | 4.49 | 600 | 4.54 | 4.49 | 600 | 4.54 | 4.49 | 600 | 4.54 | 4.49 | 3-1p regulator - 60kVA 2.4kV |  | FALSE | FALSE | 1238 | 1610 | 1486 | 1857 | {9B70EF06-4FA0-4EA9-9AC0-25628CCA940F}
4831 | 3880 | {2C77C972-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SAN MATEO | Bank 4 | CB 407 | PGE\C7CF | 2016-11-01 17:06:29.8260163 -07:00 | 024190407 | 063131110 | 4 | 3 | 3 | 2 | 492 | 3.72 | 3.68 | 492 | 3.72 | 3.68 | 554 | 4.19 | 4.15 | 554 | 4.19 | 4.15 | 515 | 3.9 | 3.86 | 515 | 3.9 | 3.86 | 598 | 4.53 | 4.48 | 598 | 4.53 | 4.48 | 3-1p regulator - 60kVA 2.4kV |  | FALSE | FALSE | 1238 | 1610 | 1486 | 1857 | {0C4D4826-1215-4CC1-BFE3-6837E95C9C26}
4832 | 3880 | {2C77C97B-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SAN MATEO | Bank 4 | CB 408 | PGE\C7CF | 2016-11-01 17:07:59.1807519 -07:00 | 024190408 | 063131111 | 4 | 3 | 3 | 2 | 505 | 3.82 | 3.78 | 505 | 3.82 | 3.78 | 586 | 4.44 | 4.4 | 586 | 4.44 | 4.4 | 515 | 3.9 | 3.86 | 515 | 3.9 | 3.86 | 598 | 4.53 | 4.48 | 598 | 4.53 | 4.48 | 3-1p regulator - 60kVA 2.4kV |  | FALSE | FALSE | 1238 | 1610 | 1486 | 1857 | {AAF34E84-CE6B-4C09-A3A6-334551EA1D7C}
4833 | 3882 | {DD064303-671D-11E5-80CA-005056A729E5} | KERN | CHARCA | Bank 1 | CB 1102 | PGE\JWCp | 2016-11-03 10:35:59.7911508 -07:00 | 2545001102 | 162081101 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 1844 | {7663984D-0884-43A2-AF8C-7D2AAFDE05B5}
4836 | 3870 | {812C05F9-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WEST SACRAMENTO | Bank 3 | CB 1110 | PGE\TEJ2 | 2016-11-02 07:32:55.7001882 -07:00 | 0631301110 | 013111109 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {1D1B96B6-9BCA-44C8-815F-1E6241E36A45}
4837 | 3870 | {812C0625-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WEST SACRAMENTO | Bank 3 | CB 1111 | PGE\TEJ2 | 2016-11-02 07:49:46.5782487 -07:00 | 0631301111 | 013111111 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {12969CD6-856F-4C56-B13A-FCB88D5E46C2}
4686 | 3828 | {464AAEDE-671D-11E5-80CA-005056A729E5} | STOCKTON | NEW HOPE | Bank 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\BXYD | 2017-01-11 14:58:06.0940989 -08:00 | 1620801101 | 162081102 | 8 | 3 | 3 | 1 | 183 | 3.99 | 3.95 | 173 | 3.78 | 3.74 | 211 | 4.6 | 4.55 | 200 | 4.36 | 4.32 | 266 | 5.81 | 5.75 | 252 | 5.5 | 5.45 | 284 | 6.2 | 6.14 | 269 | 5.87 | 5.81 |  |  | FALSE | FALSE | 263 | 343 | 316 | 395 | {31D561E2-941D-495B-BDD8-EA1E9A0602C3}
4687 | 3827 | {CFDD3654-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN LEANDRO | Bank 2 | CB 1109 | PGE\RDR1 | 2017-05-15 13:29:17.7150387 -07:00 | 0131101109 | 013111112 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | some, not all of 750Cu XLP will be replaced under PM#30866455 in 2016/2017 |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {8940F9D4-E5BC-47BD-AEFA-6425AA145945}
4689 | 3827 | {CFDD367D-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN LEANDRO | Bank 2 | CB 1111 | PGE\RDR1 | 2017-05-15 14:12:49.0180551 -07:00 | 0131101111 | 013111113 | 7 | 3 | 3 | 2 | 564 | 12.18 | 12.06 | 564 | 12.18 | 12.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | PM# 30866456 will replace all of 1000Al XLP inside the station up to riser SW8705 in 2017/2018 |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {8359DCED-FB7C-4E28-96D7-5FC74F14C4EC}
4690 | 3828 | {464AAEE4-671D-11E5-80CA-005056A729E5} | STOCKTON | NEW HOPE | Bank 1 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\BXYD | 2017-01-11 14:59:22.1289863 -08:00 | 1620801102 | 103531103 | 8 | 3 | 3 | 1 | 263 | 5.74 | 5.68 | 263 | 5.74 | 5.68 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 |  |  | FALSE | FALSE | 263 | 343 | 316 | 395 | {10B0E002-E8AE-48A5-B8A2-DA2BE3016F32}
4691 | 3829 | {CFDD3689-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN LEANDRO | Bank 3 | CB 1112 | PGE\RDR1 | 2017-05-15 15:00:37.6324197 -07:00 | 0131101112 | 083692105 | 7 | 3 | 3 | 2 | 481 | 10.39 | 10.29 | 481 | 10.39 | 10.29 | 592 | 12.79 | 12.66 | 592 | 12.79 | 12.66 | 495 | 10.69 | 10.58 | 495 | 10.69 | 10.58 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 750 Cu P&L cable will be replaced under 30866456 in 2017/2018 |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {D9284C6A-1D56-4AFC-A1C8-AA384E0B3272}
4692 | 3829 | {CFDD3692-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN LEANDRO | Bank 3 | CB 1113 | PGE\RDR1 | 2017-05-18 10:05:59.6560969 -07:00 | 0131101113 | 083750401 | 7 | 3 | 3 | 2 | 435 | 9.4 | 9.31 | 435 | 9.4 | 9.31 | 496 | 10.71 | 10.6 | 496 | 10.71 | 10.6 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 550 | 11.88 | 11.76 | 550 | 11.88 | 11.76 | This circuit will swap customers with U1103 around 2017/2018 under PM# 30866456 |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {1F3E116C-7980-4FB3-8989-83CFB9B73B1E}
4693 | 3830 | {A6861C85-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | RAWSON | Bank 1 | CB 1103 | PGE\CTD7 | 2017-04-19 17:03:26.0648205 -07:00 | 1035301103 | 083750402 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 687 | 894 | 825 | 1031 | {59B33199-C714-40E2-87B2-8FCBA97AE0BF}
4694 | 3813 | {B6D7356A-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | ROB ROY | Bank 1 | CB 2105 | PGE\ACT0 | 2016-10-31 08:39:08.5852804 -07:00 | 0836902105 | 182631105 | 12 | 3 | 3 | 2 | 595 | 22.49 | 22.27 | 595 | 22.49 | 22.27 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 595 | 773 | 714 | 893 | {AE8E8798-2D6E-461C-AD99-B12600E75ED6}
4695 | 3831 | {C47631FD-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | ROLAND | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\ACT0 | 2016-10-31 08:58:26.4220764 -07:00 | 083750401 | 182631107 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {DA5A99E7-AF46-400C-B879-CF9673DDF137}
4696 | 3832 | {C4763203-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | ROLAND | Bank 2 (Non SCADA) | CB 402 (Non-SCADA) | PGE\ACT0 | 2016-10-31 09:06:26.0348383 -07:00 | 083750402 | 182631108 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {ECAF2F80-504B-403C-905D-41FE14666C95}
4697 | 2755 | {A4EDE239-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SAN LUIS OBISPO | Bank 4 | CB 1105 | PGE\A9S5 | 2016-11-11 10:44:19.2548767 -08:00 | 1826301105 | 182661104 | 8 | 3 | 3 | 2 | 581 | 12.68 | 12.55 | 581 | 12.68 | 12.55 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3071 | {BCE18988-2D8B-4830-BD1F-8E1783776EE2}
4698 | 1016 | {A4EDE255-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SAN LUIS OBISPO | Bank 6 | CB 1107 | PGE\A9S5 | 2016-11-11 10:46:58.4219102 -08:00 | 1826301107 | 182661105 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {58ED9B56-1523-4B05-92E5-382EAF645EF3}
4699 | 1016 | {B4D03AA1-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SAN LUIS OBISPO | Bank 6 | CB 1108 | PGE\A9S5 | 2016-11-11 10:47:49.8265679 -08:00 | 1826301108 | 182661106 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {10971087-D617-49EB-9BA5-0473FD901015}
4700 | 3835 | {B4D03AB2-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SAN MIGUEL | Bank 1 | CB 1104 | PGE\A9S5 | 2016-11-11 10:48:50.6067362 -08:00 | 1826601104 | 182661107 | 8 | 3 | 3 | 1 | 416 | 9.08 | 8.99 | 416 | 9.08 | 8.99 | 484 | 10.56 | 10.45 | 484 | 10.56 | 10.45 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1067 | {EF16CA2F-3541-4550-B558-E39116931332}
4702 | 3835 | {B4D03ACC-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SAN MIGUEL | Bank 1 | CB 1105 | PGE\A9S5 | 2016-11-11 10:50:28.3912786 -08:00 | 1826601105 | 182671105 | 8 | 3 | 3 | 1 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1067 | {EAF0EA67-C29D-4FE1-BCB4-DC1AD47D6840}
4703 | 3835 | {B4D03AD1-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SAN MIGUEL | Bank 1 | CB 1106 | PGE\J2T4 | 2017-03-02 13:58:40.8410545 -08:00 | 1826601106 | 182671106 | 8 | 3 | 3 | 1 | 210 | 4.58 | 4.53 | 199 | 4.34 | 4.3 | 243 | 5.3 | 5.25 | 230 | 5.02 | 4.97 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1067 | {E787B45B-F371-4305-84A6-3285DA3DE1B6}
4704 | 3835 | {B4D03ADC-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SAN MIGUEL | Bank 1 | CB 1107 | PGE\A9S5 | 2016-11-11 10:49:50.3721950 -08:00 | 1826601107 | 182671107 | 8 | 3 | 3 | 1 | 223 | 4.87 | 4.82 | 223 | 4.87 | 4.82 | 248 | 5.41 | 5.36 | 248 | 5.41 | 5.36 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 302 | 6.59 | 6.52 | 302 | 6.59 | 6.52 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1067 | {5700E6B6-B5C9-4171-8645-E57EC0E24446}
4705 | 1014 | {BAD0BE2F-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SANTA MARIA | Bank 2 | CB 1105 | PGE\A9S5 | 2016-11-11 10:51:27.9848618 -08:00 | 1826701105 | 182671108 | 8 | 3 | 3 | 2 | 720 | 15.71 | 15.55 | 720 | 15.71 | 15.55 | 855 | 18.66 | 18.47 | 855 | 18.66 | 18.47 | 900 | 19.64 | 19.44 | 900 | 19.64 | 19.44 | 1000 | 21.82 | 21.6 | 1000 | 21.82 | 21.6 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {DE5E441C-80B7-4966-985D-D44834B1CCC6}
4706 | 1014 | {BAD0BE49-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SANTA MARIA | Bank 2 | CB 1106 | PGE\A9S5 | 2016-11-11 10:51:56.3159146 -08:00 | 1826701106 | 182671109 | 8 | 3 | 3 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {C44D20EB-881E-471B-97E0-9E4465BAC71E}
4707 | 1014 | {C0C81A14-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SANTA MARIA | Bank 2 | CB 1107 | PGE\ACT0 | 2016-12-01 07:52:06.0098736 -08:00 | 1826701107 | 182011101 | 8 | 3 | 3 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 634 | 13.84 | 13.7 | 634 | 13.84 | 13.7 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F89168F4-9661-4D3F-BE1A-CF9922B6D455}
4708 | 1014 | {C0C81A19-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SANTA MARIA | Bank 2 | CB 1108 | PGE\A9S5 | 2016-11-11 10:53:22.9921274 -08:00 | 1826701108 | 063601105 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 665 | 14.51 | 14.36 | 665 | 14.51 | 14.36 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {6261A266-7095-461A-9B11-0F62690FA374}
4709 | 3838 | {C0C81A3F-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SANTA MARIA | Bank 3 | CB 1109 | PGE\A9S5 | 2016-11-11 10:57:52.2083805 -08:00 | 1826701109 | 182011102 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {EB5BB030-627E-4635-8844-211950CE8AAF}
4710 | 3833 | {C476320C-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SALINAS | Bank 4 | CB 1101 | PGE\ACT0 | 2016-10-31 13:35:28.4802327 -07:00 | 1820101101 | 063601106 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {65A70A57-E44A-4EB9-BD7B-3337ED62A631}
4711 | 2662 | {812C04A0-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACAVILLE | Bank 2 | CB 1105 | PGE\TEJ2 | 2016-10-31 13:35:49.6343751 -07:00 | 0636001105 | 182011106 | 8 | 3 | 3 | 1 | 584 | 12.75 | 12.62 | 584 | 12.75 | 12.62 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {4FFCD4BC-DDE8-4EC1-A96B-61221AA8614B}
4712 | 3833 | {C4763214-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SALINAS | Bank 4 | CB 1102 | PGE\ACT0 | 2016-10-31 13:44:56.6067103 -07:00 | 1820101102 | 182011107 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {93A9C7C7-9886-41CF-934C-0D51B55DA3FD}
4713 | 2662 | {812C04B0-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACAVILLE | Bank 2 | CB 1106 | PGE\TEJ2 | 2016-10-31 13:47:42.4752661 -07:00 | 0636001106 | 063601107 | 8 | 3 | 3 | 1 | 584 | 12.75 | 12.62 | 515 | 11.24 | 11.13 | 600 | 13.09 | 12.96 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {97C7DE57-596E-4699-A0EE-F489D1797C61}
4714 | 3833 | {C4763231-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SALINAS | Bank 4 | CB 1106 | PGE\ACT0 | 2016-10-31 13:49:10.0400216 -07:00 | 1820101106 | 063601108 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {5560FD85-FA58-4222-A2F6-B22E7ACEA295}
4715 | 3833 | {CAB6F267-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SALINAS | Bank 4 | CB 1107 | PGE\ACT0 | 2016-10-31 13:52:07.7768357 -07:00 | 1820101107 | 063601109 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {2782DB47-E3E4-43E2-8F06-5D6FDC155E41}
4716 | 2662 | {812C04B9-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACAVILLE | Bank 2 | CB 1107 | PGE\TEJ2 | 2016-10-31 13:54:41.5799292 -07:00 | 0636001107 | 063601110 | 8 | 3 | 3 | 1 | 584 | 12.75 | 12.62 | 584 | 12.75 | 12.62 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {3442E8E1-C298-4E26-8064-D7974888B0E3}
4717 | 2662 | {812C04C2-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACAVILLE | Bank 2 | CB 1108 | PGE\TEJ2 | 2016-10-31 14:06:07.0420991 -07:00 | 0636001108 | 063601111 | 8 | 3 | 3 | 1 | 573 | 12.51 | 12.38 | 573 | 12.51 | 12.38 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {7126E98D-0D4B-49D6-A8C1-FC7C303A4F1E}
4719 | 2663 | {812C04DC-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACAVILLE | Bank 3 | CB 1109 | PGE\TEJ2 | 2016-10-31 14:18:48.1715390 -07:00 | 0636001109 | 182011103 | 8 | 3 | 3 | 1 | 584 | 12.75 | 12.62 | 584 | 12.75 | 12.62 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {EC58417A-F8D0-477A-8A73-C0FAB781C2E3}
4720 | 2663 | {812C0501-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACAVILLE | Bank 3 | CB 1110 | PGE\TEJ2 | 2016-10-31 14:26:49.5130308 -07:00 | 0636001110 | 182011104 | 8 | 3 | 3 | 1 | 499 | 10.89 | 10.78 | 499 | 10.89 | 10.78 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 553 | 12.07 | 11.95 | 553 | 12.07 | 11.95 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {7CA4E363-2159-4928-90F3-715AA61751A0}
4721 | 2663 | {812C053B-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACAVILLE | Bank 3 | CB 1111 | PGE\TEJ2 | 2016-10-31 14:33:25.6952912 -07:00 | 0636001111 | 182011105 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {CEBBC715-7BD2-40A5-8A56-4C6239B3448C}
4722 | 3839 | {CAB6F278-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SALINAS | Bank 6 | CB 1103 | PGE\ACT0 | 2016-10-31 15:01:10.5558861 -07:00 | 1820101103 | 063601112 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F1E43636-9792-4271-8ECD-F1516423B997}
4723 | 3839 | {D123CB85-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SALINAS | Bank 6 | CB 1104 | PGE\JLDe | 2017-03-13 14:32:49.6014423 -07:00 | 1820101104 | 182011108 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B8EB3206-BB99-4F61-99F6-35663ABF3D7F}
4724 | 3839 | {D73E3F8B-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SALINAS | Bank 6 | CB 1105 | PGE\ACT0 | 2016-10-31 15:13:51.0123631 -07:00 | 1820101105 | 182011109 | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 582 | 12.7 | 12.57 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {7790CA24-81B9-48F1-AA39-6F6EBA11388D}
4725 | 2663 | {812C0552-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | VACAVILLE | Bank 3 | CB 1112 | PGE\TEJ2 | 2016-10-31 15:15:48.9713875 -07:00 | 0636001112 | 182191101 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 689 | 15.04 | 14.89 | 689 | 15.04 | 14.89 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 732 | 15.98 | 15.82 | 732 | 15.98 | 15.82 | Tie to the Vacaville 1102 through 1000 Al XLP Conc PVC UG, 397 Al OH, and 600 Al XLP Conc PVC UG. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {AF96A7B5-6CAF-416D-B591-FEB1C1A82AE4}
4726 | 3839 | {D73E3F9C-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SALINAS | Bank 6 | CB 1108 | PGE\ACT0 | 2016-10-31 15:19:26.0323026 -07:00 | 1820101108 | 042550401 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {5870B7CB-153E-4DFB-95D0-551146E16EB1}
4729 | 3839 | {D73E3FA1-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SALINAS | Bank 6 | CB 1109 | PGE\ACT0 | 2016-10-31 15:21:24.4720766 -07:00 | 1820101109 | 182191102 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9C8F86AB-6261-4A06-9F05-0EC6690343C0}
4730 | 3841 | {D73E3FBB-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SAN ARDO | Bank 1 | CB 1101 | PGE\ACT0 | 2016-11-22 16:20:49.0848533 -08:00 | 1821901101 | 043021101 | 8 | 3 | 2 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {F342D299-E9D4-4098-A80A-85F43ED65ABC}
4731 | 3843 | {AC6A2982-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | VALLEJO STA C | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-19 16:32:14.7797514 -08:00 | 04255401 | 182742101 | 4 | 3 | 3 | 2 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 350 | 2.65 | 2.62 | 350 | 2.65 | 2.62 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {4ED9DDFB-D295-4299-9586-050D5DE6AA5B}
4732 | 3841 | {DD5B5FA8-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SAN ARDO | Bank 1 | CB 1102 | PGE\ACT0 | 2016-10-31 16:10:28.0493896 -07:00 | 1821901102 | 043021102 | 8 | 3 | 2 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {D40CDAAE-CAF3-47BD-A9F8-6F45E11992BA}
4733 | 3844 | {AC6A298B-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | WOODACRE | Bank 1 | CB 1101 | PGE\C7CF | 2016-12-19 16:33:28.9769865 -08:00 | 0430201101 | 062041102 | 8 | 3 | 3 | 2 | 429 | 9.36 | 9.27 | 429 | 9.36 | 9.27 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 429 | 558 | 515 | 644 | {F7A65DE7-5690-4510-A0AB-D2C3B55C2FEF}
4734 | 3845 | {E37B05D5-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SAN BENITO | Bank 1 | CB 2101 | PGE\ACT0 | 2016-11-01 16:25:10.6900599 -07:00 | 1827402101 | 062041103 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | * 4/0Al starts near SCADA Switch 9293 on Hwy 156 LIMITS TRANSFERS FROM HOLLISTER 2101: 345A, 386A, 443A, 473A * 1/0Cu starts near SCADA Recloser 63516 on Hwy 156 LIMITS TRANSFERS FROM HOLLISTER 2101: 282A, 315A, 358A, 382A |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {81C9EA7D-A1CA-4F92-B87B-97D984E8E015}
4736 | 3844 | {B2679F85-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | WOODACRE | Bank 1 | CB 1102 | PGE\C7CF | 2016-12-19 16:33:46.3717473 -08:00 | 0430201102 | 182742102 | 8 | 3 | 3 | 2 | 429 | 9.36 | 9.27 | 429 | 9.36 | 9.27 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 429 | 558 | 515 | 644 | {4A0143C7-5204-433E-A039-20E5125E1D9C}
4737 | 2574 | {4D891702-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DAVIS | Bank 1 | CB 1102 | PGE\TEJ2 | 2016-11-01 07:49:34.3508652 -07:00 | 0620401102 | 182742103 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {2E00612D-6749-4AF2-985B-8FD6DB1B361C}
4738 | 2574 | {4D891712-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DAVIS | Bank 1 | CB 1103 | PGE\TEJ2 | 2016-11-01 07:54:23.9066421 -07:00 | 0620401103 | 062041104 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {34628DAB-F11D-4485-9B42-AEC4052CB5E5}
4739 | 3845 | {E37B05F5-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SAN BENITO | Bank 1 | CB 2102 | PGE\ACT0 | 2016-11-01 07:57:47.2135668 -07:00 | 1827402102 | 062041105 | 12 | 3 | 3 | 2 | 369 | 13.95 | 13.81 | 369 | 13.95 | 13.81 | 414 | 15.65 | 15.49 | 414 | 15.65 | 15.49 | 415 | 15.68 | 15.52 | 415 | 15.68 | 15.52 | 443 | 16.74 | 16.57 | 443 | 16.74 | 16.57 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {99509938-3063-44F8-AC75-F032F00A3B4B}
4740 | 3845 | {EA1DF6AF-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SAN BENITO | Bank 1 | CB 2103 | PGE\ACT0 | 2016-11-01 16:15:51.4018447 -07:00 | 1827402103 | 062041106 | 12 | 3 | 3 | 2 | 369 | 13.95 | 13.81 | 369 | 13.95 | 13.81 | 414 | 15.65 | 15.49 | 414 | 15.65 | 15.49 | 415 | 15.68 | 15.52 | 415 | 15.68 | 15.52 | 443 | 16.74 | 16.57 | 443 | 16.74 | 16.57 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {8704C7DA-510A-4803-903A-62F05FE8D68E}
4741 | 2574 | {4D891730-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DAVIS | Bank 1 | CB 1104 | PGE\JMB4 | 2017-02-14 16:43:03.5338356 -08:00 | 0620401104 | 062041107 | 8 | 3 | 3 | 1 | 540 | 11.78 | 11.66 | 540 | 11.78 | 11.66 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 598 | 13.05 | 12.92 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {E3458CCB-6FFD-4E15-BB44-75C9F347AAC5}
4742 | 2581 | {4D891751-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DAVIS | Bank 2 | CB 1105 | PGE\JMB4 | 2017-02-14 16:42:39.2441685 -08:00 | 0620401105 | 062041108 | 8 | 3 | 3 | 1 | 540 | 11.78 | 11.66 | 540 | 11.78 | 11.66 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 598 | 13.05 | 12.92 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F837072E-885D-4DE2-BE2D-BB5E1BB4592D}
4743 | 2581 | {4D891761-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DAVIS | Bank 2 | CB 1106 | PGE\TEJ2 | 2016-11-01 08:22:27.8487963 -07:00 | 0620401106 | 013700401 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {09B51B7C-A840-4BC7-BDA4-4C163EE9342C}
4744 | 2581 | {4D89177F-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DAVIS | Bank 2 | CB 1107 | PGE\TEJ2 | 2017-05-25 13:23:26.4119678 -07:00 | 0620401107 | 062041109 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {A2577972-288C-44BB-9182-5855E0BD9F5B}
4745 | 2581 | {4D8917AB-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DAVIS | Bank 2 | CB 1108 | PGE\JMB4 | 2017-03-05 18:35:44.4392725 -08:00 | 0620401108 | 102841101 | 8 | 3 | 3 | 1 | 636 | 13.88 | 13.74 | 570 | 12.44 | 12.32 | 792 | 17.28 | 17.11 | 570 | 12.44 | 12.32 | 691 | 15.08 | 14.93 | 570 | 12.44 | 12.32 | 833 | 18.18 | 18 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {BF76304D-4CEA-43AA-AE6D-E0EE75D99043}
4747 | 3846 | {BF48EF79-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | ARLINGTON | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-12-12 12:47:28.5034800 -08:00 | 013700401 | 062041110 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 303 | 395 | 364 | 433 | {8E2D4AE9-872F-4E21-BDFE-48E994E6AF6B}
4749 | 2583 | {4D8917BE-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DAVIS | Bank 3 | CB 1109 | PGE\TEJ2 | 2016-11-01 09:19:58.9974552 -07:00 | 0620401109 | 102841102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F469FEBA-1CCA-4A22-83FE-4BF1867A0000}
4750 | 3840 | {7A8F2494-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | ANITA | Bank 1 | CB 1101 (Non-SCADA) | PGE\JXF8 | 2016-11-01 11:56:36.0282649 -07:00 | 1028401101 | 012540401 | 8 | 4 | 4 | 1 | 360 | 7.48 | 7.41 | 360 | 7.48 | 7.41 | 469 | 9.75 | 9.65 | 469 | 9.75 | 9.65 | 433 | 9 | 8.91 | 433 | 9 | 8.91 | 517 | 10.75 | 10.64 | 517 | 10.75 | 10.64 |  |  | FALSE | FALSE | 360 | 469 | 433 | 541 | {B14F8BA9-ECFF-40AA-8D83-FBE26CC24C62}
4751 | 2583 | {53849C94-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DAVIS | Bank 3 | CB 1110 | PGE\TEJ2 | 2016-11-01 12:31:49.6189856 -07:00 | 0620401110 | 012540402 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {224AC03F-6005-4F5F-9070-93C93E84E8BD}
4752 | 3840 | {7A8F24B2-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | ANITA | Bank 1 | CB 1102 (Non-SCADA) | PGE\JXF8 | 2016-11-01 11:56:55.5588572 -07:00 | 1028401102 | 062041111 | 8 | 4 | 4 | 1 | 360 | 7.48 | 7.41 | 360 | 7.48 | 7.41 | 469 | 9.75 | 9.65 | 469 | 9.75 | 9.65 | 433 | 9 | 8.91 | 433 | 9 | 8.91 | 517 | 10.75 | 10.64 | 517 | 10.75 | 10.64 |  |  | FALSE | FALSE | 360 | 469 | 433 | 541 | {BA033487-71E2-41CE-A1C3-12425D49F090}
4753 | 3847 | {8E35B629-4AB1-11E6-AFF0-80000BC6CD8D} | EAST BAY | OAKLAND X | UNIT .SUB.#1 | CB 401 (Non-SCADA) | PGE\C7CF | 2016-11-01 09:45:40.2028121 -07:00 | 012540401 | 102841105 | 4 | 3 | 3 | 2 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 396 | 3 | 2.97 | 396 | 3 | 2.97 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {E6CB0DDF-A0A6-403B-9F0C-F1DC8AE13F03}
4754 | 3849 | {98DF5329-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND X | UNIT SUB#2 | CB 402 (Non-SCADA) | PGE\C7CF | 2016-11-01 09:49:30.3747270 -07:00 | 012540402 | 102841106 | 4 | 3 | 3 | 2 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 396 | 3 | 2.97 | 396 | 3 | 2.97 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {11EE2135-2C0F-4A83-913D-2CCBC624E31F}
4755 | 2583 | {53849CC7-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DAVIS | Bank 3 | CB 1111 | PGE\TEJ2 | 2016-11-01 09:49:46.1162602 -07:00 | 0620401111 | 252781101 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {A19609D4-14B9-4C92-96A1-8FB1C3DFF345}
4756 | 3848 | {7A8F24C5-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | ANITA | Bank 2 | CB 1105 | PGE\JXF8 | 2016-11-01 09:53:30.0008702 -07:00 | 1028401105 | 012111105 | 8 | 4 | 4 | 1 | 514 | 10.68 | 10.57 | 514 | 10.68 | 10.57 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 570 | 11.85 | 11.73 | 570 | 11.85 | 11.73 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 |  |  | FALSE | FALSE | 1443 | 1876 | 1732 | 2165 | {4EE7D24B-C259-4B73-ABDB-E426609BBE4C}
4757 | 3848 | {7A8F24D5-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | ANITA | Bank 2 | CB 1106 | PGE\JXF8 | 2016-11-01 09:56:21.2531840 -07:00 | 1028401106 | 012111115 | 8 | 4 | 4 | 1 | 514 | 10.68 | 10.57 | 514 | 10.68 | 10.57 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 570 | 11.85 | 11.73 | 570 | 11.85 | 11.73 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 |  |  | FALSE | FALSE | 1443 | 1876 | 1732 | 2165 | {257458FF-AD45-4F1C-AB7D-932D27DF3533}
4759 | 3852 | {E8FE8E3E-671D-11E5-80CA-005056A729E5} | KERN | MCKITTRICK | Bank 1 | CB 1101 | PGE\BXYD | 2016-11-01 10:21:40.3895079 -07:00 | 2527801101 | 012111116 | 8 | 3 | 3 | 1 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 577 | 750 | 692 | 842 | {BFCA559E-0AF6-4869-B228-8C7E701FCFD2}
4760 | 2555 | {17E29104-22D1-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND L | Bank 5 | CB 1105 (Non-SCADA) | PGE\C7CF | 2016-11-01 10:30:02.9459835 -07:00 | 0121101105 | 012111114 | 8 | 3 | 3 | 2 | 446 | 9.73 | 9.63 | 446 | 9.73 | 9.63 | 549 | 11.98 | 11.86 | 549 | 11.98 | 11.86 | 459 | 10.02 | 9.92 | 459 | 10.02 | 9.92 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {0107AC09-8374-4C75-822A-A5FD858FA350}
4761 | 2555 | {17E290FE-22D1-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND L | Bank 5 | CB 1115 | PGE\C7CF | 2016-11-01 10:32:24.1461117 -07:00 | 0121101115 | 062041112 | 8 | 3 | 3 | 2 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 523 | 11.41 | 11.3 | 523 | 11.41 | 11.3 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 539 | 11.76 | 11.64 | 539 | 11.76 | 11.64 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {62EA4C45-3FAD-4536-B91B-F2D37C04A3A7}
4762 | 2555 | {17E29101-22D1-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND L | Bank 5 | CB 1116 | PGE\C7CF | 2016-11-01 10:33:46.5263561 -07:00 | 0121101116 | 253181104 | 8 | 3 | 3 | 2 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 523 | 11.41 | 11.3 | 523 | 11.41 | 11.3 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 539 | 11.76 | 11.64 | 539 | 11.76 | 11.64 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {BF8F9E39-8E51-480D-BA04-59CA95549874}
4763 | 2553 | {E552B2D3-334C-11E6-B38D-D4BED91EFF1A} | EAST BAY | OAKLAND L | Bank 1 | CB 1114 | PGE\C7CF | 2016-11-01 10:36:37.7964243 -07:00 | 0121101114 | 253181105 | 8 | 3 | 3 | 2 | 490 | 10.69 | 10.58 | 490 | 10.69 | 10.58 | 549 | 11.98 | 11.86 | 549 | 11.98 | 11.86 | 505 | 11.02 | 10.91 | 505 | 11.02 | 10.91 | 565 | 12.33 | 12.21 | 565 | 12.33 | 12.21 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {7DC8C81D-4CF9-440E-9B6C-91719E4559D3}
4764 | 2583 | {53849CEC-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DAVIS | Bank 3 | CB 1112 | PGE\TEJ2 | 2016-11-01 12:31:17.7780613 -07:00 | 0620401112 | 254211101 | 8 | 3 | 3 | 1 | 565 | 12.33 | 12.21 | 565 | 12.33 | 12.21 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {76ACE992-584D-4749-8E83-9A9B7A149823}
4765 | 3854 | {E8FE8E28-671D-11E5-80CA-005056A729E5} | KERN | MC FARLAND | Bank 2 | CB 1104 | PGE\BXYD | 2016-11-01 11:01:22.8303538 -07:00 | 2531801104 | 254211102 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {3F7198A1-69B5-4702-9571-5410C7A3B7EC}
4766 | 3854 | {E8FE8E30-671D-11E5-80CA-005056A729E5} | KERN | MC FARLAND | Bank 2 | CB 1105 | PGE\BXYD | 2016-11-01 11:02:20.6607705 -07:00 | 2531801105 | 252771101 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {F4BAD3BE-6128-4CD3-91AB-52030E3D45AF}
4767 | 3855 | {E8FE8DFA-671D-11E5-80CA-005056A729E5} | KERN | MARICOPA | Bank 1 | CB 1101 (Non-SCADA) | PGE\BXYD | 2016-11-01 11:27:27.3921752 -07:00 | 2542101101 | 252771104 | 8 | 3 | 3 | 1 | 512 | 11.17 | 11.06 | 512 | 11.17 | 11.06 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 512 | 666 | 615 | 769 | {F45BD41F-70EC-4DA9-BCD9-149A260ECFE4}
4768 | 3855 | {E8FE8E03-671D-11E5-80CA-005056A729E5} | KERN | MARICOPA | Bank 1 | CB 1102 (Non-SCADA) | PGE\BXYD | 2016-11-01 11:28:38.9602968 -07:00 | 2542101102 | 252771105 | 8 | 3 | 3 | 1 | 512 | 11.17 | 11.06 | 512 | 11.17 | 11.06 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 512 | 666 | 615 | 769 | {4CC51D49-2EA7-47D2-89F6-BFC021AC3DC7}
4769 | 3856 | {E3005A85-671D-11E5-80CA-005056A729E5} | KERN | MAGUNDEN | Bank 1 | CB 1101 | PGE\BXYD | 2016-11-01 11:42:57.3314325 -07:00 | 2527701101 | 252771106 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F683C075-1B84-47E7-87EE-40B6F925D271}
4770 | 3856 | {E3005A90-671D-11E5-80CA-005056A729E5} | KERN | MAGUNDEN | Bank 1 | CB 1104 | PGE\BXYD | 2016-11-01 11:45:42.7371576 -07:00 | 2527701104 | 252771108 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {404D21F6-4AD3-4956-A226-0A8AB76BE6F2}
4771 | 3856 | {E3005A95-671D-11E5-80CA-005056A729E5} | KERN | MAGUNDEN | Bank 1 | CB 1105 | PGE\BXYD | 2016-11-01 11:48:09.0209555 -07:00 | 2527701105 | 103271101 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 666 | 14.53 | 14.38 | 666 | 14.53 | 14.38 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {43F9433B-9977-4342-9802-DC8B4315A7FE}
4772 | 3856 | {E3005A9D-671D-11E5-80CA-005056A729E5} | KERN | MAGUNDEN | Bank 1 | CB 1106 | PGE\BXYD | 2016-11-01 11:49:45.6308441 -07:00 | 2527701106 | 252772108 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {1C4469BE-B69F-4CE6-A460-D0A9B3485C70}
4773 | 3856 | {E8FE8DAF-671D-11E5-80CA-005056A729E5} | KERN | MAGUNDEN | Bank 1 | CB 1108 | PGE\BXYD | 2016-11-01 11:50:57.5985673 -07:00 | 2527701108 | 252772109 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B525AB8A-FC61-4729-BBF3-C1433DFF91E5}
4774 | 3853 | {7A8F24F9-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | ANTLER | Bank 1 | CB 1101 | PGE\JXF8 | 2016-11-01 11:55:22.8908573 -07:00 | 1032701101 | 192021124 | 8 | 4 | 4 | 2 | 250 | 5.2 | 5.15 | 250 | 5.2 | 5.15 | 250 | 5.2 | 5.15 | 250 | 5.2 | 5.15 | 250 | 5.2 | 5.15 | 250 | 5.2 | 5.15 | 250 | 5.2 | 5.15 | 250 | 5.2 | 5.15 |  |  | FALSE | FALSE | 606 | 722 | 722 | 722 | {2FE67684-E55F-46A1-B546-086A833C2E4C}
4776 | 3857 | {E8FE8DBD-671D-11E5-80CA-005056A729E5} | KERN | MAGUNDEN | Bank 3 | CB 2108 | PGE\BXYD | 2016-11-07 08:30:46.7330472 -08:00 | 2527702108 | 102211101 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {F6BB6C9C-DF38-40FE-BBDF-8EB454A51C18}
4777 | 3857 | {E8FE8DE6-671D-11E5-80CA-005056A729E5} | KERN | MAGUNDEN | Bank 3 | CB 2109 | PGE\BXYD | 2016-11-07 08:31:00.0094982 -08:00 | 2527702109 | 102211102 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {8796988C-1D64-4D08-B5BB-6DECB21B780E}
4781 | 1060 | {CF0BE2DF-0E4A-11E6-95F2-D4BED91EFF1A} | HUMBOLDT | ARCATA | BANK 2 | CB 1124 | PGE\C8M4 | 2017-08-02 14:46:59.4706307 -07:00 | 1920201124 | 253491103 | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 552 | 12.05 | 11.93 | 656 | 14.32 | 14.18 | 623 | 13.6 | 13.46 | 666 | 14.53 | 14.38 | 632 | 13.79 | 13.65 | 711 | 15.52 | 15.36 | 675 | 14.73 | 14.58 | 1124 is used to carry other feeders and will have identical capability as the circuit is being picked up. |  | FALSE | TRUE | 1374 | 1787 | 1649 | 2000 | {9AE804D3-E9BA-4A27-822F-1858B07FA079}
4782 | 3860 | {80988F6A-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | BUCKS CREEK | Bank 4 | CB 1101 | PGE\SDK6 | 2017-01-24 13:53:51.6339084 -08:00 | 1022101101 | 253491104 | 8 | 3 | 3 | 1 | 70 | 1.53 | 1.51 | 66 | 1.44 | 1.43 | 78 | 1.7 | 1.68 | 74 | 1.61 | 1.59 | 84 | 1.83 | 1.81 | 79 | 1.72 | 1.7 | 92 | 2.01 | 1.99 | 87 | 1.9 | 1.88 |  |  | TRUE | FALSE | 153 | 153 | 153 | 153 | {00000000-0000-0000-0000-000000000000}
4783 | 2643 | {0D207778-9B9A-11E6-841B-D4BED91EFF1A} | SACRAMENTO | VACA DIXON | Bank 8 | CB 1108 | PGE\TEJ2 | 2016-11-01 13:53:01.7240600 -07:00 |  | 253491105 | 8 | 3 | 3 | 1 | 228 | 4.98 | 4.93 | 228 | 4.98 | 4.93 | 318 | 6.94 | 6.87 | 318 | 6.94 | 6.87 | 277 | 6.05 | 5.99 | 277 | 6.05 | 5.99 | 335 | 7.31 | 7.24 | 335 | 7.31 | 7.24 | This circuit ties to the BESS 2 MW battery charging / discharging system. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {B0DE559F-8086-40D1-A16E-3A3A2D90BCB0}
4786 | 3860 | {80988F73-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | BUCKS CREEK | Bank 4 | CB 1102 | PGE\SDK6 | 2017-01-24 13:54:13.8175350 -08:00 | 1022101102 | 102211103 | 8 | 3 | 3 | 1 | 121 | 2.64 | 2.61 | 114 | 2.49 | 2.47 | 130 | 2.84 | 2.81 | 128 | 2.79 | 2.76 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 |  |  | TRUE | FALSE | 153 | 153 | 153 | 153 | {A0041E0E-AFDC-4BF4-BA62-7E34D764B18D}
4787 | 3862 | {E3005A46-671D-11E5-80CA-005056A729E5} | KERN | LERDO | Bank 1 (Non SCADA) | CB 1103 (Non-SCADA) | PGE\BXYD | 2016-11-01 13:58:22.5278370 -07:00 | 2534901103 | 024251101 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F506B27F-76E1-499D-BBDC-99E9D0E360FF}
4788 | 3862 | {E3005A52-671D-11E5-80CA-005056A729E5} | KERN | LERDO | Bank 1 (Non SCADA) | CB 1104 (Non-SCADA) | PGE\BXYD | 2016-11-01 13:59:54.4564548 -07:00 | 2534901104 | 024251102 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {5F4C6C65-60D6-4E6F-9320-002195D5EF53}
4789 | 3862 | {E3005A58-671D-11E5-80CA-005056A729E5} | KERN | LERDO | Bank 1 (Non SCADA) | CB 1105 (Non-SCADA) | PGE\BXYD | 2016-11-01 14:01:01.2920856 -07:00 | 2534901105 | 024251104 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {790ADDD1-F3CF-4136-91EC-5CB8B1138423}
4790 | 3860 | {80988F7C-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | BUCKS CREEK | Bank 4 | CB 1103 | PGE\SDK6 | 2017-01-26 08:39:14.4202969 -08:00 | 1022101103 | 253491106 | 8 | 3 | 3 | 1 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 |  |  | TRUE | FALSE | 137 | 141 | 141 | 141 | {1A646B4A-80F0-4011-B535-F9B2032B63AC}
4791 | 3858 | {2C77CD1F-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | WOODSIDE | Bank 1 (Non SCADA) | CB 1101 | PGE\C7CF | 2016-11-01 14:11:05.7597962 -07:00 | 0242501101 | 253491107 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {BAF21668-5258-4AC9-A632-4D59DC420D43}
4792 | 3858 | {32E43829-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | WOODSIDE | Bank 1 (Non SCADA) | CB 1102 | PGE\C7CF | 2016-11-01 14:14:40.7244008 -07:00 | 0242501102 | 253491108 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {8D24BD3D-226A-4C36-A11D-4FE42B4594FE}
4793 | 3859 | {8AE3F426-3E2B-11E6-A936-80000BC6CD8D} | PENINSULA | WOODSIDE | Bank 2 (Non SCADA) | CB 1104 (SW-TBD) (Non-SCADA) | PGE\C7CF | 2016-11-01 14:20:07.0256893 -07:00 | 024251104 | 253491109 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {797F7E54-C010-4041-9B7A-01567B9A7956}
4794 | 3863 | {E3005A61-671D-11E5-80CA-005056A729E5} | KERN | LERDO | Bank 2 (Non SCADA) | CB 1106 (Non-SCADA) | PGE\BXYD | 2016-11-01 14:22:46.6139221 -07:00 | 2534901106 | 062041101 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {EB89C591-EC3A-4011-B621-91BFED71F0E2}
4795 | 3863 | {E3005A6D-671D-11E5-80CA-005056A729E5} | KERN | LERDO | Bank 2 (Non SCADA) | CB 1107 (Non-SCADA) | PGE\BXYD | 2016-11-01 14:24:41.2194673 -07:00 | 2534901107 | 253911102 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {CEF348AE-AE67-4FB6-AD0A-BDE3A32348F1}
4796 | 3863 | {E3005A73-671D-11E5-80CA-005056A729E5} | KERN | LERDO | Bank 2 (Non SCADA) | CB 1108 (Non-SCADA) | PGE\BXYD | 2016-11-01 14:27:15.2351746 -07:00 | 2534901108 | 253911103 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {6D35F83C-2338-46F7-9051-BF297B392B41}
4797 | 3863 | {E3005A79-671D-11E5-80CA-005056A729E5} | KERN | LERDO | Bank 2 (Non SCADA) | CB 1109 (Non-SCADA) | PGE\BXYD | 2016-11-01 14:28:36.7195585 -07:00 | 2534901109 | 022850402 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {E3B44DF6-F79E-48F8-ADA3-14E016ED7504}
4798 | 2574 | {E9AF3BFE-235B-11E6-B38D-D4BED91EFF1A} | SACRAMENTO | DAVIS | Bank 1 | CB 1101 | PGE\TEJ2 | 2016-11-01 14:30:16.8815708 -07:00 | 0620401101 | 253911104 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 689 | 15.04 | 14.89 | 689 | 15.04 | 14.89 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 732 | 15.98 | 15.82 | 732 | 15.98 | 15.82 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {84A88DCD-1201-436F-BD08-86EF0461814E}
4799 | 3865 | {E30059D8-671D-11E5-80CA-005056A729E5} | KERN | LAMONT | Bank 1 | CB 1102 (Non-SCADA) | PGE\APE3 | 2017-03-10 13:20:34.1509780 -08:00 | 2539101102 | 253911105 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {5F97AE2B-0E49-434E-8C91-DEB38EA13A7A}
4800 | 3865 | {E30059EA-671D-11E5-80CA-005056A729E5} | KERN | LAMONT | Bank 1 | CB 1103 (Non-SCADA) | PGE\APE3 | 2017-03-10 13:19:55.8678418 -08:00 | 2539101103 | 253911106 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {4BEDEAC4-75DE-4AA5-9E45-866A40469A28}
4801 | 3864 | {2C77CCFB-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SULLIVAN | Bank 402 (Non SCADA) | CB 402 (Non-SCADA) | PGE\C7CF | 2016-11-01 14:36:44.9592323 -07:00 | 02285402 | 063131104 | 4 | 3 | 3 | 2 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 396 | 3 | 2.97 | 396 | 3 | 2.97 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {20919ABF-12AB-4774-8D7F-4AE9E93BCA5A}
4802 | 3865 | {E30059F9-671D-11E5-80CA-005056A729E5} | KERN | LAMONT | Bank 1 | CB 1104 (Non-SCADA) | PGE\APE3 | 2017-03-10 13:22:12.4172677 -08:00 | 2539101104 | 254201103 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {D1D88072-5B89-4D8A-BC8B-97DE88A4DAA3}
4803 | 3869 | {9F082D3B-0B43-11E6-9D37-D4BED91EFF1A} | KERN | LAMONT | BANK 3 (Non SCADA) | CB 1105 (Non-SCADA) | PGE\APE3 | 2017-03-10 13:23:39.3889402 -08:00 | 2539101105 | 254202104 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {D04CC17D-A17A-40C0-929E-099A38246F1F}
4804 | 3869 | {97762D00-0B43-11E6-9D37-D4BED91EFF1A} | KERN | LAMONT | BANK 3 (Non SCADA) | CB 1106 (Non-SCADA) | PGE\BXYD | 2016-11-01 14:46:33.3972797 -07:00 | 2539101106 | 062031113 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {1B8A9152-8639-4712-B5BD-EC712F2FC67B}
4805 | 3866 | {812C0570-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WEST SACRAMENTO | Bank 1 | CB 1104 | PGE\TEJ2 | 2016-11-01 14:48:13.0046019 -07:00 | 0631301104 | 062031101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {D162C832-B137-4F71-8540-30E095574021}
4838 | 3883 | {E30058DB-671D-11E5-80CA-005056A729E5} | KERN | GOOSE LAKE | Bank 1 (Non SCADA) | CB 1103 (Non-SCADA) | PGE\KWG0 | 2016-11-02 08:41:25.9813487 -07:00 | 2542001103 | 062031102 | 8 | 3 | 3 | 1 | 345 | 7.53 | 7.45 | 345 | 7.53 | 7.45 | 386 | 8.42 | 8.34 | 386 | 8.42 | 8.34 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {E168FCAD-3CFA-47B0-A22F-8EEFFAD23933}
4839 | 3883 | {E30058E1-671D-11E5-80CA-005056A729E5} | KERN | GOOSE LAKE | Bank 1 (Non SCADA) | CB 2104 (Non-SCADA) | PGE\KWG0 | 2016-11-02 08:45:18.0686449 -07:00 | 2542002104 | 062031103 | 8 | 3 | 3 | 1 | 345 | 7.53 | 7.45 | 345 | 7.53 | 7.45 | 386 | 8.42 | 8.34 | 386 | 8.42 | 8.34 | 443 | 9.67 | 9.57 | 443 | 9.67 | 9.57 | 473 | 10.32 | 10.22 | 473 | 10.32 | 10.22 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {827AD063-D292-4BEA-B6D8-C000061BFC3B}
4840 | 3884 | {872F7D65-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WOODLAND | Bank 1 | CB 1113 | PGE\TEJ2 | 2016-11-02 08:59:06.6892857 -07:00 | 0620301113 | 062031104 | 8 | 3 | 3 | 1 | 745 | 16.26 | 16.1 | 745 | 16.26 | 16.1 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {DE61EF7B-E62B-489D-83AA-972F0536E9CF}
4841 | 3884 | {872F7D3C-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WOODLAND | Bank 1 | CB 1101 | PGE\TEJ2 | 2016-11-02 09:09:52.8525634 -07:00 | 0620301101 | 062031105 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {232C4CC3-0FE0-45CD-BF62-A2891D51F164}
4842 | 3884 | {872F7D53-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WOODLAND | Bank 1 | CB 1102 | PGE\TEJ2 | 2016-11-02 09:21:37.0033078 -07:00 | 0620301102 | 062031106 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {137CBCE4-7129-4519-8D3E-DB13B94FD9CB}
4843 | 3884 | {872F7D5C-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WOODLAND | Bank 1 | CB 1103 | PGE\TEJ2 | 2016-11-02 09:40:29.8081684 -07:00 | 0620301103 | 062031107 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {5D5447F6-3A26-4C34-A9A2-750A9A745E15}
4845 | 3885 | {872F7D86-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WOODLAND | Bank 2 | CB 1104 | PGE\TEJ2 | 2016-11-02 09:56:57.6987232 -07:00 | 0620301104 | 062031108 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {AFA5BB55-3560-41E3-ABED-0B4C8A09F440}
4847 | 3885 | {872F7D90-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WOODLAND | Bank 2 | CB 1105 | PGE\JMB4 | 2017-05-15 14:54:30.4325583 -07:00 | 0620301105 | 062031109 | 8 | 3 | 3 | 1 | 700 | 15.28 | 15.13 | 566 | 12.35 | 12.23 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 600 | 13.09 | 12.96 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {2D88CC87-6F2D-4A31-A9DF-7F0A09DDF165}
4848 | 3885 | {872F7DA7-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WOODLAND | Bank 2 | CB 1106 | PGE\TEJ2 | 2016-11-02 10:15:09.7249240 -07:00 | 0620301106 | 062031110 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {145D965D-5394-4FA9-BDCC-259BAACD7DED}
4849 | 3885 | {872F7DBE-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WOODLAND | Bank 2 | CB 1107 | PGE\TEJ2 | 2016-11-02 10:23:15.4167416 -07:00 | 0620301107 | 062031111 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {2F275E26-ED55-4F85-98EE-75468A80FEA6}
4850 | 3885 | {872F7DCE-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WOODLAND | Bank 2 | CB 1108 | PGE\TEJ2 | 2016-11-02 10:30:39.2065573 -07:00 | 0620301108 | 062031112 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {820A3496-75FE-4238-B6DB-C8C57DC65AAD}
4851 | 3886 | {872F7DE8-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WOODLAND | Bank 3 | CB 1109 | PGE\TEJ2 | 2016-11-02 10:38:28.8501197 -07:00 | 0620301109 | 022470401 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {A401719D-545E-441D-9BC8-D4DD9BEDA2DB}
4852 | 3886 | {872F7DF8-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WOODLAND | Bank 3 | CB 1110 | PGE\TEJ2 | 2016-11-02 10:57:52.9457719 -07:00 | 0620301110 | 022470402 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {6E6A8E5A-67C2-4275-9B32-823E97C6D100}
4853 | 3886 | {872F7E08-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WOODLAND | Bank 3 | CB 1111 | PGE\TEJ2 | 2016-11-02 11:07:07.8690401 -07:00 | 0620301111 | 022510401 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {80B06F29-DC21-4409-A88E-33F9C22CB2C1}
4854 | 3886 | {872F7E11-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WOODLAND | Bank 3 | CB 1112 | PGE\TEJ2 | 2016-11-02 11:20:59.4128345 -07:00 | 0620301112 | 022510402 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9F73BF98-8970-44E8-B281-49ACA25D12B2}
4855 | 3887 | {6658551C-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | ACTON | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\DMAL | 2017-05-12 20:54:31.2217281 -07:00 | 022470401 | 254501103 | 3 | 3 | 3 | 2 | 277 | 2 | 1.98 | 277 | 2 | 1.98 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 382 | 2.75 | 2.72 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 277 | 360 | 333 | 416 | {9B840CED-D4F9-40BA-981B-2DD41B3C5E26}
4856 | 3888 | {66585522-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | ACTON | Bank 2 (Non SCADA) | CB 402 (Non-SCADA) | PGE\DMAL | 2017-05-12 20:54:11.2840335 -07:00 | 022470402 | 162370402 | 3 | 3 | 3 | 2 | 277 | 2 | 1.98 | 277 | 2 | 1.98 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 277 | 360 | 333 | 416 | {82544C23-B40B-4F45-98A1-7355592EF2E4}
4857 | 3889 | {9402A8A3-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | NORIEGA | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\DMAL | 2017-05-12 21:04:37.8081455 -07:00 | 022510401 | 162370403 | 3 | 3 | 3 | 2 | 346 | 2.49 | 2.47 | 346 | 2.49 | 2.47 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 346 | 451 | 416 | 520 | {D9AC7902-E97B-44B4-9C43-8D6FFFECC2C8}
4858 | 3891 | {9402A8AB-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | NORIEGA | Bank 2 (Non SCADA) | CB 402 (Non-SCADA) | PGE\DMAL | 2017-05-12 21:07:56.4362579 -07:00 | 022510402 | 162370412 | 3 | 3 | 3 | 2 | 346 | 2.49 | 2.47 | 346 | 2.49 | 2.47 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 368 | 2.65 | 2.62 | 368 | 2.65 | 2.62 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 346 | 451 | 416 | 520 | {601F49F2-E11E-4669-BA4D-8A851A98C45E}
4859 | 3882 | {DD06430B-671D-11E5-80CA-005056A729E5} | KERN | CHARCA | Bank 1 | CB 1103 | PGE\JWCp | 2016-11-03 11:01:51.0653689 -07:00 | 2545001103 | 013090401 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 1844 | {123D828F-542C-4596-A034-E03E2115A19D}
4860 | 3890 | {464AB094-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 2 (Non SCADA) | CB A402 (Non-SCADA) | PGE\SZC1 | 2017-03-07 14:30:40.0961389 -08:00 | 162370402 | 013090402 | 3 | 3 | 3 | 1 | 300 | 2.16 | 2.14 | 285 | 2.05 | 2.03 | 326 | 2.35 | 2.33 | 326 | 2.35 | 2.33 | 311 | 2.24 | 2.22 | 311 | 2.24 | 2.22 | 336 | 2.42 | 2.4 | 336 | 2.42 | 2.4 |  |  | TRUE | FALSE | 1553 | 2018 | 1863 | 2163 | {904B602F-37EE-4AD3-B28F-2D3D79FCAEDF}
4861 | 3890 | {92A1D4D9-DCC9-11E5-83B3-2016D89D35F7} | STOCKTON | STOCKTON A | Bank 2 (Non SCADA) | CB A403 (Non-SCADA) | PGE\SZC1 | 2016-11-02 16:43:04.4790830 -07:00 | 162370403 | 083500402 | 3 | 3 | 3 | 1 | 600 | 4.32 | 4.28 | 570 | 4.11 | 4.07 | 600 | 4.32 | 4.28 | 570 | 4.11 | 4.07 | 600 | 4.32 | 4.28 | 570 | 4.11 | 4.07 | 600 | 4.32 | 4.28 | 570 | 4.11 | 4.07 |  |  | TRUE | FALSE | 1553 | 2018 | 1863 | 2163 | {2C3E4EA0-E317-4AE9-9B53-71C178634CEF}
4862 | 3890 | {AAE22B47-DCC9-11E5-83B3-2016D89D35F7} | STOCKTON | STOCKTON A | Bank 2 (Non SCADA) | CB A412 (Non-SCADA) | PGE\SZC1 | 2016-11-04 08:34:51.4798221 -07:00 | 162370412 | 152011102 | 3 | 3 | 3 | 1 | 600 | 4.32 | 4.28 | 570 | 4.11 | 4.07 | 600 | 4.32 | 4.28 | 570 | 4.11 | 4.07 | 600 | 4.32 | 4.28 | 570 | 4.11 | 4.07 | 600 | 4.32 | 4.28 | 570 | 4.11 | 4.07 |  |  | TRUE | FALSE | 1553 | 2018 | 1863 | 2163 | {3354C477-6D9B-4B55-A719-1BDC9F4A1723}
4864 | 3899 | {D3B6EE8E-0E48-11E6-95F2-D4BED91EFF1A} | DIABLO | BRYANT | UNIT SUB 401 (Non SCADA) | CB 401 (Non-SCADA) | PGE\MFN3 | 2016-11-23 14:24:02.9504370 -08:00 | 013090401 | 152011103 | 4 | 3 | 1 | 1 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 361 | 2.73 | 2.7 | 361 | 2.73 | 2.7 | 361 | 2.73 | 2.7 | 361 | 2.73 | 2.7 | 361 | 2.73 | 2.7 | 361 | 2.73 | 2.7 |  |  | FALSE | FALSE | 303 | 361 | 361 | 361 | {58793C1B-4E06-43D0-A36F-42320DA5B6FD}
4866 | 3900 | {CB3A2E90-0E48-11E6-95F2-D4BED91EFF1A} | DIABLO | BRYANT | UNIT SUB 402 (Non SCADA) | CB 402 (Non-SCADA) | PGE\MFN3 | 2016-11-23 14:24:52.0634063 -08:00 | 013090402 | 152011104 | 4 | 3 | 1 | 1 | 264 | 2 | 1.98 | 264 | 2 | 1.98 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 317 | 2.4 | 2.38 | 317 | 2.4 | 2.38 | 350 | 2.65 | 2.62 | 350 | 2.65 | 2.62 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {E229DCA9-00A5-42C3-81EE-EE7EF48A4859}
4868 | 3902 | {EA1DF6CE-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SEACLIFF | Bank 2 (Non SCADA) | CB 402 (Non-SCADA) | PGE\ACT0 | 2016-11-03 10:59:27.9416803 -07:00 | 083500402 | 152011105 | 4 | 3 | 3 | 2 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 429 | 3.25 | 3.22 | 429 | 3.25 | 3.22 | 396 | 3 | 2.97 | 396 | 3 | 2.97 | 495 | 3.75 | 3.71 | 495 | 3.75 | 3.71 |  |  | FALSE | FALSE | 330 | 429 | 396 | 495 | {D0D9B7DD-BF22-4CC8-8761-E2488D4706FC}
4870 | 3903 | {620DC93E-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | MARYSVILLE | Bank 3 | CB 1102 | PGE\TEJ2 | 2016-11-03 09:29:19.9824226 -07:00 | 1520101102 | 152011106 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {0175C542-4973-4CEC-8458-86910F25BDEC}
4871 | 3903 | {620DC947-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | MARYSVILLE | Bank 3 | CB 1103 | PGE\TEJ2 | 2016-11-03 09:36:38.4368108 -07:00 | 1520101103 | 152011107 | 8 | 3 | 3 | 1 | 325 | 7.09 | 7.02 | 325 | 7.09 | 7.02 | 363 | 7.92 | 7.84 | 363 | 7.92 | 7.84 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {E042E64A-B808-4C47-834C-7D74ACA73BE7}
4872 | 3903 | {620DC957-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | MARYSVILLE | Bank 3 | CB 1104 | PGE\TEJ2 | 2016-11-03 09:41:31.8652199 -07:00 | 1520101104 | 152011108 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {2AC77AC8-8379-4B6E-AD3D-F59B6A5E23E8}
4873 | 3903 | {620DC960-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | MARYSVILLE | Bank 3 | CB 1105 | PGE\TEJ2 | 2016-11-03 09:45:39.0993066 -07:00 | 1520101105 | 024190409 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {5F1AD55B-6B07-4968-9D10-9AC69F77E7B1}
4875 | 3904 | {620DC912-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | MARYSVILLE | Bank 1 | CB 1106 | PGE\TEJ2 | 2016-11-03 09:56:39.8558065 -07:00 | 1520101106 | 024190410 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {C0E7E409-3E8C-4A8A-8354-414D6C527FFB}
4876 | 3904 | {620DC91B-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | MARYSVILLE | Bank 1 | CB 1107 | PGE\TEJ2 | 2016-11-03 10:03:57.5963697 -07:00 | 1520101107 | 182051114 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 700 Al tie to Marysville 1106, source of switch 16215. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {5071A6A7-3306-46A2-81A8-04A37398E2EF}
4877 | 3904 | {620DC924-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | MARYSVILLE | Bank 1 | CB 1108 | PGE\TEJ2 | 2016-11-03 10:07:54.8577412 -07:00 | 1520101108 | 182052101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {39646DF9-ECB2-4601-9DDA-812AC9E3C3A6}
4879 | 3880 | {2C77C984-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SAN MATEO | Bank 4 | CB 409 | PGE\C7CF | 2016-11-03 10:12:38.5916103 -07:00 | 02419409 | 182052102 | 4 | 3 | 3 | 2 | 409 | 3.1 | 3.07 | 409 | 3.1 | 3.07 | 474 | 3.59 | 3.55 | 474 | 3.59 | 3.55 | 417 | 3.16 | 3.13 | 417 | 3.16 | 3.13 | 483 | 3.66 | 3.62 | 483 | 3.66 | 3.62 |  |  | FALSE | FALSE | 1238 | 1610 | 1486 | 1857 | {A2A99DB4-4218-43D5-820E-3BC59DBFE72B}
4880 | 3880 | {2C77C98D-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SAN MATEO | Bank 4 | CB 410 | PGE\C7CF | 2016-11-03 10:17:13.1936052 -07:00 | 024190410 | 254501106 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 1238 | 1610 | 1486 | 1857 | {7ED4653B-CDD2-4FF9-9F6B-F0DF750B25D9}
4881 | 3906 | {F35D7381-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SOLEDAD | Bank 2 | CB 1114 (SW-TBD) (Non-SCADA) | PGE\MTDR | 2017-07-13 08:59:06.6087107 -07:00 | 1820501114 | 063642102 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {5FEFDE29-8883-4BE4-A705-AC3EA059014D}
4882 | 3909 | {F35D7393-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SOLEDAD | Bank 3 | CB 2101 | PGE\ACT0 | 2016-11-03 10:43:11.8154627 -07:00 | 1820502101 | 024180401 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {15BD09C4-8E31-4CD7-B94A-FAC959A7A4EF}
4883 | 3909 | {F35D73A4-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SOLEDAD | Bank 3 | CB 2102 | PGE\ACT0 | 2016-11-03 10:53:45.8522728 -07:00 | 1820502102 | 063642104 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {51CCAADB-593C-4309-9828-88E860077933}
4885 | 3892 | {DD06431F-671D-11E5-80CA-005056A729E5} | KERN | CHARCA | Bank 2 | CB 1106 (Non-SCADA) | PGE\JWCp | 2016-11-03 11:13:01.2591600 -07:00 | 2545001106 | 063642105 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {B96C4DD6-1E18-4AF6-BD9B-7D08F1EBDDFA}
4886 | 3908 | {68EB4C92-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PEABODY | Bank 1 | CB 2102 | PGE\TEJ2 | 2016-11-03 11:15:05.4510942 -07:00 | 0636402102 | 063642106 | 12 | 3 | 3 | 1 | 745 | 28.16 | 27.88 | 745 | 28.16 | 27.88 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {D32F1AA6-B011-47FF-A6C6-9961015A8E31}
4887 | 3907 | {2C77C8C5-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SAN CARLOS | Bank 1 | CB 401 (Non-SCADA) | PGE\C7CF | 2017-06-08 18:04:14.7790105 -07:00 | 024180401 | 063642107 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 433 | 3.28 | 3.25 | 433 | 3.28 | 3.25 |  |  | FALSE | FALSE | 1664 | 2164 | 1997 | 2497 | {03C8E830-BD08-48D5-994B-077B6FF420CF}
4888 | 3908 | {68EB4CB0-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PEABODY | Bank 1 | CB 2104 | PGE\TEJ2 | 2016-11-03 11:25:33.8049816 -07:00 | 0636402104 | 024180402 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {1616A105-BCE2-434F-AA61-7076AF7AE852}
4889 | 3908 | {68EB4CE3-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PEABODY | Bank 1 | CB 2105 | PGE\TEJ2 | 2016-11-03 11:29:15.1860456 -07:00 | 0636402105 | 024180403 | 12 | 3 | 3 | 1 | 650 | 24.57 | 24.32 | 650 | 24.57 | 24.32 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {90B16A52-F6B2-478A-8625-CB9A8F0C7101}
4891 | 3910 | {68EB4D3C-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PEABODY | Bank 2 | CB 2106 | PGE\TEJ2 | 2016-11-03 12:14:05.1476166 -07:00 | 0636402106 | 063642108 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1587 | 2063 | 1905 | 2381 | {3B5C1F2D-5E3D-47D9-BD31-631DA37FD7AA}
4892 | 3910 | {68EB4D5A-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PEABODY | Bank 2 | CB 2107 | PGE\TEJ2 | 2016-11-03 12:12:20.5074880 -07:00 | 0636402107 | 024180404 | 12 | 3 | 3 | 1 | 650 | 24.57 | 24.32 | 650 | 24.57 | 24.32 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1587 | 2063 | 1905 | 2381 | {C7DE587B-0B94-4AB1-9A63-7C7DEA800968}
4893 | 3907 | {2C77C8CF-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SAN CARLOS | Bank 1 | CB 402 (Non-SCADA) | PGE\C7CF | 2017-06-08 17:57:02.2707485 -07:00 | 024180402 | 063642109 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 1664 | 2164 | 1997 | 2497 | {7CA6CAED-37F6-4CF6-8936-530E7580B918}
4894 | 3907 | {2C77C8D9-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SAN CARLOS | Bank 1 | CB 403 (Non-SCADA) | PGE\C7CF | 2017-06-08 18:05:11.0032125 -07:00 | 024180403 | 024180405 | 4 | 3 | 3 | 2 | 200 | 1.51 | 1.49 | 200 | 1.51 | 1.49 | 260 | 1.97 | 1.95 | 260 | 1.97 | 1.95 | 240 | 1.82 | 1.8 | 240 | 1.82 | 1.8 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 |  |  | FALSE | FALSE | 1664 | 2164 | 1997 | 2497 | {0671B64C-3236-4B15-8431-D0E3D06726CB}
4895 | 3910 | {68EB4DE1-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PEABODY | Bank 2 | CB 2108 | PGE\TEJ2 | 2016-11-03 13:14:24.5989503 -07:00 | 0636402108 | 024180406 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1587 | 2063 | 1905 | 2381 | {10495D0B-097B-4420-9DEA-1F5AADEECD11}
4896 | 3907 | {2C77C8DC-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SAN CARLOS | Bank 1 | CB 404 (Non-SCADA) | PGE\C7CF | 2017-06-08 18:06:50.2379930 -07:00 | 024180404 | 024181102 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 1664 | 2164 | 1997 | 2497 | {A4D42F38-07B6-4FF2-9117-D19683E189BC}
4897 | 3910 | {A737996F-2360-11E6-B38D-D4BED91EFF1A} | SACRAMENTO | PEABODY | Bank 2 | CB 2109 | PGE\TEJ2 | 2016-11-03 13:25:34.7488109 -07:00 | 0636402109 | 024181104 | 12 | 3 | 3 | 1 | 463 | 17.5 | 17.32 | 463 | 17.5 | 17.32 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | Gen tie feeder, Potrero Hills Land Fill 8 MW generation. |  | FALSE | FALSE | 1587 | 2063 | 1905 | 2381 | {50D1F357-27EB-446B-9C5A-FE399CC2004B}
4899 | 3907 | {2C77C8DF-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SAN CARLOS | Bank 1 | CB 405 (Non-SCADA) | PGE\C7CF | 2016-11-03 13:31:44.0121551 -07:00 | 024180405 | 024181101 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 1664 | 2164 | 1997 | 2497 | {3A27E57B-D855-450D-8AAA-CB5CBE1FE746}
4900 | 3907 | {2C77C8E2-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SAN CARLOS | Bank 1 | CB 406 (Non-SCADA) | PGE\C7CF | 2017-06-08 18:10:22.9976120 -07:00 | 024180406 | 063642112 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 417 | 3.16 | 3.13 | 417 | 3.16 | 3.13 |  |  | FALSE | FALSE | 1664 | 2164 | 1997 | 2497 | {68088749-5019-4BF3-A0BF-75C721265F5D}
4901 | 3912 | {2C77C8EF-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SAN CARLOS | Bank 2 | CB 1102 | PGE\C7CF | 2016-11-03 13:47:45.3341736 -07:00 | 0241801102 | 024181103 | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 582 | 12.7 | 12.57 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {7297672D-BF95-4151-94DF-BE8C664028DD}
4902 | 3912 | {2C77C8F8-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SAN CARLOS | Bank 2 | CB 1104 | PGE\C7CF | 2016-11-03 13:52:05.6023638 -07:00 | 0241801104 | 063642113 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {FB66657A-D7B2-452B-A8CB-FF5E9E097CAF}
4903 | 3913 | {2C77C92E-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SAN CARLOS | Bank 3 | CB 1101 | PGE\C7CF | 2016-11-03 14:08:04.6681827 -07:00 | 0241801101 | 022700401 | 8 | 3 | 3 | 2 | 560 | 12.22 | 12.1 | 560 | 12.22 | 12.1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {2FCFB3A7-7925-4B89-8B15-92EB2B6C708E}
4904 | 3911 | {68EB4E11-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PEABODY | Bank 3 | CB 2112 | PGE\TEJ2 | 2016-11-03 14:10:02.1053706 -07:00 | 0636402112 | 083300402 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {830898FD-0552-4BA6-B331-1586C930E4E3}
4905 | 3913 | {2C77C937-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SAN CARLOS | Bank 3 | CB 1103 | PGE\C7CF | 2016-11-03 14:11:34.1814596 -07:00 | 0241801103 | 022700402 | 8 | 3 | 3 | 2 | 572 | 12.48 | 12.36 | 572 | 12.48 | 12.36 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {52A43419-1488-4B96-AB3C-C8F964A65225}
4906 | 3911 | {68EB4E59-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PEABODY | Bank 3 | CB 2113 | PGE\TEJ2 | 2016-11-03 14:15:40.4014923 -07:00 | 0636402113 | 022700403 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {E2DAB969-3786-430E-9C92-19B0BEA8E0D8}
4907 | 3914 | {2C77C8A9-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SAN BRUNO | Bank 1 | CB 401 | PGE\C7CF | 2016-11-03 14:44:28.9846542 -07:00 | 022700401 | 182201121 | 4 | 3 | 3 | 2 | 224 | 1.7 | 1.68 | 224 | 1.7 | 1.68 | 291 | 2.2 | 2.18 | 291 | 2.2 | 2.18 | 269 | 2.04 | 2.02 | 269 | 2.04 | 2.02 | 336 | 2.54 | 2.51 | 336 | 2.54 | 2.51 |  |  | FALSE | FALSE | 661 | 860 | 794 | 992 | {3AD2AEB7-63FD-4507-B7C0-772EB95D1A7D}
4908 | 3915 | {F96F261E-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SOQUEL | Bank 2 (Non SCADA) | CB 402 (Non-SCADA) | PGE\MTDR | 2017-07-13 09:07:28.2524347 -07:00 | 083300402 | 182201122 | 4 | 3 | 3 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 455 | 3.44 | 3.41 | 455 | 3.44 | 3.41 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {A2BEEBAD-1A05-468E-BB0B-B6FD0402CC60}
4909 | 3914 | {2C77C8B2-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SAN BRUNO | Bank 1 | CB 402 (Non-SCADA) | PGE\C7CF | 2016-11-03 16:23:19.2663947 -07:00 | 022700402 | 182201123 | 4 | 3 | 3 | 2 | 224 | 1.7 | 1.68 | 224 | 1.7 | 1.68 | 291 | 2.2 | 2.18 | 291 | 2.2 | 2.18 | 269 | 2.04 | 2.02 | 269 | 2.04 | 2.02 | 336 | 2.54 | 2.51 | 336 | 2.54 | 2.51 |  |  | FALSE | FALSE | 661 | 860 | 794 | 992 | {75BE0F7D-BB9B-4277-A9CE-A38C1F233973}
4910 | 3914 | {2C77C8B5-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | SAN BRUNO | Bank 1 | CB 403 (Non-SCADA) | PGE\C7CF | 2016-11-03 16:23:05.2258547 -07:00 | 022700403 | 182852201 | 4 | 3 | 3 | 2 | 224 | 1.7 | 1.68 | 224 | 1.7 | 1.68 | 291 | 2.2 | 2.18 | 291 | 2.2 | 2.18 | 269 | 2.04 | 2.02 | 269 | 2.04 | 2.02 | 336 | 2.54 | 2.51 | 336 | 2.54 | 2.51 |  |  | FALSE | FALSE | 661 | 860 | 794 | 992 | {F036BDB0-EBA6-4408-9F0D-462EF2BF957A}
4911 | 1045 | {F96F2627-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SPENCE | Bank 2 | CB 1121 | PGE\ACT0 | 2016-11-03 16:28:16.8130327 -07:00 | 1822001121 | 182852202 | 8 | 3 | 3 | 2 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 577 | 722 | 692 | 722 | {B81A9AC3-A2CE-4624-8E15-208E56C74F00}
4912 | 1045 | {F96F262D-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SPENCE | Bank 2 | CB 1122 | PGE\ACT0 | 2016-11-22 16:22:51.2043301 -08:00 | 1822001122 | 162370404 | 8 | 3 | 3 | 2 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 583 | 12.72 | 12.59 | 583 | 12.72 | 12.59 | 583 | 12.72 | 12.59 | 583 | 12.72 | 12.59 | 583 | 12.72 | 12.59 | 583 | 12.72 | 12.59 |  |  | FALSE | FALSE | 577 | 722 | 692 | 722 | {54A03C08-92E5-4254-BE56-EDDF5AC29A34}
4913 | 1045 | {F96F2636-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | SPENCE | Bank 2 | CB 1123 | PGE\ACT0 | 2016-11-03 16:33:12.3310819 -07:00 | 1822001123 | 083330411 | 8 | 3 | 3 | 2 | 426 | 9.3 | 9.21 | 426 | 9.3 | 9.21 | 479 | 10.45 | 10.35 | 479 | 10.45 | 10.35 | 482 | 10.52 | 10.41 | 482 | 10.52 | 10.41 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 577 | 722 | 692 | 722 | {3827EB7B-EA00-4265-A4A5-DC8116A14BA1}
4916 | 3920 | {F96F263F-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | VIEJO | Bank 1 | CB 2201 (Under Construction) | PGE\ACT0 | 2016-11-22 16:26:17.8908459 -08:00 | 1828502201 | 083330413 | 11 | 3 | 3 | 2 | 468 | 17.51 | 17.33 | 468 | 17.51 | 17.33 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 528 | 19.75 | 19.55 | 528 | 19.75 | 19.55 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 801 | 916 | 916 | 916 | {58DDED7D-E625-4ED5-92EE-4895500D570D}
4917 | 3920 | {FF9017F1-78E9-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | VIEJO | Bank 1 | CB 2202 (Under Construction) | PGE\ACT0 | 2016-11-04 08:21:36.6244603 -07:00 | 1828502202 | 083330414 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 801 | 916 | 916 | 916 | {9B24C329-7ED9-4406-8FCF-9DC906FB7ACF}
4918 | 3890 | {464AB097-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 2 (Non SCADA) | CB A404 (Non-SCADA) | PGE\SZC1 | 2017-03-07 14:32:51.2790616 -08:00 | 162370404 | 162370405 | 3 | 3 | 3 | 1 | 300 | 2.16 | 2.14 | 285 | 2.05 | 2.03 | 346 | 2.49 | 2.47 | 346 | 2.49 | 2.47 | 321 | 2.31 | 2.29 | 321 | 2.31 | 2.29 | 357 | 2.57 | 2.54 | 357 | 2.57 | 2.54 |  |  | TRUE | FALSE | 1553 | 2018 | 1863 | 2163 | {85060E95-5764-4B03-8044-1B415455201A}
4919 | 3922 | {1849F834-78EA-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | WATSONVILLE | Bank 2 (Non SCADA) | CB 411 (Non-SCADA) | PGE\MTDR | 2017-07-13 10:10:45.3467475 -07:00 | 083330411 | 162371101 | 3 | 3 | 3 | 2 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 390 | 2.81 | 2.78 | 390 | 2.81 | 2.78 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 443 | 3.19 | 3.16 | 420 | 3.03 | 3 |  |  | FALSE | FALSE | 1165 | 1515 | 1398 | 1748 | {E3CCF345-743F-48C1-BA92-1676EEF59AFB}
4920 | 3922 | {1849F83A-78EA-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | WATSONVILLE | Bank 2 (Non SCADA) | CB 413 (Non-SCADA) | PGE\MTDR | 2017-07-17 14:10:07.7119183 -07:00 | 083330413 | 182681101 | 4 | 3 | 3 | 2 | 315 | 2.38 | 2.36 | 299 | 2.26 | 2.24 | 409 | 3.1 | 3.07 | 388 | 2.94 | 2.91 | 378 | 2.86 | 2.83 | 359 | 2.72 | 2.69 | 472 | 3.57 | 3.53 | 448 | 3.39 | 3.36 |  |  | FALSE | FALSE | 1109 | 1442 | 1331 | 1664 | {5341FA15-8EE8-4BC9-9152-151675A32DD4}
4921 | 3922 | {1849F83D-78EA-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | WATSONVILLE | Bank 2 (Non SCADA) | CB 414 (Non-SCADA) | PGE\ACT0 | 2016-11-04 09:00:08.7376359 -07:00 | 083330414 | 182681102 | 3 | 3 | 3 | 2 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 390 | 2.81 | 2.78 | 390 | 2.81 | 2.78 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 450 | 3.24 | 3.21 | 450 | 3.24 | 3.21 |  |  | FALSE | FALSE | 1165 | 1515 | 1398 | 1748 | {A45D4429-315F-45CA-A543-3DDFA1DC6392}
4923 | 3890 | {464AB09A-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 2 (Non SCADA) | CB A405 (Non-SCADA) | PGE\SZC1 | 2016-11-04 09:01:51.9898092 -07:00 | 162370405 | 162371102 | 3 | 3 | 3 | 1 | 300 | 2.16 | 2.14 | 285 | 2.05 | 2.03 | 300 | 2.16 | 2.14 | 285 | 2.05 | 2.03 | 300 | 2.16 | 2.14 | 285 | 2.05 | 2.03 | 300 | 2.16 | 2.14 | 285 | 2.05 | 2.03 |  |  | TRUE | FALSE | 1553 | 2018 | 1863 | 2163 | {7226802D-BE79-43B5-AF52-593BB131E817}
4925 | 3923 | {464AB0A0-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 3 | CB 1101 (Non-SCADA) | PGE\SZC1 | 2017-03-07 14:42:41.0484031 -08:00 | 1623701101 | 162371103 | 8 | 3 | 3 | 1 | 405 | 8.84 | 8.75 | 405 | 8.84 | 8.75 | 461 | 10.06 | 9.96 | 461 | 10.06 | 9.96 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | Capability of 1101: Summer Norm/Emerg: 435/496; Winter Norm/Emerg: 500/500 |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3071 | {AB812F58-4527-4D08-9D21-7ED5B1B26EB7}
4927 | 3924 | {057C16B4-78EB-11E5-8C7B-9CB70D532D7F} | LOS PADRES | ZACA | Bank 1 | CB 1101 | PGE\ACT0 | 2016-11-04 15:03:16.0754531 -07:00 | 1826801101 | 162371104 | 8 | 3 | 3 | 2 | 391 | 8.53 | 8.44 | 391 | 8.53 | 8.44 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {E26A1E0F-0BD9-4AD0-8C2A-78321E6A95AF}
4928 | 3924 | {057C16BF-78EB-11E5-8C7B-9CB70D532D7F} | LOS PADRES | ZACA | Bank 1 | CB 1102 | PGE\ACT0 | 2016-11-04 15:02:43.3460780 -07:00 | 1826801102 | 162371105 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {F12E7BB1-6523-4EB1-88AA-719392E238B3}
4929 | 3923 | {464AB0A3-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 3 | CB 1102 | PGE\SZC1 | 2016-11-04 11:15:29.9444863 -07:00 | 1623701102 | 183052108 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3071 | {F58426C7-3215-4980-831E-0FF5CD8AE336}
4930 | 3923 | {464AB0A8-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 3 | CB 1103 (Non-SCADA) | PGE\SZC1 | 2017-03-07 14:48:09.2631148 -08:00 | 1623701103 | 013501101 | 8 | 3 | 3 | 1 | 360 | 7.86 | 7.78 | 360 | 7.86 | 7.78 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 371 | 8.1 | 8.02 | 371 | 8.1 | 8.02 | 412 | 8.99 | 8.9 | 412 | 8.99 | 8.9 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3071 | {ACAC535D-0C6C-459A-8FA4-4CCABA5E0EA3}
4931 | 3923 | {464AB0AB-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 3 | CB 1104 (Non-SCADA) | PGE\BXYD | 2017-01-11 10:11:51.7256075 -08:00 | 1623701104 | 013501103 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3071 | {16F2099F-C197-4F58-ABEF-EB3C00B6ACF1}
4932 | 3923 | {464AB0B4-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 3 | CB 1105 (Non-SCADA) | PGE\SZC1 | 2016-11-04 11:59:12.2158847 -07:00 | 1623701105 | 183052109 | 8 | 3 | 3 | 1 | 566 | 12.35 | 12.23 | 566 | 12.35 | 12.23 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3071 | {0E63A718-25D4-4441-B215-DB7814313A5E}
4935 | 3925 | {DFCFAD3E-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | TEMPLETON | Bank 2 | CB 2108 | PGE\ACT0 | 2016-11-07 08:26:26.5967612 -08:00 | 1830502108 | 013501104 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {B67A2463-8E5C-4C2E-866D-B20EE3BCC912}
4936 | 3926 | {C3D958FC-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | JARVIS | Bank 1 | CB 1101 | PGE\WPS3 | 2016-11-04 13:41:52.3720032 -07:00 | 0135001101 | 183052110 | 8 | 3 | 3 | 2 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 549 | 11.98 | 11.86 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | EDPI Capbaility mapped equivalent to Old Capability sheet | 3phase Bank | FALSE | FALSE | 1374 | 1787 | 1649 | 1844 | {984FC274-75F3-454C-AE52-A6E8D5F9B857}
4937 | 3926 | {C3D95921-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | JARVIS | Bank 1 | CB 1103 | PGE\WPS3 | 2016-11-04 13:54:44.8082123 -07:00 | 0135001103 | 013761101 | 8 | 3 | 3 | 2 | 492 | 10.74 | 10.63 | 492 | 10.74 | 10.63 | 554 | 12.09 | 11.97 | 554 | 12.09 | 11.97 | 560 | 12.22 | 12.1 | 560 | 12.22 | 12.1 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 | EDPI capability values is less than the old capability sheet due to the revised ratings on 4/0 CU, old sheet used 4ft/sec ratings. | 3phase Bank | FALSE | FALSE | 1374 | 1787 | 1649 | 1844 | {FF9A3FA2-F18A-41BA-8384-63F14E156DF0}
4938 | 3925 | {DFCFAD4F-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | TEMPLETON | Bank 2 | CB 2109 | PGE\ACT0 | 2016-11-04 14:11:21.4360634 -07:00 | 1830502109 | 013501105 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {29A5EE13-DFF3-4521-BF08-3940C7572684}
4939 | 3926 | {C3D95938-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | JARVIS | Bank 1 | CB 1104 | PGE\MAJc | 2017-06-28 14:47:37.8730710 -07:00 | 0135001104 | 013501106 | 8 | 3 | 3 | 2 | 391 | 8.53 | 8.44 | 391 | 8.53 | 8.44 | 440 | 9.6 | 9.5 | 440 | 9.6 | 9.5 | 443 | 9.67 | 9.57 | 443 | 9.67 | 9.57 | 473 | 10.32 | 10.22 | 473 | 10.32 | 10.22 | Way load of 8Amp at 1/0Cu OH Conductor is not mapped. | 3-phase Bnak | FALSE | FALSE | 1374 | 1787 | 1649 | 1844 | {642FE2BC-CF2E-4EA6-8D3C-716E797AEE7C}
4941 | 3925 | {E5CA29F5-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | TEMPLETON | Bank 2 | CB 2110 (Under Construction) | PGE\J2T4 | 2017-03-02 13:37:29.9782153 -08:00 | 1830502110 | 013501108 | 12 | 3 | 3 | 1 | 530 | 20.03 | 19.83 | 530 | 20.03 | 19.83 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {C8059C95-8CCD-41EB-B004-58164C030E2D}
4942 | 3930 | {C3D95B87-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | MT EDEN | Bank 1 | CB 1101 | PGE\RDR1 | 2017-05-04 08:25:19.9187007 -07:00 | 0137601101 | 183052111 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {A9A97A8F-F5F8-44B3-99D6-7C8A42707222}
4943 | 3931 | {C3D95952-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | JARVIS | Bank 2 | CB 1105 | PGE\WPS3 | 2016-11-30 13:09:15.7584882 -08:00 | 0135001105 | 183052112 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 356 | 7.77 | 7.69 | 600 | 13.09 | 12.96 | 438 | 9.56 | 9.46 | 557 | 12.16 | 12.04 | 367 | 8.01 | 7.93 | 600 | 13.09 | 12.96 | 444 | 9.69 | 9.59 | EDPI capability is less than the old capability sheet because of the ratings on the 350Al 1F/1W. Note: Way Load of 109A Summer and 148A Winter | 3-phase BK | FALSE | FALSE | 1374 | 1787 | 1649 | 1844 | {F368AA9E-0844-49A4-8D65-D56C1C425A2C}
4945 | 3931 | {C3D95962-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | JARVIS | Bank 2 | CB 1106 | PGE\WPS3 | 2016-11-04 14:30:20.4055892 -07:00 | 0135001106 | 183052113 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  | 3-phase Bank | FALSE | FALSE | 1374 | 1787 | 1649 | 1844 | {6EB2E07E-C036-4DF1-B935-C659A75E2AB2}
4946 | 3931 | {C3D9596B-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | JARVIS | Bank 2 | CB 1108 | PGE\WPS3 | 2016-11-04 14:37:42.5502744 -07:00 | 0135001108 | 013111114 | 8 | 3 | 3 | 2 | 475 | 10.37 | 10.27 | 475 | 10.37 | 10.27 | 554 | 12.09 | 11.97 | 554 | 12.09 | 11.97 | 489 | 10.67 | 10.56 | 489 | 10.67 | 10.56 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 | EDPI capbility is identical to old capability sheet. | 3-phase Bank | FALSE | FALSE | 1374 | 1787 | 1649 | 1844 | {B3C07F3B-087B-4841-B294-061A2728A3EB}
4949 | 3933 | {EBC8D8DD-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | TEMPLETON | Bank 3 | CB 2111 | PGE\ACT0 | 2016-11-07 08:19:57.5348818 -08:00 | 1830502111 | 013761103 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {72B28108-C40D-482B-97C2-8B07FD1F3072}
4954 | 3933 | {F254AB6F-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | TEMPLETON | Bank 3 | CB 2112 | PGE\ACT0 | 2016-11-07 08:18:30.6911972 -08:00 | 1830502112 | 013111115 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {546BDA01-7022-407F-8247-BEA68C919292}
4955 | 3933 | {F8B1A694-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | TEMPLETON | Bank 3 | CB 2113 | PGE\ACT0 | 2016-11-07 08:16:29.5687779 -08:00 | 1830502113 | 013501109 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 650 | 24.57 | 24.32 | 650 | 24.57 | 24.32 | 650 | 24.57 | 24.32 | 650 | 24.57 | 24.32 | 650 | 24.57 | 24.32 | 650 | 24.57 | 24.32 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {E19CE8FE-65FF-4663-AFA9-F01654913670}
4956 | 3829 | {CFDD369B-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN LEANDRO | Bank 3 | CB 1114 | PGE\RDR1 | 2017-05-18 10:29:37.6297651 -07:00 | 0131101114 | 013761105 | 7 | 3 | 3 | 2 | 467 | 10.09 | 9.99 | 467 | 10.09 | 9.99 | 523 | 11.3 | 11.19 | 523 | 11.3 | 11.19 | 481 | 10.39 | 10.29 | 481 | 10.39 | 10.29 | 539 | 11.64 | 11.52 | 539 | 11.64 | 11.52 | The 750 Cu P&L cable will be replaced with 1100 Al EPR cable in 2017/2018 under PM# 30866456 |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {7E0C109B-58E3-45C0-8A28-560E2E3B83BD}
4957 | 3930 | {C9E299CD-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | MT EDEN | Bank 1 | CB 1103 | PGE\RDR1 | 2017-05-03 14:21:46.9470165 -07:00 | 0137601103 | 013111116 | 7 | 3 | 3 | 2 | 564 | 12.18 | 12.06 | 564 | 12.18 | 12.06 | 700 | 15.12 | 14.97 | 700 | 15.12 | 14.97 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 700 | 15.12 | 14.97 | 700 | 15.12 | 14.97 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {31C7C2E0-E69F-4F0F-965A-07A7E36C9C5E}
4958 | 3829 | {CFDD36C0-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN LEANDRO | Bank 3 | CB 1115 | PGE\RDR1 | 2017-05-19 09:19:15.8083011 -07:00 | 0131101115 | 013761109 | 7 | 3 | 3 | 2 | 486 | 10.5 | 10.4 | 486 | 10.5 | 10.4 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 549 | 11.86 | 11.74 | 549 | 11.86 | 11.74 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {A9617E58-EAA1-4187-87A4-80FF50CE0676}
4959 | 3935 | {C3D9598C-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | JARVIS | Bank 3 | CB 1109 | PGE\WPS3 | 2016-11-04 15:10:50.0252604 -07:00 | 0135001109 | 013501110 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  | 3-phase Bk | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {FFBDD05D-AEF5-43A3-9D9B-D76FD2B5B8CA}
4962 | 3930 | {C9E299E1-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | MT EDEN | Bank 1 | CB 1105 | PGE\RDR1 | 2017-05-04 08:53:55.8892995 -07:00 | 0137601105 | 013761114 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {8163B7C9-55B3-4A7F-82BE-3B411035FA29}
4963 | 3829 | {CFDD36C9-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN LEANDRO | Bank 3 | CB 1116 | PGE\RDR1 | 2017-05-19 10:13:10.9566615 -07:00 | 0131101116 | 013501111 | 7 | 3 | 3 | 2 | 486 | 10.5 | 10.4 | 486 | 10.5 | 10.4 | 554 | 11.97 | 11.85 | 554 | 11.97 | 11.85 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 598 | 12.92 | 12.79 | 598 | 12.92 | 12.79 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {DF41988E-9651-485D-A32A-8C4E0AD11035}
4964 | 3930 | {C9E299EA-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | MT EDEN | Bank 1 | CB 1109 | PGE\RDR1 | 2017-05-08 14:27:22.9293586 -07:00 | 0137601109 | 013460401 | 7 | 3 | 3 | 2 | 564 | 12.18 | 12.06 | 564 | 12.18 | 12.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {3CA2D923-0637-4424-B939-A09B0DEC4FEC}
4965 | 3935 | {C3D95995-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | JARVIS | Bank 3 | CB 1110 | PGE\WPS3 | 2016-11-04 15:34:57.8665085 -07:00 | 0135001110 | 013460402 | 8 | 3 | 3 | 2 | 475 | 10.37 | 10.27 | 475 | 10.37 | 10.27 | 584 | 12.75 | 12.62 | 584 | 12.75 | 12.62 | 489 | 10.67 | 10.56 | 489 | 10.67 | 10.56 | 592 | 12.92 | 12.79 | 592 | 12.92 | 12.79 |  | 3-phase BK | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {1F1FF2ED-40B8-4669-A62D-8BD60CF55DD2}
4967 | 3930 | {C9E29A24-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | MT EDEN | Bank 1 | CB 1114 | PGE\RDR1 | 2017-05-08 12:44:38.4209264 -07:00 | 0137601114 | 013501112 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {8E39C073-91EF-4FAC-9655-8A4AD549CD36}
4969 | 3935 | {C3D9599E-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | JARVIS | Bank 3 | CB 1111 | PGE\WPS3 | 2016-11-04 15:43:12.1115235 -07:00 | 0135001111 | 013260401 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  | 3-phase BK | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {EC78C94A-993A-4877-AC95-E05E261D3BF4}
4971 | 3940 | {E049142F-0E48-11E6-95F2-D4BED91EFF1A} | MISSION | SAN LORENZO | BANK 401 (Non SCADA) | CB 401 (Non-SCADA) | PGE\MXUA | 2016-11-04 15:51:19.2799351 -07:00 | 013460401 | 013260402 | 3 | 3 | 3 | 2 | 264 | 1.9 | 1.88 | 264 | 1.9 | 1.88 | 343 | 2.47 | 2.45 | 343 | 2.47 | 2.45 | 317 | 2.28 | 2.26 | 317 | 2.28 | 2.26 | 396 | 2.85 | 2.82 | 396 | 2.85 | 2.82 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {2871E84D-A867-4B38-81BD-D7AA3880AAF5}
4972 | 3941 | {E6FF50AE-0E48-11E6-95F2-D4BED91EFF1A} | MISSION | SAN LORENZO | BANK 402 (Non SCADA) | CB 402 (Non-SCADA) | PGE\MXUA | 2016-11-04 15:54:26.1720635 -07:00 | 013460402 | 082462106 | 3 | 3 | 3 | 2 | 264 | 1.9 | 1.88 | 264 | 1.9 | 1.88 | 343 | 2.47 | 2.45 | 343 | 2.47 | 2.45 | 317 | 2.28 | 2.26 | 317 | 2.28 | 2.26 | 396 | 2.85 | 2.82 | 396 | 2.85 | 2.82 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {15B227BC-3438-4F9F-8E9E-D00DD9595B29}
4973 | 3935 | {C3D959ED-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | JARVIS | Bank 3 | CB 1112 | PGE\WPS3 | 2016-11-04 15:57:05.9224103 -07:00 | 0135001112 | 082462107 | 8 | 3 | 3 | 2 | 492 | 10.74 | 10.63 | 492 | 10.74 | 10.63 | 554 | 12.09 | 11.97 | 554 | 12.09 | 11.97 | 560 | 12.22 | 12.1 | 560 | 12.22 | 12.1 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 |  | 3-phase BK | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {8C76AE55-570E-43D6-832E-E17ACBC2B4D6}
4979 | 3944 | {E0491421-0E48-11E6-95F2-D4BED91EFF1A} | MISSION | SOTO | BANK 401 (Non SCADA) | CB 401 (Non-SCADA) | PGE\MXUA | 2016-11-04 17:19:06.2058343 -07:00 | 013260401 | 082462109 | 3 | 3 | 3 | 2 | 264 | 1.9 | 1.88 | 264 | 1.9 | 1.88 | 343 | 2.47 | 2.45 | 343 | 2.47 | 2.45 | 317 | 2.28 | 2.26 | 317 | 2.28 | 2.26 | 396 | 2.85 | 2.82 | 396 | 2.85 | 2.82 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {28EACCCC-19C0-4024-BF4E-C6E7C5CDB46A}
4980 | 3945 | {D9C71D0F-0E48-11E6-95F2-D4BED91EFF1A} | MISSION | SOTO | BANK 402 (Non SCADA) | CB 402 (Non-SCADA) | PGE\MXUA | 2016-11-04 17:25:32.0069720 -07:00 | 013260402 | 082462110 | 3 | 3 | 3 | 2 | 240 | 1.73 | 1.71 | 240 | 1.73 | 1.71 | 240 | 1.73 | 1.71 | 240 | 1.73 | 1.71 | 240 | 1.73 | 1.71 | 240 | 1.73 | 1.71 | 240 | 1.73 | 1.71 | 240 | 1.73 | 1.71 |  |  | FALSE | FALSE | 240 | 240 | 240 | 240 | {7E8CC65A-813A-4B56-B0EF-70B024256146}
4981 | 3946 | {A394F88B-FDD1-11E5-9D37-D4BED91EFF1A} | SAN JOSE | NORTECH | BANK 2 | CB 2106 | PGE\DVN5 | 2016-11-23 14:11:26.4992486 -08:00 | 0824602106 | 082462111 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {2B091EA9-D397-4229-A3EB-D4D873F17851}
4983 | 3946 | {B00739DE-FDD1-11E5-9D37-D4BED91EFF1A} | SAN JOSE | NORTECH | BANK 2 | CB 2107 | PGE\DVN5 | 2016-11-23 14:11:52.6785656 -08:00 | 0824602107 | 012221101 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {F2DC8640-EDEB-478A-8325-74783C35DE7D}
4984 | 3947 | {F4D10D03-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | NORTECH | Bank 3 | CB 2109 | PGE\DVN5 | 2016-11-23 14:12:40.4773132 -08:00 | 0824602109 | 012221102 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {8180F283-8772-42F4-92A7-908B6E065516}
4985 | 3947 | {F4D10DAD-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | NORTECH | Bank 3 | CB 2110 | PGE\MXEN | 2016-11-04 18:16:33.7699821 -07:00 | 0824602110 | 012221103 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {E0E3F64B-E715-4957-822B-68138FA27CEA}
4986 | 3947 | {F4D10DEF-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | NORTECH | Bank 3 | CB 2111 | PGE\MXEN | 2016-11-04 18:18:17.0630758 -07:00 | 0824602111 | 012221104 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {1A69A6B2-507F-4623-B764-B9B71757585E}
4987 | 3949 | {C9E29BC8-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | NEWARK | Bank 3 | CB 1101 | PGE\RDR1 | 2017-05-30 10:51:35.7256180 -07:00 | 0122201101 | 012221105 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  | 3-phase Bank | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {DB69B2D2-288C-4EE8-9121-A0FE7EE709B8}
4988 | 3949 | {C9E29BD1-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | NEWARK | Bank 3 | CB 1102 | PGE\RDR1 | 2017-05-26 14:03:09.2622908 -07:00 | 0122201102 | 012221106 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | Way load at 4/0CU is 191A summer, 144A winter | 3-phase Bank | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {46C93643-079C-4458-84D4-D479D7BF8F99}
4989 | 3949 | {C9E29BDA-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | NEWARK | Bank 3 | CB 1103 | PGE\RDR1 | 2017-05-26 14:20:44.5737138 -07:00 | 0122201103 | 012221107 | 7 | 3 | 3 | 2 | 492 | 10.63 | 10.52 | 492 | 10.63 | 10.52 | 554 | 11.97 | 11.85 | 554 | 11.97 | 11.85 | 560 | 12.1 | 11.98 | 560 | 12.1 | 11.98 | 598 | 12.92 | 12.79 | 598 | 12.92 | 12.79 |  | 3-phase Bank | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {0D0D1C31-772E-4A86-BCD4-B528739CD14C}
4990 | 3949 | {C9E29BF1-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | NEWARK | Bank 3 | CB 1104 | PGE\RDR1 | 2017-05-26 14:34:16.8137463 -07:00 | 0122201104 | 012221108 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  | 3-phase Bank | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {4FCD647E-2F79-4E83-B841-FC268E1D1B73}
4991 | 3950 | {C9E29C04-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | NEWARK | Bank 4 | CB 1105 | PGE\RDR1 | 2017-05-26 14:42:17.1531413 -07:00 | 0122201105 | 012222107 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  | 3-phase Bank | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {50BC84A8-2BBE-43D8-9E58-AF98EB6880C1}
4994 | 3950 | {C9E29C14-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | NEWARK | Bank 4 | CB 1106 | PGE\RDR1 | 2017-05-30 10:18:23.7048796 -07:00 | 0122201106 | 012222108 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  | 3-phase BK | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {9B03371A-DFF1-41DB-8859-3FB485B28E19}
4996 | 3950 | {C9E29C2B-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | NEWARK | Bank 4 | CB 1107 | PGE\JLDe | 2017-06-26 14:28:59.2490000 -07:00 | 0122201107 | 012222109 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | EDPI capability is less than the old capability sheet due to missing way loads inlcusion in the worksheet. | 3-phase Bank | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {2E9C8061-1802-41D8-9250-058400F69634}
4998 | 3950 | {C9E29C3B-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | NEWARK | Bank 4 | CB 1108 | PGE\RDR1 | 2017-05-30 10:40:24.3398106 -07:00 | 0122201108 | 012222110 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  | 3-phase Bank | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {F00B6418-A43F-4EE8-BEBF-14AB607A14BA}
5000 | 3953 | {C9E29B66-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | NEWARK | Bank 22 | CB 2107 | PGE\RDR1 | 2017-05-25 14:19:51.2631175 -07:00 | 0122202107 | 182811101 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 665 | 24.88 | 24.63 | 665 | 24.88 | 24.63 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 667 | 24.95 | 24.7 | 667 | 24.95 | 24.7 |  | 3-phase bank | FALSE | FALSE | 2004 | 2606 | 2200 | 2640 | {35DD0C51-15E0-4E65-BBEF-01EC6DF40844}
5004 | 3953 | {C9E29B87-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | NEWARK | Bank 22 | CB 2108 | PGE\RDR1 | 2017-05-25 14:24:50.7809568 -07:00 | 0122202108 | 182811102 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 665 | 24.88 | 24.63 | 665 | 24.88 | 24.63 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 667 | 24.95 | 24.7 | 667 | 24.95 | 24.7 |  | 3-phase BK | FALSE | FALSE | 2004 | 2606 | 2200 | 2640 | {795930A3-B74C-4A60-B173-546CABA5A2CE}
5006 | 3953 | {C9E29BAC-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | NEWARK | Bank 22 | CB 2109 | PGE\RDR1 | 2017-05-26 09:25:55.5411758 -07:00 | 0122202109 | 182811103 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  | 3-phase BK | FALSE | FALSE | 2004 | 2606 | 2200 | 2640 | {503782C2-6CFC-4C30-B95B-9D92F1B07A83}
5009 | 3953 | {C9E29BB5-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | NEWARK | Bank 22 | CB 2110 | PGE\RDR1 | 2017-05-25 14:49:12.9097622 -07:00 | 0122202110 | 182811104 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  | 3-phase BK | FALSE | FALSE | 2004 | 2606 | 2200 | 2640 | {0848ED14-2CEB-4029-A314-E82BCF7C6B1C}
5019 | 3959 | {D38A1B68-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SISQUOC | Bank 2 | CB 1101 | PGE\ACT0 | 2016-11-07 09:08:46.0316046 -08:00 | 1828101101 | 182721101 | 8 | 2 | 1 | 2 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {BA52ED12-2085-43E7-8725-15A9EE8A899A}
5020 | 3959 | {D9CC1C5A-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SISQUOC | Bank 2 | CB 1102 | PGE\ACT0 | 2016-11-07 09:08:27.1727034 -08:00 | 1828101102 | 182721102 | 8 | 2 | 1 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {B89ABFD8-5486-46CB-90E0-0092640E6496}
5021 | 3960 | {D9CC1C74-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SISQUOC | Bank 3 | CB 1103 | PGE\ACT0 | 2016-11-07 09:07:50.2920726 -08:00 | 1828101103 | 182721104 | 8 | 1 | 1 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {63A948AD-D0A0-4A14-8FEF-0D3FAC307B69}
5022 | 3960 | {DFCFAD2D-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SISQUOC | Bank 3 | CB 1104 | PGE\ACT0 | 2016-11-07 09:09:38.1914361 -08:00 | 1828101104 | 162371106 | 8 | 1 | 1 | 2 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {14FD112C-E7CB-46D7-8168-99C0379B7DB3}
5023 | 3961 | {CD07BE8C-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SANTA YNEZ | Bank 1 | CB 1101 | PGE\ACT0 | 2016-11-07 09:39:17.9686732 -08:00 | 1827201101 | 162371107 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {05AC2AEF-7C19-4111-9BF4-8F7C93BD4D3E}
5025 | 3962 | {CD07BEA1-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SANTA YNEZ | Bank 2 | CB 1102 | PGE\ACT0 | 2016-11-07 09:55:25.1533293 -08:00 | 1827201102 | 162371108 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {66D86096-056D-4175-9648-56398ED4531A}
5026 | 3962 | {CD07BEA9-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SANTA YNEZ | Bank 2 | CB 1104 | PGE\ACT0 | 2016-11-07 10:23:37.0348969 -08:00 | 1827201104 | 162211101 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {787FA41D-C518-4674-94F4-D7441FA52FBF}
5028 | 3928 | {464AB0BD-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 4 | CB 1106 (Non-SCADA) | PGE\SZC1 | 2017-03-07 14:53:36.1674013 -08:00 | 1623701106 | 162371109 | 8 | 3 | 3 | 1 | 457 | 9.97 | 9.87 | 457 | 9.97 | 9.87 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {FCD9B884-560C-41C1-AEF4-2E75C5B7075C}
5029 | 3928 | {464AB0C3-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 4 | CB 1107 (Non-SCADA) | PGE\ACT0 | 2016-11-23 08:17:30.6173285 -08:00 | 1623701107 | 163091101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Other Limiting Factor: 397AL parallel with 2/0CU. Sum Nor=704A, Sum Emer=785A, Win Nor=896A, Win Emer=968A |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {CFD2CCEA-75DC-444E-9E63-FE79823E8A61}
5030 | 3928 | {464AB0D2-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 4 | CB 1108 (Non-SCADA) | PGE\SZC1 | 2016-11-07 11:34:23.0586650 -08:00 | 1623701108 | 162371110 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {E910D532-A0F3-454F-B41C-27CA813A4972}
5032 | 3963 | {2FE3CAFB-671D-11E5-80CA-005056A729E5} | STOCKTON | CALAVERAS CEMENT | Bank 1 | CB 1101 | PGE\BXYD | 2017-01-17 10:15:30.8058506 -08:00 | 1622101101 | 162371111 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {8A329E82-2203-4D44-B106-8AEBBFEC49C9}
5034 | 3932 | {464AB0DE-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 5 | CB 1109 (Non-SCADA) | PGE\SZC1 | 2016-11-07 13:59:16.9699659 -08:00 | 1623701109 | 163091103 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {EE63AF8F-7C38-491D-8004-C8BF9F2F75CB}
5035 | 3964 | {2FE3CB12-671D-11E5-80CA-005056A729E5} | STOCKTON | CARBONA | Bank 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\JWCp | 2017-05-11 10:23:25.5796107 -07:00 | 1630901101 | 022811103 | 8 | 3 | 3 | 1 | 636 | 13.88 | 13.74 | 600 | 13.09 | 12.96 | 700 | 15.28 | 15.13 | 600 | 13.09 | 12.96 | 700 | 15.28 | 15.13 | 600 | 13.09 | 12.96 | 700 | 15.28 | 15.13 | 600 | 13.09 | 12.96 | !!LIMITING FACTOR!! SW D4757 + Wayload: Summer Norm/Emerg= 654/654; Winter Norm/Emerg= 612/612 |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {E8E924CA-3D2F-4270-94CD-221F7BCB7446}
5037 | 3932 | {464AB0E4-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 5 | CB 1110 | PGE\BXYD | 2017-01-11 10:20:48.3222472 -08:00 | 1623701110 | 063621108 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 570 | 12.44 | 12.32 | 675 | 14.73 | 14.58 | 675 | 14.73 | 14.58 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 675 | 14.73 | 14.58 | 675 | 14.73 | 14.58 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {BCBD53A7-0E6F-4335-8E87-E813F9FF708C}
5039 | 3932 | {464AB0E9-671D-11E5-80CA-005056A729E5} | STOCKTON | STOCKTON A | Bank 5 | CB 1111 | PGE\SZC1 | 2016-11-07 14:50:36.7633272 -08:00 | 1623701111 | 022811104 | 8 | 3 | 3 | 1 | 510 | 11.13 | 11.02 | 510 | 11.13 | 11.02 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 554 | 12.09 | 11.97 | 554 | 12.09 | 11.97 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {D372B0E4-0361-457C-AD43-FFE1AF8ED2C0}
5040 | 3964 | {2FE3CB1B-671D-11E5-80CA-005056A729E5} | STOCKTON | CARBONA | Bank 1 (Non SCADA) | CB 1103 (Non-SCADA) | PGE\APE3 | 2017-05-10 16:37:39.5047917 -07:00 | 1630901103 | 063621109 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 750 | 16.37 | 16.21 | 580 | 12.66 | 12.53 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 750 | 16.37 | 16.21 | 580 | 12.66 | 12.53 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F9C17061-8098-47AC-BF13-59D5C4846C2B}
5103 | 3999 | {2C77C79C-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | PACIFICA | Bank 2 | CB 1103 | PGE\C7CF | 2016-11-08 12:54:36.7571254 -08:00 | 0228101103 | 013111108 | 8 | 3 | 3 | 2 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {1A3651B2-DAC4-4947-9505-C634FBE9A976}
5105 | 3992 | {53849D51-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DEEPWATER | Bank 3 | CB 1108 | PGE\JMB4 | 2017-05-12 09:42:54.1654058 -07:00 | 0636201108 | 163121105 | 8 | 3 | 3 | 1 | 636 | 13.88 | 13.74 | 636 | 13.88 | 13.74 | 792 | 17.28 | 17.11 | 792 | 17.28 | 17.11 | 691 | 15.08 | 14.93 | 691 | 15.08 | 14.93 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {010C7B6A-5671-4718-A87A-3D58E31227EB}
5106 | 3999 | {2C77C7AC-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | PACIFICA | Bank 2 | CB 1104 | PGE\C7CF | 2016-11-08 13:10:50.2861171 -08:00 | 0228101104 | 163121106 | 8 | 3 | 3 | 2 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {D343128F-7488-49C5-AF09-28D2C39023A6}
5107 | 3992 | {53849D5A-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DEEPWATER | Bank 3 | CB 1109 | PGE\JMB4 | 2017-05-12 11:06:54.1275478 -07:00 | 0636201109 | 022690401 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 728 | 15.89 | 15.73 | 728 | 15.89 | 15.73 | 634 | 13.84 | 13.7 | 634 | 13.84 | 13.7 | 768 | 16.76 | 16.59 | 768 | 16.76 | 16.59 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9B7FE424-FD2E-48E4-B919-4C25A4C41415}
5109 | 3827 | {CFDD362E-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN LEANDRO | Bank 2 | CB 1108 | PGE\RDR1 | 2017-05-15 12:34:39.8892048 -07:00 | 0131101108 | 022690403 | 7 | 3 | 3 | 2 | 394 | 8.51 | 8.42 | 394 | 8.51 | 8.42 | 449 | 9.7 | 9.6 | 449 | 9.7 | 9.6 | 464 | 10.02 | 9.92 | 464 | 10.02 | 9.92 | 519 | 11.21 | 11.1 | 519 | 11.21 | 11.1 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {C6922CDE-3082-4860-BEB5-9E3443908DAA}
5110 | 4000 | {369796C7-671D-11E5-80CA-005056A729E5} | STOCKTON | COUNTRY CLUB | Bank 4 | CB 1105 | PGE\BXYD | 2017-01-12 16:34:56.7508314 -08:00 | 1631201105 | 163912104 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 641 | 833 | 769 | 962 | {6FA30636-73EC-40A7-89A8-643D1E515AC9}
5111 | 4000 | {369796CC-671D-11E5-80CA-005056A729E5} | STOCKTON | COUNTRY CLUB | Bank 4 | CB 1106 | PGE\BXYD | 2017-01-12 16:35:22.2725950 -08:00 | 1631201106 | 254201106 | 8 | 3 | 3 | 1 | 512 | 11.17 | 11.06 | 512 | 11.17 | 11.06 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 |  |  | FALSE | FALSE | 641 | 833 | 769 | 962 | {3763C9B7-5AA3-4755-9F58-BC48B8ED65FE}
5112 | 4001 | {25CD6746-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MILLBRAE | Bank 1 | CB 401 | PGE\C7CF | 2016-11-08 13:34:56.0381216 -08:00 | 022690401 | 022690404 | 4 | 3 | 3 | 2 | 336 | 2.54 | 2.51 | 336 | 2.54 | 2.51 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 792 | 1030 | 951 | 1189 | {2337E3AD-0BFC-43C7-A961-2E43E47FFA54}
5113 | 4001 | {25CD674F-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MILLBRAE | Bank 1 | CB 403 (Non-SCADA) | PGE\C7CF | 2016-11-09 15:33:08.1842239 -08:00 | 022690403 | 163912105 | 4 | 3 | 3 | 2 | 336 | 2.54 | 2.51 | 336 | 2.54 | 2.51 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 389 | 2.94 | 2.91 | 389 | 2.94 | 2.91 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 792 | 1030 | 951 | 1189 | {568DC02C-C6F1-4ED5-8025-86937BE44452}
5114 | 4005 | {36979701-671D-11E5-80CA-005056A729E5} | STOCKTON | EIGHT MILE | Bank 2 | CB 2104 | PGE\BXYD | 2017-01-12 15:22:36.0854068 -08:00 | 1639102104 | 163912106 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {AAECDC5F-926A-4D7F-B116-0DAAF7170553}
5116 | 4007 | {E30058EA-671D-11E5-80CA-005056A729E5} | KERN | GOOSE LAKE | Bank 2 (Non SCADA) | CB 1106 (Non-SCADA) | PGE\T1SI | 2016-11-08 14:29:13.8866749 -08:00 | 2542001106 | 014091101 | 8 | 4 | 4 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {0BB43473-C125-4B3E-9F6F-BA1575967287}
5117 | 4001 | {25CD6752-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MILLBRAE | Bank 1 | CB 404 (Non-SCADA) | PGE\C7CF | 2016-11-09 15:35:57.1048671 -08:00 | 022690404 | 163912101 | 4 | 3 | 3 | 2 | 100 | 0.76 | 0.75 | 100 | 0.76 | 0.75 | 130 | 0.98 | 0.97 | 130 | 0.98 | 0.97 | 120 | 0.91 | 0.9 | 120 | 0.91 | 0.9 | 150 | 1.14 | 1.13 | 150 | 1.14 | 1.13 |  |  | FALSE | FALSE | 792 | 1030 | 951 | 1189 | {1574703A-F2AB-4E83-B005-844C3FCF37B6}
5118 | 4005 | {36979706-671D-11E5-80CA-005056A729E5} | STOCKTON | EIGHT MILE | Bank 2 | CB 2105 | PGE\ACT0 | 2016-11-08 13:54:16.5522952 -08:00 | 1639102105 | 163912102 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {B52D28D1-BAAE-4989-BEBE-DB3E82FDCA03}
5120 | 4005 | {B00CC3F7-DA91-11E5-BF25-2016D89D35F7} | STOCKTON | EIGHT MILE | Bank 2 | CB 2106 | PGE\ACT0 | 2016-11-08 13:57:39.3072265 -08:00 | 1639102106 | 163912103 | 12 | 3 | 3 | 1 | 661 | 24.98 | 24.73 | 661 | 24.98 | 24.73 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {09CBB7E6-E12A-4895-8928-9AA17DDDF60B}
5121 | 4004 | {B7382A33-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | CASTRO VALLEY | Bank 1 | CB 1101 | PGE\GMK5 | 2016-11-08 15:35:30.1674952 -08:00 | 0140901101 | 163481101 | 8 | 3 | 3 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {10701250-79CC-4B75-949E-4866FBD381FD}
5122 | 4009 | {36979717-671D-11E5-80CA-005056A729E5} | STOCKTON | EIGHT MILE | Bank 3 | CB 2101 | PGE\BXYD | 2017-01-12 15:25:06.2363693 -08:00 | 1639102101 | 014091102 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {1DA12FFA-E8FA-4473-AD7C-8CBEB097FDB3}
5123 | 4009 | {3697972B-671D-11E5-80CA-005056A729E5} | STOCKTON | EIGHT MILE | Bank 3 | CB 2102 | PGE\BXYD | 2017-01-12 15:25:37.4989697 -08:00 | 1639102102 | 163481105 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {19F33D46-3214-423F-BAD5-0279C7A887A6}
5124 | 4009 | {36979745-671D-11E5-80CA-005056A729E5} | STOCKTON | EIGHT MILE | Bank 3 | CB 2103 | PGE\BXYD | 2017-01-12 15:26:17.5288263 -08:00 | 1639102103 | 252721103 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {A3FC4B0A-ABDD-4885-B180-6A301A899D17}
5125 | 4008 | {4C486EAF-671D-11E5-80CA-005056A729E5} | STOCKTON | WEBER | Bank 3 | CB 1101 | PGE\SZC1 | 2016-11-08 14:11:36.0037384 -08:00 | 1634801101 | 163481112 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Other Limiting Factor: Parallel 600AL EPR Cable. Missing in equipment list! |  | FALSE | FALSE | 1145 | 1489 | 1374 | 1718 | {51C2C8C8-8835-401C-8FB2-40ABE8678156}
5126 | 4004 | {B7382A51-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | CASTRO VALLEY | Bank 1 | CB 1102 | PGE\GMK5 | 2016-11-08 15:33:05.2830054 -08:00 | 0140901102 | 162161101 | 8 | 3 | 3 | 2 | 525 | 11.46 | 11.35 | 525 | 11.46 | 11.35 | 588 | 12.83 | 12.7 | 588 | 12.83 | 12.7 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {00000000-0000-0000-0000-000000000000}
5127 | 4008 | {4C486EB7-671D-11E5-80CA-005056A729E5} | STOCKTON | WEBER | Bank 3 | CB 1105 | PGE\SZC1 | 2016-11-08 14:18:18.4654166 -08:00 | 1634801105 | 252721107 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1145 | 1489 | 1374 | 1718 | {BC23CCD1-2B78-48A5-A3D6-84869B1C5BFD}
5128 | 4011 | {E30058F6-671D-11E5-80CA-005056A729E5} | KERN | KERN OIL | Bank 1 | CB 1103 | PGE\T1SI | 2016-11-08 14:23:05.9334110 -08:00 | 2527201103 | 014091103 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {AFF40558-22A8-4205-AAF5-102FD4282DF8}
5130 | 4008 | {4C486EC5-671D-11E5-80CA-005056A729E5} | STOCKTON | WEBER | Bank 3 | CB 1112 (Non-SCADA) | PGE\SZC1 | 2016-11-08 14:27:31.3105015 -08:00 | 1634801112 | 163481113 | 8 | 3 | 3 | 1 | 478 | 10.43 | 10.33 | 478 | 10.43 | 10.33 | 531 | 11.59 | 11.47 | 531 | 11.59 | 11.47 | 492 | 10.74 | 10.63 | 492 | 10.74 | 10.63 | 546 | 11.92 | 11.8 | 546 | 11.92 | 11.8 |  |  | FALSE | FALSE | 1145 | 1489 | 1374 | 1718 | {66305F57-8ECB-4FF5-921C-C518BF5BD851}
5131 | 4010 | {36979753-671D-11E5-80CA-005056A729E5} | STOCKTON | ELECTRA | Bank 1 (Non SCADA) | CB 1101 | PGE\BXYD | 2017-01-12 15:15:48.8291962 -08:00 | 1621601101 | 014091104 | 8 | 3 | 3 | 1 | 325 | 7.09 | 7.02 | 308 | 6.72 | 6.65 | 363 | 7.92 | 7.84 | 344 | 7.51 | 7.43 | 415 | 9.06 | 8.97 | 394 | 8.6 | 8.51 | 443 | 9.67 | 9.57 | 420 | 9.17 | 9.08 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {502B0FA4-0976-42EF-847F-52C89422E298}
5132 | 4011 | {E3005901-671D-11E5-80CA-005056A729E5} | KERN | KERN OIL | Bank 1 | CB 1107 | PGE\T1SI | 2016-11-08 14:34:05.4735472 -08:00 | 2527201107 | 163091104 | 8 | 4 | 4 | 1 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {25B6E156-7167-427C-B4D0-E65E15706985}
5133 | 4004 | {B7382A68-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | CASTRO VALLEY | Bank 1 | CB 1103 | PGE\GMK5 | 2016-11-08 15:32:30.3207814 -08:00 | 0140901103 | 012240401 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {99B938F2-A334-4CFC-AF90-BA51A9E02FD8}
5134 | 4013 | {4C486ECE-671D-11E5-80CA-005056A729E5} | STOCKTON | WEBER | Bank 4 | CB 1113 | PGE\SZC1 | 2016-11-08 14:46:10.6919545 -08:00 | 1634801113 | 012240402 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1145 | 1489 | 1374 | 1718 | {3B63945B-E308-494C-8556-D81967548868}
5135 | 4004 | {B7382A8D-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | CASTRO VALLEY | Bank 1 | CB 1104 | PGE\GMK5 | 2016-11-08 15:31:44.2027474 -08:00 | 0140901104 | 163091102 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {CE058C1D-8018-452B-941D-4760B6C405FB}
5041 | 3964 | {2FE3CB1E-671D-11E5-80CA-005056A729E5} | STOCKTON | CARBONA | Bank 1 (Non SCADA) | CB 1104 (Non-SCADA) | PGE\APE3 | 2017-05-10 16:39:11.5333210 -07:00 | 1630901104 | 012980401 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {30B23115-935A-4763-BD5E-A9BBFAD556B1}
5042 | 3965 | {B8DDB879-0E48-11E6-95F2-D4BED91EFF1A} | MISSION | STATION O | BANK 401 (Non SCADA) | CB 401 (Non-SCADA) | PGE\MXUA | 2016-11-07 15:41:55.2670525 -08:00 | 012240401 | 163341101 | 3 | 3 | 3 | 2 | 264 | 1.9 | 1.88 | 264 | 1.9 | 1.88 | 343 | 2.47 | 2.45 | 343 | 2.47 | 2.45 | 317 | 2.28 | 2.26 | 317 | 2.28 | 2.26 | 396 | 2.85 | 2.82 | 396 | 2.85 | 2.82 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {9AB5E2A4-4044-413F-B0D3-84EEAFA866A3}
5043 | 3966 | {C07E0029-0E48-11E6-95F2-D4BED91EFF1A} | MISSION | STATION O | BANK 402 (Non SCADA) | CB 402 (Non-SCADA) | PGE\MXUA | 2016-11-07 15:44:34.3451679 -08:00 | 012240402 | 013761102 | 3 | 3 | 3 | 2 | 264 | 1.9 | 1.88 | 264 | 1.9 | 1.88 | 343 | 2.47 | 2.45 | 343 | 2.47 | 2.45 | 317 | 2.28 | 2.26 | 317 | 2.28 | 2.26 | 396 | 2.85 | 2.82 | 396 | 2.85 | 2.82 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {B08E1FB2-F6BA-4608-A418-B02EBD9FA1D2}
5044 | 3967 | {2FE3CB27-671D-11E5-80CA-005056A729E5} | STOCKTON | CARBONA | Bank 2 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\BXYD | 2017-01-17 09:47:49.8419096 -08:00 | 1630901102 | 013761104 | 8 | 3 | 3 | 1 | 343 | 7.49 | 7.42 | 343 | 7.49 | 7.42 | 446 | 9.73 | 9.63 | 446 | 9.73 | 9.63 | 412 | 8.99 | 8.9 | 412 | 8.99 | 8.9 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 343 | 446 | 412 | 515 | {EA9E5025-AF9B-4EE8-8EF1-6AC256AC301A}
5045 | 3968 | {CB3A2E89-0E48-11E6-95F2-D4BED91EFF1A} | MISSION | WARD | BANK 401 (Non SCADA) | CB 401 (Non-SCADA) | PGE\MXUA | 2016-11-07 15:52:57.8403534 -08:00 | 012980401 | 013761106 | 3 | 3 | 3 | 2 | 264 | 1.9 | 1.88 | 264 | 1.9 | 1.88 | 343 | 2.47 | 2.45 | 343 | 2.47 | 2.45 | 317 | 2.28 | 2.26 | 317 | 2.28 | 2.26 | 396 | 2.85 | 2.82 | 396 | 2.85 | 2.82 |  |  | FALSE | FALSE | 264 | 343 | 317 | 396 | {B8D0427D-54EB-42D9-8492-CECF12089117}
5047 | 3969 | {2FE3CB68-671D-11E5-80CA-005056A729E5} | STOCKTON | CLAY | Bank 1 | CB 1101 | PGE\BXYD | 2017-01-12 17:02:35.0102612 -08:00 | 1633401101 | 163341102 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {B0840CFB-F348-4AFA-BCD2-B658EB5E8039}
5049 | 3942 | {C9E29A30-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | MT EDEN | Bank 2 | CB 1102 | PGE\RDR1 | 2017-05-08 13:06:26.5552221 -07:00 | 0137601102 | 013761107 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3000 | {98E5A0FC-AB88-4EC0-A703-289E03458224}
5050 | 3942 | {C9E29A39-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | MT EDEN | Bank 2 | CB 1104 | PGE\RDR1 | 2017-05-03 14:47:36.5333461 -07:00 | 0137601104 | 013761108 | 7 | 3 | 3 | 2 | 564 | 12.18 | 12.06 | 564 | 12.18 | 12.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 2951 | {D5E31491-90FD-4C53-81A1-DC048486E6B4}
5051 | 3942 | {C9E29A6F-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | MT EDEN | Bank 2 | CB 1106 | PGE\RDR1 | 2017-05-08 10:37:37.0363370 -07:00 | 0137601106 | 163341103 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3000 | {5FBC72D5-9084-41D0-B270-F681C4AC8E24}
5052 | 3969 | {2FE3CB6D-671D-11E5-80CA-005056A729E5} | STOCKTON | CLAY | Bank 1 | CB 1102 | PGE\BXYD | 2017-01-12 17:02:52.8099753 -08:00 | 1633401102 | 013761110 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 489 | 10.67 | 10.56 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {3FCFB471-C27B-4DA9-8C9A-2041BBF6DBC5}
5054 | 3942 | {C9E29A86-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | MT EDEN | Bank 2 | CB 1107 | PGE\RDR1 | 2017-05-08 13:30:51.3673479 -07:00 | 0137601107 | 024161101 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3000 | {29DF8C34-296F-4D96-9BC0-0C0A5658C4C1}
5055 | 3942 | {C9E29A9D-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | MT EDEN | Bank 2 | CB 1108 | PGE\RDR1 | 2017-05-08 13:54:47.6769948 -07:00 | 0137601108 | 024161102 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3000 | {B445EC63-FBB3-40AE-B9C1-2C6882A4F5F3}
5056 | 3971 | {2FE3CB78-671D-11E5-80CA-005056A729E5} | STOCKTON | CLAY | Bank 2 | CB 1103 | PGE\BXYD | 2017-01-12 17:05:42.6950643 -08:00 | 1633401103 | 024160402 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {60513D54-BCA5-4500-A245-B6FA96383043}
5057 | 3975 | {C9E29ABE-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | MT EDEN | Bank 3 | CB 1110 | PGE\RDR1 | 2017-05-08 14:50:19.6339998 -07:00 | 0137601110 | 163120401 | 7 | 3 | 3 | 2 | 564 | 12.18 | 12.06 | 564 | 12.18 | 12.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2640 | 2200 | 2640 | {5EC9E920-E1A0-4BF4-833F-ECA2FA35B6C3}
5058 | 3916 | {2C77C80E-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | REDWOOD CITY | Bank 1 | CB 1101 | PGE\C7CF | 2016-11-08 08:53:13.9768073 -08:00 | 0241601101 | 163621101 | 8 | 3 | 3 | 2 | 505 | 11.02 | 10.91 | 505 | 11.02 | 10.91 | 586 | 12.79 | 12.66 | 586 | 12.79 | 12.66 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {EED17CC4-D015-4A4D-A479-AC9FB7EB90D6}
5059 | 3916 | {2C77C817-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | REDWOOD CITY | Bank 1 | CB 1102 | PGE\C7CF | 2016-11-08 08:55:59.5352334 -08:00 | 0241601102 | 163621102 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {62518E08-4021-4D81-8B41-B67397F48363}
5060 | 3917 | {2C77C82A-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | REDWOOD CITY | Bank 2 | CB 402 (SW-TBD) (Non-SCADA) | PGE\C7CF | 2016-11-08 09:05:09.8970257 -08:00 | 024160402 | 013761111 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 3-1p regulator 34.5kVA |  | FALSE | FALSE | 990 | 1288 | 1189 | 1486 | {6F05C9AE-1D74-48A3-A9E9-DAA89EBB62C5}
5061 | 3974 | {2FE3CBDA-671D-11E5-80CA-005056A729E5} | STOCKTON | COUNTRY CLUB | Bank 1 | CB 401 | PGE\BXYD | 2017-01-12 16:03:22.8674912 -08:00 | 163120401 | 163621103 | 4 | 3 | 3 | 1 | 379 | 2.87 | 2.84 | 379 | 2.87 | 2.84 | 416 | 3.15 | 3.12 | 416 | 3.15 | 3.12 | 428 | 3.24 | 3.21 | 428 | 3.24 | 3.21 | 471 | 3.57 | 3.53 | 471 | 3.57 | 3.53 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {42221589-D0F3-4EA0-A34A-3988A226F5D4}
5063 | 3976 | {4C486F2C-671D-11E5-80CA-005056A729E5} | STOCKTON | WEST LANE | Bank 1 | CB 1101 | PGE\BXYD | 2017-01-10 16:14:57.9066383 -08:00 | 1636201101 | 163151101 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {3909BA85-97EE-4633-9248-57093EE470C1}
5064 | 3976 | {4C486F3D-671D-11E5-80CA-005056A729E5} | STOCKTON | WEST LANE | Bank 1 | CB 1102 | PGE\BXYD | 2017-01-10 16:15:26.7515930 -08:00 | 1636201102 | 163151102 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 550 | 12 | 11.88 | 522 | 11.39 | 11.28 | 550 | 12 | 11.88 | 522 | 11.39 | 11.28 | 550 | 12 | 11.88 | 522 | 11.39 | 11.28 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {B9AFC2BB-9D15-4622-84B8-F7CACF8434A8}
5065 | 3975 | {C9E29ACE-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | MT EDEN | Bank 3 | CB 1111 | PGE\RDR1 | 2017-05-09 08:28:35.2780990 -07:00 | 0137601111 | 013761112 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2640 | 2200 | 2640 | {96636E78-A8E9-4060-A0A3-76102B347A98}
5066 | 3976 | {4C486F45-671D-11E5-80CA-005056A729E5} | STOCKTON | WEST LANE | Bank 1 | CB 1103 | PGE\BXYD | 2017-01-10 16:16:13.4900918 -08:00 | 1636201103 | 013761113 | 8 | 3 | 3 | 1 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 | 550 | 12 | 11.88 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {93751D58-4A18-4506-BC95-B87EBE0F7488}
5068 | 3977 | {4C486E9D-671D-11E5-80CA-005056A729E5} | STOCKTON | WATERLOO | Bank 2 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\BXYD | 2017-01-10 16:52:47.2748669 -08:00 | 1631501101 | 163120402 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {95CF72AA-BB3B-415F-B9ED-8392441A2B75}
5069 | 3977 | {4C486EA3-671D-11E5-80CA-005056A729E5} | STOCKTON | WATERLOO | Bank 2 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\BXYD | 2017-01-10 16:53:59.0885714 -08:00 | 1631501102 | 163120403 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {61C008BD-B3C3-4497-912A-3598F2C3858E}
5070 | 3975 | {C9E29AD7-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | MT EDEN | Bank 3 | CB 1112 | PGE\RDR1 | 2017-05-09 08:57:31.7318917 -07:00 | 0137601112 | 163121101 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2640 | 2200 | 2640 | {32AA12AA-FF38-4BF5-98E5-386F8B345AC1}
5071 | 3975 | {C9E29B0A-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | MT EDEN | Bank 3 | CB 1113 | PGE\RDR1 | 2017-05-09 09:54:02.5194979 -07:00 | 0137601113 | 024160403 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2640 | 2200 | 2640 | {5E9B76CB-10E7-496E-9A5C-B7E39A394E4F}
5075 | 3974 | {2FE3CBDF-671D-11E5-80CA-005056A729E5} | STOCKTON | COUNTRY CLUB | Bank 1 | CB 402 | PGE\BXYD | 2017-01-12 16:05:56.5752765 -08:00 | 163120402 | 163121102 | 4 | 3 | 3 | 1 | 379 | 2.87 | 2.84 | 379 | 2.87 | 2.84 | 416 | 3.15 | 3.12 | 416 | 3.15 | 3.12 | 428 | 3.24 | 3.21 | 428 | 3.24 | 3.21 | 471 | 3.57 | 3.53 | 471 | 3.57 | 3.53 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {1C2F1EC1-ECD6-4487-AACB-5E3333C18468}
5076 | 3974 | {2FE3CBE4-671D-11E5-80CA-005056A729E5} | STOCKTON | COUNTRY CLUB | Bank 1 | CB 403 | PGE\BXYD | 2017-01-12 16:08:39.9863240 -08:00 | 163120403 | 024160405 | 4 | 3 | 3 | 1 | 440 | 3.33 | 3.3 | 440 | 3.33 | 3.3 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {518FA77A-D5D3-4E7F-BD6D-EECB30599FF6}
5077 | 3978 | {2FE3CBEF-671D-11E5-80CA-005056A729E5} | STOCKTON | COUNTRY CLUB | Bank 2 | CB 1101 | PGE\ACT0 | 2016-11-08 11:28:40.1187338 -08:00 | 1631201101 | 024160404 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {3077FFFE-C7D2-49EB-A714-5760247B423B}
5078 | 3917 | {2C77C82D-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | REDWOOD CITY | Bank 2 | CB 403 (SW-TBD) (Non-SCADA) | PGE\C7CF | 2016-11-08 09:52:25.2204166 -08:00 | 024160403 | 024160406 | 4 | 3 | 3 | 2 | 356 | 2.69 | 2.66 | 356 | 2.69 | 2.66 | 392 | 2.97 | 2.94 | 392 | 2.97 | 2.94 | 367 | 2.78 | 2.75 | 367 | 2.78 | 2.75 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 990 | 1288 | 1189 | 1486 | {7F18C44F-7B3F-4713-9332-BBE7D6B7AB6F}
5079 | 3978 | {369796AF-671D-11E5-80CA-005056A729E5} | STOCKTON | COUNTRY CLUB | Bank 2 | CB 1102 | PGE\BXYD | 2017-01-12 16:14:14.6864695 -08:00 | 1631201102 | 024160408 | 8 | 3 | 3 | 1 | 480 | 10.48 | 10.38 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 494 | 10.78 | 10.67 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 |  |  | FALSE | FALSE | 481 | 625 | 577 | 720 | {C85FD1C8-401D-48FA-844E-99617D3437C6}
5080 | 3917 | {2C77C830-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | REDWOOD CITY | Bank 2 | CB 405 (Non-SCADA) | PGE\C7CF | 2016-11-08 10:10:50.7195468 -08:00 | 024160405 | 024160409 | 4 | 3 | 3 | 2 | 378 | 2.86 | 2.83 | 378 | 2.86 | 2.83 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 389 | 2.94 | 2.91 | 389 | 2.94 | 2.91 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 990 | 1288 | 1189 | 1486 | {D40C0A48-8097-49BE-AE72-0F3F0465F558}
5081 | 3918 | {2C77C83D-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | REDWOOD CITY | Bank 3 | CB 404 (Non-SCADA) | PGE\C7CF | 2016-11-08 10:21:28.2658512 -08:00 | 024160404 | 024160410 | 4 | 3 | 3 | 2 | 454 | 3.44 | 3.41 | 454 | 3.44 | 3.41 | 499 | 3.78 | 3.74 | 499 | 3.78 | 3.74 | 468 | 3.54 | 3.5 | 468 | 3.54 | 3.5 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 |  |  | FALSE | FALSE | 1664 | 2163 | 1997 | 2163 | {BCDD45B1-AE7B-499C-9D16-DA278BCFE02D}
5082 | 3918 | {2C77C840-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | REDWOOD CITY | Bank 3 | CB 406 (Non-SCADA) | PGE\C7CF | 2016-11-08 10:26:28.6984460 -08:00 | 024160406 | 024161104 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 1664 | 2163 | 1997 | 2163 | {268E3F6A-4EC6-4616-8E94-61B567CAC1D0}
5083 | 3918 | {2C77C846-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | REDWOOD CITY | Bank 3 | CB 408 (Non-SCADA) | PGE\C7CF | 2016-11-08 10:28:40.3721714 -08:00 | 024160408 | 163121103 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 1664 | 2163 | 1997 | 2163 | {9D210F16-0ED1-48BA-9A84-268C744339DB}
5084 | 3918 | {2C77C849-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | REDWOOD CITY | Bank 3 | CB 409 (Non-SCADA) | PGE\C7CF | 2016-11-08 10:48:34.5988478 -08:00 | 02416409 | 024161105 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 1664 | 2163 | 1997 | 2163 | {82608C7E-FC2C-42DD-B916-F1AE1F530CFE}
5085 | 3918 | {2C77C84C-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | REDWOOD CITY | Bank 3 | CB 410 (Non-SCADA) | PGE\C7CF | 2016-11-08 10:51:14.5110102 -08:00 | 024160410 | 163121104 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 1664 | 2163 | 1997 | 2163 | {09F4C8A1-8208-48C3-B47B-F74CD3BA0412}
5086 | 3919 | {2C77C87A-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | REDWOOD CITY | Bank 5 | CB 1104 | PGE\C7CF | 2016-11-08 11:11:43.7918875 -08:00 | 0241601104 | 024161106 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {EFFC4D91-51C0-4CEB-ADF9-C94508B30560}
5087 | 3987 | {369796B7-671D-11E5-80CA-005056A729E5} | STOCKTON | COUNTRY CLUB | Bank 3 | CB 1103 | PGE\BXYD | 2017-01-12 16:32:20.7966317 -08:00 | 1631201103 | 063621105 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {358698A1-913E-4415-8121-DF0619E73242}
5089 | 3919 | {2C77C88A-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | REDWOOD CITY | Bank 5 | CB 1105 | PGE\C7CF | 2016-11-08 11:18:26.8510458 -08:00 | 0241601105 | 024141101 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {4BAA73A5-A67C-44CB-B4D0-CDA91A6761D9}
5090 | 3987 | {369796BC-671D-11E5-80CA-005056A729E5} | STOCKTON | COUNTRY CLUB | Bank 3 | CB 1104 | PGE\ACT0 | 2016-11-08 11:25:10.0765578 -08:00 | 1631201104 | 024141102 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {665C151E-E380-402D-8BB9-E99A7A8D1A45}
5091 | 3919 | {2C77C893-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | REDWOOD CITY | Bank 5 | CB 1106 | PGE\C7CF | 2016-11-08 11:26:28.9050210 -08:00 | 0241601106 | 063621106 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {E707C880-41B7-42F7-A47E-AF8EECBF2A61}
5092 | 3984 | {53849D1E-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DEEPWATER | Bank 2 | CB 1105 | PGE\JMB4 | 2016-11-08 12:55:32.3888972 -08:00 | 0636201105 | 022811101 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 689 | 15.04 | 14.89 | 689 | 15.04 | 14.89 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 732 | 15.98 | 15.82 | 732 | 15.98 | 15.82 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {88C0AA2B-6D38-4BFE-8957-56E0EFAC97E9}
5095 | 3996 | {2C77C7C9-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | RALSTON | Bank 1 | CB 1101 | PGE\C7CF | 2016-11-08 12:07:08.6315910 -08:00 | 0241401101 | 022811102 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 601 | 577 | 601 | {D08AC740-729F-4ED7-A8C1-C8A7C9AA810A}
5096 | 3997 | {2C77C7E3-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | RALSTON | Bank 2 | CB 1102 | PGE\C7CF | 2016-11-08 12:13:28.1165597 -08:00 | 0241401102 | 063621107 | 8 | 3 | 3 | 2 | 263 | 5.74 | 5.68 | 263 | 5.74 | 5.68 | 343 | 7.49 | 7.42 | 343 | 7.49 | 7.42 | 316 | 6.9 | 6.83 | 316 | 6.9 | 6.83 | 395 | 8.62 | 8.53 | 395 | 8.62 | 8.53 |  |  | FALSE | FALSE | 263 | 343 | 316 | 395 | {31CBFD60-3C08-420C-9528-7C88266C5D48}
5097 | 3984 | {53849D27-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DEEPWATER | Bank 2 | CB 1106 | PGE\JMB4 | 2016-11-08 12:53:11.5613153 -08:00 | 0636201106 | 252721109 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 689 | 15.04 | 14.89 | 689 | 15.04 | 14.89 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 732 | 15.98 | 15.82 | 732 | 15.98 | 15.82 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {4B1A3E15-5CC2-47E6-90EC-171E40F15545}
5099 | 3998 | {25CD6821-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | PACIFICA | Bank 1 | CB 1101 | PGE\C7CF | 2016-11-08 12:44:05.2677966 -08:00 | 0228101101 | 163481114 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {2E15BF9A-5F78-462C-A4F9-D83BAA1FAA21}
5100 | 3998 | {25CD6831-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | PACIFICA | Bank 1 | CB 1102 | PGE\C7CF | 2016-11-08 12:49:41.9878648 -08:00 | 0228101102 | 014091105 | 8 | 3 | 3 | 2 | 454 | 9.91 | 9.81 | 454 | 9.91 | 9.81 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 468 | 10.21 | 10.11 | 468 | 10.21 | 10.11 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {D3C4B4FB-00D9-4FA6-B89E-33F2D5DEDABC}
5101 | 3984 | {53849D30-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DEEPWATER | Bank 2 | CB 1107 | PGE\JMB4 | 2016-11-08 12:51:21.1135728 -08:00 | 0636201107 | 063441101 | 8 | 3 | 3 | 1 | 636 | 13.88 | 13.74 | 636 | 13.88 | 13.74 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 717 | 15.65 | 15.49 | 717 | 15.65 | 15.49 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {253133B4-A882-46F0-9B44-656A7A2589D8}
5137 | 4011 | {E3005906-671D-11E5-80CA-005056A729E5} | KERN | KERN OIL | Bank 1 | CB 1109 | PGE\T1SI | 2016-11-08 14:46:37.2382437 -08:00 | 2527201109 | 063441105 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B13BDE13-3841-4405-9C78-82E28F4FDE6D}
5138 | 4013 | {4C486ED3-671D-11E5-80CA-005056A729E5} | STOCKTON | WEBER | Bank 4 | CB 1114 | PGE\SZC1 | 2016-11-08 15:07:56.8946457 -08:00 | 1634801114 | 014091106 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1145 | 1489 | 1374 | 1718 | {E8649E64-F4B1-43F6-BAE5-DED0C67E34A0}
5140 | 4006 | {B7382AC3-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | CASTRO VALLEY | Bank 2 | CB 1105 | PGE\GMK5 | 2016-11-08 15:30:28.6423347 -08:00 | 0140901105 | 014091107 | 8 | 3 | 3 | 2 | 525 | 11.46 | 11.35 | 525 | 11.46 | 11.35 | 588 | 12.83 | 12.7 | 588 | 12.83 | 12.7 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {660C2DBB-B24D-452B-BF2A-9616D87E4778}
5141 | 4012 | {6F0BC791-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PLAINFIELD | Bank 1 | CB 1101 | PGE\BCF1 | 2016-11-08 14:59:30.6953203 -08:00 | 0634401101 | 014091108 | 8 | 1 | 1 | 1 | 430 | 9.38 | 9.29 | 430 | 9.38 | 9.29 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 430 | 559 | 516 | 601 | {DB5F1094-4202-4965-BF1F-3C616BE4B201}
5142 | 4014 | {6F0BC7C0-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PLAINFIELD | Bank 2 | CB 1105 | PGE\JMB4 | 2016-11-22 15:53:58.2000428 -08:00 | 0634401105 | 014091109 | 8 | 1 | 1 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 674 | 674 | 674 | 674 | {D272E1BA-4E4C-48E8-BDEE-77360A613E7F}
5143 | 4006 | {B7382AE8-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | CASTRO VALLEY | Bank 2 | CB 1106 | PGE\GMK5 | 2016-11-08 15:29:41.3260062 -08:00 | 0140901106 | 022691102 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {653D88A1-B5C5-47B0-B2A3-3D016C9A01F9}
5144 | 4006 | {B7382B30-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | CASTRO VALLEY | Bank 2 | CB 1107 | PGE\GMK5 | 2016-11-08 15:27:40.1228908 -08:00 | 0140901107 | 063441106 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {A3F36C21-6078-4DAD-95A8-5C89AD6B43AD}
5145 | 4006 | {B7382B40-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | CASTRO VALLEY | Bank 2 | CB 1108 | PGE\GMK5 | 2016-11-08 15:41:06.4812476 -08:00 | 0140901108 | 022691103 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {D9AF3C9D-A31A-4067-94BF-5BFCAFA3D42A}
5147 | 4006 | {B7382B81-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | CASTRO VALLEY | Bank 2 | CB 1109 | PGE\GMK5 | 2016-11-08 15:42:36.1787496 -08:00 | 0140901109 | 162161102 | 8 | 3 | 3 | 2 | 513 | 11.2 | 11.09 | 513 | 11.2 | 11.09 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 528 | 11.52 | 11.4 | 528 | 11.52 | 11.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {FC177CAD-70DA-4AA3-B76C-726B5E66A9B7}
5148 | 4002 | {25CD675F-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MILLBRAE | Bank 3 | CB 1102 | PGE\C7CF | 2016-11-08 15:41:19.9288786 -08:00 | 0226901102 | 163481102 | 8 | 3 | 3 | 2 | 525 | 11.46 | 11.35 | 525 | 11.46 | 11.35 | 588 | 12.83 | 12.7 | 588 | 12.83 | 12.7 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {88FA1499-BD7C-48C8-A736-551E2FF1EDE3}
5150 | 4014 | {6F0BC7D0-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PLAINFIELD | Bank 2 | CB 1106 | PGE\JMB4 | 2016-11-22 15:54:24.6433988 -08:00 | 0634401106 | 163481103 | 8 | 1 | 1 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 674 | 674 | 674 | 674 | {9A0C9916-7A0D-41CB-A1EC-4551F2F3FE74}
5152 | 4002 | {25CD676F-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MILLBRAE | Bank 3 | CB 1103 | PGE\C7CF | 2016-11-08 15:53:31.3359782 -08:00 | 0226901103 | 163481106 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {FC61CEE3-2D5A-4D32-B40D-3FF412DDD672}
5153 | 4010 | {3697975F-671D-11E5-80CA-005056A729E5} | STOCKTON | ELECTRA | Bank 1 (Non SCADA) | CB 1102 | PGE\VXRO | 2017-02-08 18:02:54.2389271 -08:00 | 1621601102 | 163481107 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 219 | 4.78 | 4.73 | 500 | 10.91 | 10.8 | 239 | 5.22 | 5.17 | 500 | 10.91 | 10.8 | 272 | 5.94 | 5.88 | 500 | 10.91 | 10.8 | 287 | 6.26 | 6.2 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {8A5D4E83-E27A-41F5-BA02-412673BD6952}
5155 | 4015 | {4C486EDE-671D-11E5-80CA-005056A729E5} | STOCKTON | WEBER | Bank 5 | CB 1102 | PGE\BXYD | 2017-01-10 16:35:58.3796777 -08:00 | 1634801102 | 163481108 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 2767 | {160A9F01-5CCD-484E-B5E0-705C10037FCB}
5156 | 4015 | {4C486EEF-671D-11E5-80CA-005056A729E5} | STOCKTON | WEBER | Bank 5 | CB 1103 | PGE\BXYD | 2017-01-10 16:37:35.8035512 -08:00 | 1634801103 | 022691106 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 489 | 10.67 | 10.56 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 2767 | {470F62D9-40CB-465A-9D23-D308EA6E7910}
5158 | 4015 | {C559ADDD-0B41-11E6-9D37-D4BED91EFF1A} | STOCKTON | WEBER | Bank 5 | CB 1106 (Non-SCADA) | PGE\BXYD | 2017-01-10 16:39:40.6215515 -08:00 | 1634801106 | 163481109 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 2767 | {6DFCF591-8E2B-4374-BE1E-6AFA7C27BB6E}
5159 | 4015 | {4C486EF7-671D-11E5-80CA-005056A729E5} | STOCKTON | WEBER | Bank 5 | CB 1107 | PGE\BXYD | 2017-01-10 16:40:07.3604657 -08:00 | 1634801107 | 014722101 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 2767 | {7C5CC9C3-CF7D-4171-9922-83D1B24DE821}
5160 | 4015 | {4C486EFC-671D-11E5-80CA-005056A729E5} | STOCKTON | WEBER | Bank 5 | CB 1108 | PGE\BXYD | 2017-01-10 16:40:38.3582618 -08:00 | 1634801108 | 163481110 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 2767 | {6848141D-A76D-4C3C-8E98-3B1A1B488378}
5161 | 4002 | {25CD6778-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MILLBRAE | Bank 3 | CB 1106 | PGE\C7CF | 2016-11-08 16:35:33.9866350 -08:00 | 0226901106 | 163481111 | 8 | 3 | 3 | 2 | 560 | 12.22 | 12.1 | 560 | 12.22 | 12.1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {474E6A31-0BCA-4F78-BE55-0478BBC46C74}
5162 | 4030 | {4C486F0A-671D-11E5-80CA-005056A729E5} | STOCKTON | WEBER | Bank 6 | CB 1109 | PGE\BXYD | 2017-01-10 16:42:57.3464770 -08:00 | 1634801109 | 022691108 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 2767 | {94BEA477-5ACF-4A2D-A4D5-C1499B859EC5}
5163 | 4018 | {B7382BE7-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DIXON LANDING | Bank 1 | CB 2101 | PGE\RDR1 | 2017-05-20 20:06:48.2378264 -07:00 | 0147202101 | 022691101 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {DE14B96D-6507-4A38-B9B8-C5EF80404DE9}
5164 | 4030 | {4C486F1B-671D-11E5-80CA-005056A729E5} | STOCKTON | WEBER | Bank 6 | CB 1110 | PGE\BXYD | 2017-01-10 16:48:46.4807716 -08:00 | 1634801110 | 014722102 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 2767 | {F7C070A4-269F-4F51-AD6B-A47E6B9C52B6}
5165 | 4030 | {D69D4644-0B41-11E6-9D37-D4BED91EFF1A} | STOCKTON | WEBER | Bank 6 | CB 1111 (Non-SCADA) | PGE\SZC1 | 2016-11-08 16:31:31.4920094 -08:00 | 1634801111 | 022691104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 2767 | {A8FE652B-A344-4CD5-A8E3-FB9336E64961}
5166 | 4002 | {25CD6781-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MILLBRAE | Bank 3 | CB 1108 | PGE\C7CF | 2016-11-08 16:36:20.2733726 -08:00 | 0226901108 | 014722103 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {5D7454AD-23DE-4760-BCB5-317B1CDB6F00}
5167 | 4003 | {25CD67B1-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MILLBRAE | Bank 4 | CB 1101 | PGE\C7CF | 2016-11-08 16:43:49.6097302 -08:00 | 0226901101 | 022691105 | 8 | 3 | 3 | 2 | 443 | 9.67 | 9.57 | 443 | 9.67 | 9.57 | 496 | 10.82 | 10.71 | 496 | 10.82 | 10.71 | 456 | 9.95 | 9.85 | 456 | 9.95 | 9.85 | 511 | 11.15 | 11.04 | 511 | 11.15 | 11.04 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {6A3CEAF6-2AED-4B02-BCF9-6247C11A9554}
5168 | 4018 | {BD86D818-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DIXON LANDING | Bank 1 | CB 2102 | PGE\RDR1 | 2017-05-20 20:19:30.6430797 -07:00 | 0147202102 | 022691107 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {F73DE2E8-F5AA-4982-BEF6-1912B522D4D9}
5169 | 4003 | {25CD67C1-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MILLBRAE | Bank 4 | CB 1104 | PGE\C7CF | 2016-11-08 16:50:32.1954264 -08:00 | 0226901104 | 014381102 | 8 | 3 | 3 | 2 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {B921F4ED-3C8A-40A8-A037-325561122862}
5170 | 4018 | {BD86D83D-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DIXON LANDING | Bank 1 | CB 2103 | PGE\RDR1 | 2017-05-20 20:21:43.6564779 -07:00 | 0147202103 | 014381103 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {377DEBA2-B14B-4E2F-B4B3-A92A87C68FDF}
5171 | 4003 | {25CD67FB-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MILLBRAE | Bank 4 | CB 1105 | PGE\C7CF | 2016-11-08 17:02:53.9293883 -08:00 | 0226901105 | 014381104 | 8 | 3 | 3 | 2 | 560 | 12.22 | 12.1 | 560 | 12.22 | 12.1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {4DF71098-9A73-4E15-834B-6E069063F356}
5172 | 4003 | {25CD6804-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MILLBRAE | Bank 4 | CB 1107 | PGE\C7CF | 2016-11-08 17:14:19.0547493 -08:00 | 0226901107 | 182671110 | 8 | 3 | 3 | 2 | 445 | 9.71 | 9.61 | 445 | 9.71 | 9.61 | 547 | 11.94 | 11.82 | 547 | 11.94 | 11.82 | 458 | 10 | 9.9 | 458 | 10 | 9.9 | 582 | 12.7 | 12.57 | 582 | 12.7 | 12.57 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {B4556B82-3BE8-4476-BBB3-794730D50F8C}
5173 | 4034 | {C3D95872-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | GRANT | Bank 1 | CB 1102 | PGE\GMK5 | 2016-11-09 07:36:31.5304546 -08:00 | 0143801102 | 182671111 | 8 | 3 | 3 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {C1F6EF3E-84F8-4546-BBA8-A1E825F0E67D}
5175 | 4034 | {C3D9587B-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | GRANT | Bank 1 | CB 1103 | PGE\GMK5 | 2016-11-09 07:46:30.0697388 -08:00 | 0143801103 | 014381105 | 8 | 3 | 3 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 758 | 16.54 | 16.37 | 758 | 16.54 | 16.37 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 768 | 16.76 | 16.59 | 768 | 16.76 | 16.59 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {C2382CB5-E474-4304-A095-274D583352B2}
5176 | 4034 | {C3D95884-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | GRANT | Bank 1 | CB 1104 | PGE\GMK5 | 2016-11-09 08:16:46.6127888 -08:00 | 0143801104 | 014381107 | 8 | 3 | 3 | 2 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {DDA5B752-13CA-4CBF-BDE0-A4DEE9700CEE}
5179 | 3838 | {C6F0026B-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SANTA MARIA | Bank 3 | CB 1110 | PGE\A9S5 | 2016-11-11 10:56:16.1411363 -08:00 | 1826701110 | 014381106 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {C58E6283-2F6E-47C8-98F3-CD996086DC79}
5180 | 3838 | {C6F00276-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SANTA MARIA | Bank 3 | CB 1111 | PGE\A9S5 | 2016-11-11 10:56:44.3464720 -08:00 | 1826701111 | 182671112 | 8 | 3 | 3 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 634 | 13.84 | 13.7 | 634 | 13.84 | 13.7 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {10FEEB89-7DEF-41E2-B283-E58A26BD41AF}
5181 | 4036 | {C3D9589A-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | GRANT | Bank 2 | CB 1105 | PGE\GMK5 | 2016-11-09 12:02:27.6580621 -08:00 | 0143801105 | 163451701 | 8 | 3 | 3 | 2 | 151 | 3.3 | 3.27 | 151 | 3.3 | 3.27 | 166 | 3.62 | 3.58 | 166 | 3.62 | 3.58 | 156 | 3.4 | 3.37 | 156 | 3.4 | 3.37 | 171 | 3.73 | 3.69 | 171 | 3.73 | 3.69 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {84095DB0-E7D6-4859-9E84-0B747EB0706C}
5183 | 4036 | {C3D958BA-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | GRANT | Bank 2 | CB 1107 | PGE\GMK5 | 2016-11-09 12:01:25.3807971 -08:00 | 0143801107 | 024131101 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {A4707F12-D207-4A84-9B9B-A60B44E371A0}
5184 | 4036 | {C3D958B1-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | GRANT | Bank 2 | CB 1106 | PGE\GMK5 | 2016-11-09 12:00:43.4311243 -08:00 | 0143801106 | 024131102 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {A6F95EC7-5D9A-4873-B310-F98688964EDB}
5185 | 3838 | {C6F0027B-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | SANTA MARIA | Bank 3 | CB 1112 | PGE\A9S5 | 2016-11-11 10:57:21.8342332 -08:00 | 1826701112 | 014381108 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 665 | 14.51 | 14.36 | 665 | 14.51 | 14.36 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9D8899D9-9D98-4D65-9F04-6DE9B771D61F}
5186 | 4039 | {36979794-671D-11E5-80CA-005056A729E5} | STOCKTON | FROGTOWN | Bank 1 | CB 1701 | PGE\BXYD | 2017-01-12 14:56:43.7194558 -08:00 | 1634501701 | 024131103 | 10 | 3 | 3 | 1 | 303 | 9.37 | 9.28 | 287 | 8.87 | 8.78 | 394 | 12.18 | 12.06 | 374 | 11.56 | 11.44 | 363 | 11.22 | 11.11 | 344 | 10.64 | 10.53 | 400 | 12.37 | 12.25 | 380 | 11.75 | 11.63 |  |  | TRUE | FALSE | 303 | 394 | 363 | 454 | {5795CA21-BF0F-405D-9505-CD5C39D9B7AD}
5192 | 4040 | {25CD667E-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MENLO | Bank 3 | CB 1101 | PGE\C7CF | 2016-11-09 15:26:32.2626355 -08:00 | 0241301101 | 024131104 | 8 | 3 | 3 | 2 | 475 | 10.37 | 10.27 | 475 | 10.37 | 10.27 | 584 | 12.75 | 12.62 | 584 | 12.75 | 12.62 | 489 | 10.67 | 10.56 | 489 | 10.67 | 10.56 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {7CDB2A15-52D4-45EF-80F8-DF4602024E3A}
5193 | 4040 | {25CD6695-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MENLO | Bank 3 | CB 1102 | PGE\C7CF | 2016-11-09 15:27:23.6659535 -08:00 | 0241301102 | 022440401 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 583 | 12.72 | 12.59 | 583 | 12.72 | 12.59 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 583 | 12.72 | 12.59 | 583 | 12.72 | 12.59 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {13138BEE-1B65-46C3-9370-EA49C11F0143}
5194 | 4036 | {C3D958CA-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | GRANT | Bank 2 | CB 1108 | PGE\GMK5 | 2016-11-09 12:01:43.2900563 -08:00 | 0143801108 | 022440402 | 8 | 3 | 3 | 2 | 151 | 3.3 | 3.27 | 151 | 3.3 | 3.27 | 166 | 3.62 | 3.58 | 166 | 3.62 | 3.58 | 156 | 3.4 | 3.37 | 156 | 3.4 | 3.37 | 171 | 3.73 | 3.69 | 171 | 3.73 | 3.69 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {AF34A1F4-31D8-483B-8363-65F849F9067C}
5196 | 4041 | {25CD66DA-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MENLO | Bank 4 | CB 1103 | PGE\C7CF | 2016-11-09 15:28:51.8379171 -08:00 | 0241301103 | 182571101 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {8B2DB01B-0BE8-4E57-9D4E-5099E0F30535}
5197 | 4041 | {25CD6729-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MENLO | Bank 4 | CB 1104 | PGE\C7CF | 2016-11-09 15:30:34.2230802 -08:00 | 0241301104 | 182571102 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {8B690D18-72D7-4308-B2FA-05C23CF0B145}
5198 | 4042 | {25CD6630-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | LAWNDALE | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2016-11-09 15:23:55.0266167 -08:00 | 022440401 | 182571103 | 4 | 3 | 3 | 2 | 288 | 2.18 | 2.16 | 288 | 2.18 | 2.16 | 288 | 2.18 | 2.16 | 288 | 2.18 | 2.16 | 288 | 2.18 | 2.16 | 288 | 2.18 | 2.16 | 288 | 2.18 | 2.16 | 288 | 2.18 | 2.16 |  |  | FALSE | FALSE | 288 | 288 | 288 | 288 | {823696BD-4B73-4EF3-B0E4-73E57C8F1CDA}
5199 | 4043 | {25CD6636-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | LAWNDALE | Bank 2 (Non SCADA) | CB 402 (Non-SCADA) | PGE\C7CF | 2016-11-09 15:23:30.6272575 -08:00 | 022440402 | 024110401 | 4 | 3 | 3 | 2 | 288 | 2.18 | 2.16 | 288 | 2.18 | 2.16 | 288 | 2.18 | 2.16 | 288 | 2.18 | 2.16 | 288 | 2.18 | 2.16 | 288 | 2.18 | 2.16 | 288 | 2.18 | 2.16 | 288 | 2.18 | 2.16 |  |  | FALSE | FALSE | 288 | 288 | 288 | 288 | {CD61C94C-634D-494F-88D6-5200E62FE373}
5200 | 4044 | {C97098A7-1171-11E6-95F2-D4BED91EFF1A} | LOS PADRES | DIVIDE | Bank 3 | CB 1101 | PGE\RPBK | 2017-05-16 14:39:21.9590279 -07:00 | 1825701101 | 024110402 | 8 | 3 | 3 | 2 | 430 | 9.38 | 9.29 | 408 | 8.9 | 8.81 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 489 | 10.67 | 10.56 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | PER RICHARD BENEFIEL (OF REGULATOR ON BANK 3): The astrisk footnote on the maintenance card shows that the reg has an FA rating of 1000 KVA or 10 MVA FA capacity rating= 481 amps @ 12,000 Volts per nameplate. | 481 A CAPABILITY | TRUE | FALSE | 430 | 558 | 515 | 644 | {B367782F-11DB-448C-940E-A568AE2D8521}
5202 | 4045 | {5715119C-1172-11E6-95F2-D4BED91EFF1A} | LOS PADRES | DIVIDE | Bank 4 | CB 1102 | PGE\A9S5 | 2016-11-11 08:58:32.1826230 -08:00 | 1825701102 | 024110403 | 8 | 3 | 3 | 2 | 677 | 14.77 | 14.62 | 677 | 14.77 | 14.62 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 717 | 15.65 | 15.49 | 717 | 15.65 | 15.49 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {648C7E4B-6F53-42C7-8C9B-22A1C941F484}
5204 | 4045 | {739DAEE9-1172-11E6-95F2-D4BED91EFF1A} | LOS PADRES | DIVIDE | Bank 4 | CB 1103 | PGE\A9S5 | 2016-11-11 08:58:58.0615299 -08:00 | 1825701103 | 024110404 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {92E4FBF6-280B-4891-9B5E-1299754D90C0}
5210 | 4046 | {25CD65A1-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | HILLSDALE | Bank 1 | CB 401 (SW-TBD) (Non-SCADA) | PGE\C7CF | 2016-11-09 12:15:55.8674387 -08:00 | 024110401 | 024110405 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 417 | 3.16 | 3.13 | 417 | 3.16 | 3.13 |  |  | FALSE | FALSE | 412 | 536 | 495 | 619 | {0ED64055-36C5-4C36-B8EE-82F9AD0347C4}
5211 | 4046 | {25CD65AB-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | HILLSDALE | Bank 1 | CB 402 (SW-TBD) (Non-SCADA) | PGE\C7CF | 2016-11-09 12:25:20.3047472 -08:00 | 024110402 | 024101102 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 417 | 3.16 | 3.13 | 417 | 3.16 | 3.13 |  |  | FALSE | FALSE | 412 | 536 | 495 | 619 | {B5C4D94F-B5F3-4AB8-8671-1083666119CB}
5212 | 4046 | {25CD65B5-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | HILLSDALE | Bank 1 | CB 403 (SW-TBD) (Non-SCADA) | PGE\C7CF | 2016-11-09 12:28:33.9085038 -08:00 | 024110403 | 024101101 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 417 | 3.16 | 3.13 | 417 | 3.16 | 3.13 |  |  | FALSE | FALSE | 412 | 536 | 495 | 619 | {8E555B6A-3986-430B-8392-11D61477237A}
5213 | 4046 | {25CD65BF-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | HILLSDALE | Bank 1 | CB 404 (SW-TBD) (Non-SCADA) | PGE\C7CF | 2017-06-08 17:25:43.9705485 -07:00 | 024110404 | 024101103 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 417 | 3.16 | 3.13 | 417 | 3.16 | 3.13 | There is a 3phase 225kVA voltage regulator on this feeder. |  | FALSE | FALSE | 412 | 536 | 495 | 619 | {063A93BD-0C2C-4C71-AFFE-B082570B9340}
5214 | 4046 | {25CD65C9-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | HILLSDALE | Bank 1 | CB 405 (SW-TBD) (Non-SCADA) | PGE\C7CF | 2016-11-09 12:37:40.0107201 -08:00 | 024110405 | 014351106 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 417 | 3.16 | 3.13 | 417 | 3.16 | 3.13 |  |  | FALSE | FALSE | 412 | 536 | 495 | 619 | {C7DF4748-7832-4514-B987-B8753905ED06}
5215 | 4047 | {25CD64DF-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | HALF MOON BAY | Bank 1 | CB 1102 | PGE\JLDe | 2016-11-09 14:55:48.0281441 -08:00 | 0241001102 | 014351107 | 8 | 3 | 3 | 2 | 429 | 9.36 | 9.27 | 429 | 9.36 | 9.27 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 429 | 558 | 515 | 644 | {A49264B1-69D9-4774-AAD8-06B4725CABEA}
5217 | 4048 | {25CD6515-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | HALF MOON BAY | Bank 2 | CB 1101 | PGE\C7CF | 2016-11-09 15:19:31.0980380 -08:00 | 0241001101 | 014351108 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {C1CDC81C-E4E1-4810-9244-97815020149F}
5218 | 4050 | {25CD653E-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | HALF MOON BAY | Bank 3 | CB 1103 | PGE\C7CF | 2016-11-09 15:19:56.0265749 -08:00 | 0241001103 | 014351109 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {5D2BF6C1-C7D7-4CCA-87D1-1CDC5EB7664B}
5219 | 4049 | {C3D957CC-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | FREMONT | Bank 2 | CB 1106 | PGE\RDR1 | 2017-06-01 10:38:34.9730475 -07:00 | 0143501106 | 152901101 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2000 | 2600 | 2200 | 2640 | {F38A683C-9888-43C2-BDF9-251EBB3036E5}
5222 | 4049 | {C3D957D5-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | FREMONT | Bank 2 | CB 1107 | PGE\RDR1 | 2017-06-01 10:39:42.5856145 -07:00 | 0143501107 | 152901102 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2000 | 2600 | 2200 | 2640 | {6A5DC710-6A6C-4565-9E27-98F16DC220FA}
5223 | 4049 | {C3D957E5-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | FREMONT | Bank 2 | CB 1108 | PGE\RDR1 | 2017-06-01 10:40:50.8534025 -07:00 | 0143501108 | 152901103 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2000 | 2600 | 2200 | 2640 | {201B62E5-73DC-4DA5-984E-9D33476DC3DD}
5224 | 4049 | {C3D957EE-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | FREMONT | Bank 2 | CB 1109 | PGE\RDR1 | 2017-06-01 10:41:46.4847855 -07:00 | 0143501109 | 152901104 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2000 | 2600 | 2200 | 2640 | {AF1DF418-5D5A-4453-8BAA-C87954A7833B}
5226 | 4053 | {68EB4C32-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | OLIVEHURST | Bank 1 | CB 1101 | PGE\TEJ2 | 2016-11-09 15:19:03.5163540 -08:00 | 1529001101 | 152901105 | 8 | 3 | 3 | 1 | 440 | 9.6 | 9.5 | 440 | 9.6 | 9.5 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {503809DE-2F75-4113-B6F0-D224479DFD88}
5227 | 4053 | {68EB4C49-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | OLIVEHURST | Bank 1 | CB 1102 | PGE\TEJ2 | 2016-11-09 15:18:33.4857737 -08:00 | 1529001102 | 153751101 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {31A4BF31-F146-41CC-945F-831B28700270}
5228 | 4054 | {68EB4C5C-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | OLIVEHURST | Bank 2 | CB 1103 | PGE\JMB4 | 2016-11-22 16:13:36.1621614 -08:00 | 1529001103 | 153751102 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 625 | 13.64 | 13.5 | 625 | 13.64 | 13.5 | 625 | 13.64 | 13.5 | 625 | 13.64 | 13.5 | 625 | 13.64 | 13.5 | 625 | 13.64 | 13.5 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {7340607F-CBE3-4766-B8C8-26201222B518}
5230 | 4054 | {68EB4C6C-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | OLIVEHURST | Bank 2 | CB 1104 | PGE\JMB4 | 2016-11-22 16:13:12.3094556 -08:00 | 1529001104 | 153751103 | 8 | 3 | 3 | 1 | 510 | 11.13 | 11.02 | 510 | 11.13 | 11.02 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 554 | 12.09 | 11.97 | 554 | 12.09 | 11.97 | 613 | 13.38 | 13.25 | 613 | 13.38 | 13.25 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {8049C6F2-224F-4ED5-B506-EC38F8527B93}
5231 | 4054 | {68EB4C75-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | OLIVEHURST | Bank 2 | CB 1105 | PGE\TEJ2 | 2016-11-09 15:23:02.6241805 -08:00 | 1529001105 | 153751104 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {9FA65E3D-B89C-4EFB-98AA-988B83D3F1E0}
5233 | 4055 | {6F0BC712-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PEASE | Bank 1 | CB 1101 | PGE\TEJ2 | 2016-11-09 15:46:09.5734129 -08:00 | 1537501101 | 153751105 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 625 | 13.64 | 13.5 | 625 | 13.64 | 13.5 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 721 | 15.73 | 15.57 | 721 | 15.73 | 15.57 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {42359696-CF83-4838-96A9-43E1C6F4B083}
5235 | 4055 | {6F0BC71B-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PEASE | Bank 1 | CB 1102 | PGE\TEJ2 | 2016-11-09 15:53:35.9797810 -08:00 | 1537501102 | 014452105 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {6AB36AA1-3428-4850-B8DA-448D373E8292}
5236 | 4056 | {6F0BC72E-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PEASE | Bank 3 | CB 1103 | PGE\TEJ2 | 2016-11-09 15:58:09.1162096 -08:00 | 1537501103 | 014452106 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1223 | 1590 | 1468 | 1835 | {F66AF8D5-7CEA-4B5D-AF88-A1745CACFA71}
5237 | 4056 | {6F0BC745-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PEASE | Bank 3 | CB 1104 | PGE\TEJ2 | 2016-11-09 16:01:35.7266238 -08:00 | 1537501104 | 014161105 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1223 | 1590 | 1468 | 1835 | {3CF211F2-1D24-4452-9249-8DD43B5930B6}
5239 | 4057 | {6F0BC774-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PEASE | Bank 4 | CB 1105 | PGE\TEJ2 | 2016-11-09 16:08:18.8274359 -08:00 | 1537501105 | 014161106 | 8 | 3 | 3 | 1 | 572 | 12.48 | 12.36 | 572 | 12.48 | 12.36 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {57660706-F953-4729-9AF6-3422DF8AF6A6}
5240 | 3893 | {ECBA7769-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | KIRKER | Bank 2 | CB 2105 | PGE\WCL5 | 2016-11-09 17:22:46.3782818 -08:00 | 0144502105 | 014161107 | 22 | 3 | 3 | 1 | 636 | 22.89 | 22.66 | 636 | 22.89 | 22.66 | 792 | 28.51 | 28.22 | 792 | 28.51 | 28.22 | 717 | 25.81 | 25.55 | 717 | 25.81 | 25.55 | 842 | 30.31 | 30.01 | 842 | 30.31 | 30.01 |  | Kuhlman,27/36/45, interior | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {8B970A11-89CA-4A38-B1C3-0BDBF8D5E5B5}
5243 | 3893 | {F2DB7ED7-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | KIRKER | Bank 2 | CB 2106 | PGE\WCL5 | 2016-11-09 17:31:11.0025679 -08:00 | 0144502106 | 014161108 | 22 | 3 | 3 | 1 | 573 | 20.62 | 20.41 | 573 | 20.62 | 20.41 | 728 | 26.2 | 25.94 | 728 | 26.2 | 25.94 | 634 | 22.82 | 22.59 | 634 | 22.82 | 22.59 | 768 | 27.64 | 27.36 | 768 | 27.64 | 27.36 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {90C6B5BF-4308-4533-A4FE-6A5C658DCE2B}
5244 | 4059 | {68AC54AD-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | ROSSMOOR | Bank 2 | CB 1105 | PGE\MFN3 | 2016-11-30 14:35:53.2146533 -08:00 | 0141601105 | 153731101 | 8 | 3 | 3 | 1 | 405 | 8.84 | 8.75 | 405 | 8.84 | 8.75 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 463 | 10.1 | 10 | 463 | 10.1 | 10 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {61DA94AF-E8E1-46B9-9351-B668F809C357}
5246 | 4059 | {68AC54BE-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | ROSSMOOR | Bank 2 | CB 1106 | PGE\MFN3 | 2016-11-30 14:36:04.7908179 -08:00 | 0141601106 | 153731102 | 8 | 3 | 3 | 1 | 745 | 16.26 | 16.1 | 745 | 16.26 | 16.1 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B36B7BD9-16F6-470E-BCDF-55E2AB6CC007}
5248 | 4059 | {6F0B7668-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | ROSSMOOR | Bank 2 | CB 1107 | PGE\MFN3 | 2016-11-30 14:36:14.1828005 -08:00 | 0141601107 | 014052101 | 8 | 3 | 3 | 1 | 566 | 12.35 | 12.23 | 566 | 12.35 | 12.23 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {2676A37A-3329-4092-B760-BE5F8D5C3FCE}
5249 | 4059 | {6F0B7676-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | ROSSMOOR | Bank 2 | CB 1108 | PGE\MFN3 | 2016-11-30 14:44:01.5690206 -08:00 | 0141601108 | 014052103 | 8 | 3 | 3 | 1 | 745 | 16.26 | 16.1 | 745 | 16.26 | 16.1 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {5C7ED0F8-A759-4795-B463-EB5C3E682B13}
5255 | 4060 | {6F0BC7EE-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PLUMAS | Bank 1 | CB 1101 | PGE\TEJ2 | 2016-11-10 07:57:14.0272077 -08:00 | 153731101 | 014722105 | 8 | 3 | 3 | 1 | 183 | 3.99 | 3.95 | 183 | 3.99 | 3.95 | 211 | 4.6 | 4.55 | 211 | 4.6 | 4.55 | 266 | 5.81 | 5.75 | 266 | 5.81 | 5.75 | 284 | 6.2 | 6.14 | 284 | 6.2 | 6.14 | Plumas 1101 tie to Plumas 1102 does not have 2 Cu and 1/o ACSR limitation. |  | FALSE | FALSE | 572 | 722 | 687 | 722 | {AF79FA18-50E1-48FA-A107-8F05EA940A89}
5256 | 4060 | {6F0BC7F7-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PLUMAS | Bank 1 | CB 1102 | PGE\TEJ2 | 2016-11-10 08:10:55.2015558 -08:00 | 153731102 | 014722106 | 8 | 3 | 3 | 1 | 345 | 7.53 | 7.45 | 345 | 7.53 | 7.45 | 386 | 8.42 | 8.34 | 386 | 8.42 | 8.34 | 443 | 9.67 | 9.57 | 443 | 9.67 | 9.57 | 473 | 10.32 | 10.22 | 473 | 10.32 | 10.22 | Plumas 1102 tie to Plumas 1101 does not have 4/o Al limitation. |  | FALSE | FALSE | 572 | 722 | 687 | 722 | {D7AFAE2F-4A39-4F25-A532-FF4F71198BCD}
5258 | 4061 | {C9E29C4A-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | NORTH DUBLIN | Bank 1 | CB 2101 | PGE\HGL3 | 2017-07-21 10:31:33.2756949 -07:00 | 0140502101 | 014722107 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 549 | 20.75 | 20.54 | 689 | 26.04 | 25.78 | 654 | 24.72 | 24.47 | 627 | 23.7 | 23.46 | 595 | 22.49 | 22.27 | 732 | 27.66 | 27.38 | 695 | 26.27 | 26.01 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {BFD15DFB-D75A-4897-869A-F3B3D41A88C1}
5259 | 4061 | {C9E29C61-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | NORTH DUBLIN | Bank 1 | CB 2103 | PGE\MXT7 | 2016-11-10 08:55:10.0402367 -08:00 | 0140502103 | 153732106 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 732 | 27.66 | 27.38 | 732 | 27.66 | 27.38 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {0B0433B5-8C01-45FA-96E0-2FCD21459325}
5263 | 4062 | {BD86D918-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DIXON LANDING | Bank 2 | CB 2105 | PGE\RDR1 | 2017-05-25 08:04:26.4393268 -07:00 | 0147202105 | 153732107 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {89548394-D1F5-4FC9-B7FC-31081321B500}
5264 | 4062 | {BD86D924-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DIXON LANDING | Bank 2 | CB 2106 | PGE\RDR1 | 2017-05-25 08:12:14.5011283 -07:00 | 0147202106 | 255292105 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {02F516CD-B267-4875-A3A8-75760951A5AD}
5265 | 4062 | {BD86D952-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DIXON LANDING | Bank 2 | CB 2107 | PGE\RDR1 | 2017-05-25 08:16:33.3134233 -07:00 | 0147202107 | 014232101 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {6E73039D-F6E9-4BF7-88AA-4D6DB5857ABB}
5266 | 4064 | {6F0BC80A-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PLUMAS | Bank 2 | CB 2106 | PGE\TEJ2 | 2016-11-10 09:20:20.5656488 -08:00 | 1537302106 | 014232102 | 12 | 3 | 3 | 1 | 345 | 13.04 | 12.91 | 345 | 13.04 | 12.91 | 386 | 14.59 | 14.44 | 386 | 14.59 | 14.44 | 443 | 16.74 | 16.57 | 443 | 16.74 | 16.57 | 473 | 17.88 | 17.7 | 473 | 17.88 | 17.7 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {9CAC9B36-03C3-4B09-B93C-84CB51F405E6}
5267 | 4064 | {6F0BC813-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PLUMAS | Bank 2 | CB 2107 | PGE\TEJ2 | 2016-11-10 09:27:50.8905156 -08:00 | 1537302107 | 255292106 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {63B8F254-4939-494E-A1D8-FDC0F935AF8B}
5269 | 1262 | {D7085CDD-671D-11E5-80CA-005056A729E5} | FRESNO | WOODWARD | Bank 2 | CB 2105 | PGE\KRBk | 2016-11-10 10:56:48.4787630 -08:00 | 2552902105 | 014232103 | 11 | 3 | 3 | 1 | 578 | 21.62 | 21.4 | 578 | 21.62 | 21.4 | 667 | 24.95 | 24.7 | 667 | 24.95 | 24.7 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 667 | 24.95 | 24.7 | 667 | 24.95 | 24.7 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {B2CBB128-F7C0-4210-9F70-7758272FBE4D}
5270 | 4065 | {CFDD3711-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN RAMON | Bank 3 | CB 2101 | PGE\MXT7 | 2016-11-10 10:20:56.7131174 -08:00 | 0142302101 | 014722109 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 720 | 27.21 | 26.94 | 720 | 27.21 | 26.94 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {4E38A7CF-BE12-46D4-9133-EDE5D9D6E223}
5273 | 2573 | {E0D1E925-9629-11E6-841B-D4BED91EFF1A} | SACRAMENTO | MAXWELL | Bank 2 | CB 1105 | PGE\TEJ2 | 2016-11-17 13:53:35.9121161 -08:00 |  | 014722110 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {E80F18D9-C5A8-46DE-85AA-62492B4B416F}
5279 | 2573 | {03C9337D-962A-11E6-841B-D4BED91EFF1A} | SACRAMENTO | MAXWELL | Bank 2 | CB 1106 | PGE\TEJ2 | 2016-11-17 13:53:21.7941161 -08:00 |  | 014722111 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 345 | 7.53 | 7.45 | 500 | 10.91 | 10.8 | 386 | 8.42 | 8.34 | 500 | 10.91 | 10.8 | 443 | 9.67 | 9.57 | 500 | 10.91 | 10.8 | 473 | 10.32 | 10.22 | Alt MTT is 440a. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {26A62331-738A-4BCB-BD3D-F157440C8197}
5280 | 4065 | {CFDD3728-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN RAMON | Bank 3 | CB 2102 | PGE\MXT7 | 2016-11-10 10:46:00.8579053 -08:00 | 0142302102 | 014232104 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 720 | 27.21 | 26.94 | 720 | 27.21 | 26.94 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {836C0853-DEAA-4D8F-9BC7-7CA5644FBF14}
5281 | 1262 | {D7085CEE-671D-11E5-80CA-005056A729E5} | FRESNO | WOODWARD | Bank 2 | CB 2106 | PGE\JWCp | 2017-08-02 14:54:32.3215221 -07:00 | 2552902106 | 153771101 | 11 | 3 | 3 | 1 | 447 | 16.72 | 16.55 | 447 | 16.72 | 16.55 | 568 | 21.25 | 21.04 | 568 | 21.25 | 21.04 | 495 | 18.52 | 18.33 | 495 | 18.52 | 18.33 | 599 | 22.41 | 22.19 | 570 | 21.33 | 21.12 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {5C8FFD76-9E8D-43C0-9E0F-98D295A8EE44}
5285 | 4065 | {CFDD3734-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN RAMON | Bank 3 | CB 2103 | PGE\MXT7 | 2016-11-10 10:55:33.3751966 -08:00 | 0142302103 | 153771102 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 674 | 25.47 | 25.22 | 674 | 25.47 | 25.22 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {FE9B8988-96B0-4BA5-AB38-2C61EB5B79A6}
5286 | 4063 | {BD86D965-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DIXON LANDING | Bank 3 | CB 2109 | PGE\RDR1 | 2017-05-25 08:24:07.8807923 -07:00 | 0147202109 | 014232105 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {4630000B-2C40-4564-A04B-4F7039ED2131}
5288 | 4063 | {BD86D97D-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DIXON LANDING | Bank 3 | CB 2110 | PGE\RDR1 | 2017-05-25 08:29:29.2978938 -07:00 | 0147202110 | 153771104 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {3029B002-6A57-4536-B46A-E6A932852E96}
5289 | 4063 | {BD86D98D-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DIXON LANDING | Bank 3 | CB 2111 | PGE\RDR1 | 2017-05-25 08:32:48.1886683 -07:00 | 0147202111 | 014232106 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {7D29C3B6-0E49-4CB1-8D73-F7E05414EB5A}
5290 | 4065 | {CFDD3778-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN RAMON | Bank 3 | CB 2104 | PGE\MXT7 | 2016-11-10 11:05:31.9143157 -08:00 | 0142302104 | 014232107 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 674 | 25.47 | 25.22 | 674 | 25.47 | 25.22 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {F860E0D6-00D1-4396-846A-A527DDBB0AAD}
5291 | 4066 | {634A363F-0B41-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | LIVE OAK | Bank 1 | CB 1101 (Non-SCADA) | PGE\TEJ2 | 2016-11-10 11:28:19.2043591 -08:00 | 1537701101 | 014232108 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 601 | 577 | 601 | {98868D09-AF43-48F4-ACDA-78C5AB9FA291}
5292 | 4066 | {5A80375C-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | LIVE OAK | Bank 1 | CB 1102 | PGE\TEJ2 | 2016-11-10 11:32:28.6709177 -08:00 | 1537701102 | 062831101 | 8 | 4 | 4 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 577 | 12.59 | 12.46 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 601 | 577 | 601 | {11792C19-B333-40CF-9E8A-0576E82C2632}
5294 | 4067 | {CFDD3799-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN RAMON | Bank 4 | CB 2105 | PGE\MXT7 | 2016-11-10 11:35:12.9123509 -08:00 | 0142302105 | 062831102 | 12 | 3 | 3 | 1 | 530 | 20.03 | 19.83 | 530 | 20.03 | 19.83 | 720 | 27.21 | 26.94 | 720 | 27.21 | 26.94 | 634 | 23.96 | 23.72 | 634 | 23.96 | 23.72 | 720 | 27.21 | 26.94 | 720 | 27.21 | 26.94 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {4BC8904C-A3FF-44C7-A586-EB021E9C7170}
5295 | 4068 | {2FEE884A-0E4A-11E6-95F2-D4BED91EFF1A} | SACRAMENTO | LIVE OAK | BANK 2 | CB 1104 | PGE\TEJ2 | 2016-11-10 11:39:51.5344863 -08:00 | 1537701104 | 062831103 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {90F3F5CD-A351-44F6-A0B8-D65472759F8D}
5296 | 4067 | {CFDD37CC-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN RAMON | Bank 4 | CB 2106 | PGE\MXT7 | 2016-11-10 11:40:55.6683250 -08:00 | 0142302106 | 014232110 | 12 | 3 | 3 | 1 | 530 | 20.03 | 19.83 | 530 | 20.03 | 19.83 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 720 | 27.21 | 26.94 | 720 | 27.21 | 26.94 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {7F8DFCA0-077F-4FDD-A7C7-97AD7E2C9575}
5297 | 4067 | {CFDD37F3-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN RAMON | Bank 4 | CB 2107 | PGE\MXT7 | 2016-11-10 12:01:45.8379875 -08:00 | 0142302107 | 014232111 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {8EFEBB35-6644-4911-A585-016D52D91B89}
5298 | 4067 | {CFDD3820-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN RAMON | Bank 4 | CB 2108 | PGE\MXT7 | 2016-11-10 11:53:10.4786963 -08:00 | 0142302108 | 014232112 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 674 | 25.47 | 25.22 | 674 | 25.47 | 25.22 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {A11AE876-7B12-4D8E-A1E7-64DD0BB18E55}
5299 | 4069 | {7530FDEA-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | RICE | Bank 1 | CB 1101 | PGE\TEJ2 | 2016-11-10 12:14:14.3313911 -08:00 | 0628301101 | 014232113 | 8 | 3 | 3 | 1 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 |  |  | FALSE | FALSE | 481 | 601 | 577 | 601 | {4111AC66-1445-47D7-9FD1-EA860514059E}
5300 | 4069 | {7530FE10-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | RICE | Bank 1 | CB 1102 | PGE\TEJ2 | 2016-11-10 12:19:17.9613322 -08:00 | 0628301102 | 014232114 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 481 | 601 | 577 | 601 | {B2B166C6-4EE4-403A-9FB4-98D868F40C2C}
5301 | 4070 | {7530FE4D-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | RICE | Bank 2 | CB 1103 | PGE\TEJ2 | 2016-11-10 12:25:24.3347075 -08:00 | 0628301103 | 153781102 | 8 | 3 | 3 | 1 | 171 | 3.73 | 3.69 | 171 | 3.73 | 3.69 | 223 | 4.87 | 4.82 | 223 | 4.87 | 4.82 | 206 | 4.5 | 4.46 | 206 | 4.5 | 4.46 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 |  |  | FALSE | FALSE | 171 | 223 | 206 | 257 | {F0772A81-F341-4DA2-B80E-114238EF2E40}
5302 | 4071 | {CFDD382C-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN RAMON | Bank 5 | CB 2110 | PGE\MXT7 | 2016-11-10 12:49:15.4883389 -08:00 | 0142302110 | 014232116 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {168A423E-4A0F-4E70-A230-8C74D58BD388}
5303 | 4071 | {CFDD384A-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN RAMON | Bank 5 | CB 2111 | PGE\MXT7 | 2016-11-10 12:52:53.7065737 -08:00 | 0142302111 | 014232117 | 12 | 3 | 3 | 1 | 530 | 20.03 | 19.83 | 530 | 20.03 | 19.83 | 720 | 27.21 | 26.94 | 720 | 27.21 | 26.94 | 634 | 23.96 | 23.72 | 634 | 23.96 | 23.72 | 720 | 27.21 | 26.94 | 720 | 27.21 | 26.94 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {401F0C78-368B-4850-8AE7-5B72C0EFDEA8}
5305 | 4071 | {781699DC-FDD3-11E5-9D37-D4BED91EFF1A} | MISSION | SAN RAMON | Bank 5 | CB 2112 (Non-SCADA) | PGE\MXT7 | 2016-11-10 12:58:49.7218101 -08:00 | 0142302112 | 153781103 | 12 | 3 | 3 | 1 | 584 | 22.07 | 21.85 | 584 | 22.07 | 21.85 | 742 | 28.04 | 27.76 | 742 | 28.04 | 27.76 | 647 | 24.45 | 24.21 | 647 | 24.45 | 24.21 | 821 | 31.03 | 30.72 | 821 | 31.03 | 30.72 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {8262ADB6-7A3C-4BF5-922A-82183C6287EC}
5306 | 4071 | {781699DF-FDD3-11E5-9D37-D4BED91EFF1A} | MISSION | SAN RAMON | Bank 5 | CB 2113 (Non-SCADA) | PGE\MXT7 | 2016-11-10 13:02:29.7955406 -08:00 | 0142302113 | 153781104 | 12 | 3 | 3 | 1 | 584 | 22.07 | 21.85 | 584 | 22.07 | 21.85 | 742 | 28.04 | 27.76 | 742 | 28.04 | 27.76 | 647 | 24.45 | 24.21 | 647 | 24.45 | 24.21 | 821 | 31.03 | 30.72 | 821 | 31.03 | 30.72 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {56BB230B-EF1B-4EFF-A8EE-23CB0024D5CC}
5307 | 4071 | {CFDD3882-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN RAMON | Bank 5 | CB 2114 | PGE\MXT7 | 2016-11-10 13:06:21.2450173 -08:00 | 0142302114 | 014232118 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {3939B08C-9C83-4035-ADFC-5733FDC27B6B}
5308 | 4072 | {473E9D9A-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | BOGUE | Bank 1 | CB 1102 | PGE\HSA1 | 2016-12-01 17:17:38.4385711 -08:00 | 1537801102 | 153781105 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {1D7101CD-AD7B-40B4-A330-345B5D197426}
5309 | 4074 | {CFDD38AC-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN RAMON | Bank 6 | CB 2116 | PGE\MXT7 | 2016-11-10 13:20:56.3967897 -08:00 | 0142302116 | 153781106 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 674 | 25.47 | 25.22 | 674 | 25.47 | 25.22 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {B2148A84-5250-4247-B19A-3FA3AB7035CA}
5310 | 4074 | {CFDD38CF-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN RAMON | Bank 6 | CB 2117 | PGE\MXT7 | 2016-11-10 13:26:58.5726401 -08:00 | 0142302117 | 014232119 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 674 | 25.47 | 25.22 | 674 | 25.47 | 25.22 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {7D9FC26A-DA9B-41B5-B0E1-83AA0E8EF2B9}
5311 | 4072 | {473E9DB1-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | BOGUE | Bank 1 | CB 1103 | PGE\TEJ2 | 2016-11-10 13:29:31.2570706 -08:00 | 1537801103 | 153781107 | 8 | 3 | 3 | 1 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B12034BE-2CEA-4546-A315-2D81F303CC5E}
5312 | 4072 | {473E9DBA-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | BOGUE | Bank 1 | CB 1104 | PGE\TEJ2 | 2016-11-10 13:34:46.4487092 -08:00 | 1537801104 | 014502104 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 670 | 14.62 | 14.47 | 670 | 14.62 | 14.47 | 634 | 13.84 | 13.7 | 634 | 13.84 | 13.7 | 670 | 14.62 | 14.47 | 670 | 14.62 | 14.47 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9CD76685-ED3B-4D65-9BE0-30B9C39BA3E1}
5313 | 4074 | {CFDD38D8-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN RAMON | Bank 6 | CB 2118 | PGE\MXT7 | 2016-11-10 13:37:24.5256291 -08:00 | 0142302118 | 014502105 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {3330AF61-62AB-41CE-A701-DCFB76D30A71}
5314 | 4073 | {473E9DCD-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | BOGUE | Bank 2 | CB 1105 | PGE\TEJ2 | 2016-11-10 13:38:00.4691811 -08:00 | 1537801105 | 014502106 | 8 | 3 | 3 | 1 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {8B62D0C8-6D17-44E6-B5A7-3ABADB72CC79}
5315 | 4073 | {473E9DD7-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | BOGUE | Bank 2 | CB 1106 | PGE\TEJ2 | 2016-11-10 13:41:42.0259431 -08:00 | 1537801106 | 014502107 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {52CAB18B-4E6C-4DDE-B1FC-FF655C617B32}
5316 | 4074 | {CFDD38F1-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN RAMON | Bank 6 | CB 2119 | PGE\MXT7 | 2016-11-10 13:54:04.2483640 -08:00 | 0142302119 | 014502108 | 12 | 3 | 3 | 1 | 530 | 20.03 | 19.83 | 530 | 20.03 | 19.83 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 634 | 23.96 | 23.72 | 634 | 23.96 | 23.72 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {47FA0356-3ACF-41DC-B579-5CA981ECB059}
5317 | 4073 | {473E9DFC-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | BOGUE | Bank 2 | CB 1107 | PGE\TEJ2 | 2016-11-10 13:56:42.3075494 -08:00 | 1537801107 | 014502109 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {DBC76081-DB71-449D-909F-C7D2C0607D3F}
5320 | 4075 | {D5F174D1-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | VINEYARD | Bank 1 | CB 2104 | PGE\ACT0 | 2017-05-03 14:21:30.1606633 -07:00 | 0145002104 | 014502110 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {1BD3CA66-91E1-4434-8E30-DB59C8D6BAC6}
5321 | 4075 | {D5F174EB-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | VINEYARD | Bank 1 | CB 2105 | PGE\ACT0 | 2017-05-03 14:22:57.4309791 -07:00 | 0145002105 | 062061102 | 12 | 3 | 3 | 1 | 573 | 21.66 | 21.44 | 573 | 21.66 | 21.44 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 634 | 23.96 | 23.72 | 634 | 23.96 | 23.72 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {C54F733E-6B0A-400F-8A09-07DDCE6EA88E}
5322 | 4075 | {D5F17505-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | VINEYARD | Bank 1 | CB 2106 | PGE\MXT7 | 2016-11-10 14:41:13.7415733 -08:00 | 0145002106 | 062061103 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 674 | 25.47 | 25.22 | 674 | 25.47 | 25.22 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {FB604E57-9E6F-42E5-9E21-09E9B82D2D34}
5323 | 4076 | {D5F17529-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | VINEYARD | Bank 2 | CB 2107 | PGE\MXT7 | 2016-11-10 14:46:21.8126781 -08:00 | 0145002107 | 062061104 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 720 | 27.21 | 26.94 | 720 | 27.21 | 26.94 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {14CC1B76-C0A4-4AAA-B24D-2EA8AEFB9FE4}
5324 | 4076 | {D5F1754E-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | VINEYARD | Bank 2 | CB 2108 | PGE\MXT7 | 2016-11-10 14:52:29.8696183 -08:00 | 0145002108 | 062061105 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 720 | 27.21 | 26.94 | 720 | 27.21 | 26.94 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {66D69D9D-84A6-47BB-9E6D-A4ACE39AE38E}
5325 | 4076 | {D5F17568-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | VINEYARD | Bank 2 | CB 2109 | PGE\MXT7 | 2016-11-10 14:56:44.6649004 -08:00 | 0145002109 | 062061106 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 674 | 25.47 | 25.22 | 674 | 25.47 | 25.22 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {BDF0C829-188A-440E-8563-C27B1DA33091}
5326 | 4076 | {D5F1757F-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | VINEYARD | Bank 2 | CB 2110 | PGE\MXT7 | 2016-11-10 14:58:54.4429362 -08:00 | 0145002110 | 062462226 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 720 | 27.21 | 26.94 | 720 | 27.21 | 26.94 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {FF445832-2BBB-4322-AC50-4D6AF72A101A}
5329 | 4016 | {53849D73-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DIXON | Bank 1 | CB 1102 | PGE\JMB4 | 2016-11-11 16:23:42.3667840 -08:00 | 0620601102 | 062462227 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F5161FDC-56B7-4FFA-A0DC-ADCD230D1DFF}
5330 | 4016 | {53849D8A-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DIXON | Bank 1 | CB 1103 | PGE\JMB4 | 2016-11-11 16:27:06.5115320 -08:00 | 0620601103 | 062462225 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 689 | 15.04 | 14.89 | 689 | 15.04 | 14.89 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 732 | 15.98 | 15.82 | 732 | 15.98 | 15.82 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {6787D49B-14EA-4753-BFBA-CA32725F920C}
5331 | 4016 | {53849DAF-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DIXON | Bank 1 | CB 1104 | PGE\JMB4 | 2016-11-11 16:30:27.6407609 -08:00 | 0620601104 | 062462223 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 689 | 15.04 | 14.89 | 689 | 15.04 | 14.89 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 732 | 15.98 | 15.82 | 732 | 15.98 | 15.82 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B2D45F4F-7A7B-444A-8EB8-DB7EEF4B448A}
5337 | 4022 | {53849DC2-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DIXON | Bank 2 | CB 1105 | PGE\JMB4 | 2016-11-11 16:53:17.4535870 -08:00 | 0620601105 | 062462224 | 8 | 3 | 3 | 1 | 745 | 16.26 | 16.1 | 745 | 16.26 | 16.1 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 7939 | 9383 | 9623 | 9623 | {D742563B-BD4F-431B-BF58-E316DB4087C1}
5339 | 4022 | {53849DD9-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | DIXON | Bank 2 | CB 1106 | PGE\JMB4 | 2016-11-11 16:51:57.9681500 -08:00 | 0620601106 | 063681105 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 689 | 15.04 | 14.89 | 689 | 15.04 | 14.89 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 732 | 15.98 | 15.82 | 732 | 15.98 | 15.82 |  |  | FALSE | FALSE | 7939 | 9383 | 9623 | 9623 | {3E9E2DD1-2834-42CF-A8DD-3264DB351471}
5341 | 4080 | {5A803627-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | GRAND ISLAND | Bank 3 | CB 2226 | PGE\JMB4 | 2016-11-11 19:27:41.4553099 -08:00 | 0624602226 | 063681103 | 12 | 3 | 1 | 1 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {ECF9A66B-568D-4B4A-82B5-3C447A75F852}
5346 | 4080 | {5A803645-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | GRAND ISLAND | Bank 3 | CB 2227 | PGE\TEJ2 | 2017-03-28 11:25:15.3144541 -07:00 | 0624602227 | 063681102 | 12 | 3 | 1 | 1 | 404 | 15.27 | 15.12 | 250 | 9.45 | 9.36 | 404 | 15.27 | 15.12 | 250 | 9.45 | 9.36 | 404 | 15.27 | 15.12 | 250 | 9.45 | 9.36 | 404 | 15.27 | 15.12 | 250 | 9.45 | 9.36 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {F0C6A0E9-48AC-4EFB-83E8-70BF114FB4DE}
5348 | 4078 | {5A8035F1-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | GRAND ISLAND | Bank 2 | CB 2225 | PGE\JMB4 | 2016-11-11 21:08:04.6999037 -08:00 | 0624602225 | 062771101 | 12 | 3 | 2 | 1 | 376 | 14.21 | 14.07 | 376 | 14.21 | 14.07 | 420 | 15.87 | 15.71 | 420 | 15.87 | 15.71 | 482 | 18.22 | 18.04 | 482 | 18.22 | 18.04 | 515 | 19.46 | 19.27 | 515 | 19.46 | 19.27 |  |  | FALSE | FALSE | 476 | 619 | 571 | 714 | {114CFD9E-E627-4668-B267-CA53E5F16D64}
5350 | 4077 | {5A803579-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | GRAND ISLAND | Bank 1 | CB 2223 | PGE\JMB4 | 2016-11-11 20:56:54.2828919 -08:00 | 0624602223 | 062771102 | 12 | 3 | 2 | 1 | 333 | 12.59 | 12.46 | 333 | 12.59 | 12.46 | 333 | 12.59 | 12.46 | 333 | 12.59 | 12.46 | 333 | 12.59 | 12.46 | 333 | 12.59 | 12.46 | 333 | 12.59 | 12.46 | 333 | 12.59 | 12.46 |  |  | FALSE | FALSE | 476 | 619 | 571 | 714 | {3F0655E6-E4B6-40EC-9AED-321504E95CF7}
5351 | 4078 | {5A8035C4-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | GRAND ISLAND | Bank 2 | CB 2224 | PGE\JMB4 | 2016-11-11 21:02:29.6960822 -08:00 | 0624602224 | 062771103 | 12 | 3 | 2 | 1 | 476 | 17.99 | 17.81 | 476 | 17.99 | 17.81 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 |  |  | FALSE | FALSE | 476 | 619 | 571 | 714 | {BE8B3E4A-161B-4E19-9BFF-D1004CAF187D}
5354 | 4099 | {7530FDB8-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PUTAH CREEK | Bank 2 | CB 1105 | PGE\SDK6 | 2017-07-18 11:33:22.6292188 -07:00 | 0636801105 | 062051102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Caution: 600AL beyond PMH11 SW 22973 |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {8E82446A-BB6C-4BD1-A84A-7C57377DE31B}
5359 | 4089 | {6F0BC84F-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PUTAH CREEK | Bank 1 | CB 1103 | PGE\SDK6 | 2017-01-31 12:42:42.8819839 -08:00 | 0636801103 | 062051101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {6E541EC3-C069-46A7-B684-A7CFC736CF71}
5360 | 4089 | {6F0BC829-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | PUTAH CREEK | Bank 1 | CB 1102 | PGE\SDK6 | 2017-01-31 12:41:33.3206921 -08:00 | 0636801102 | 063321101 | 8 | 3 | 3 | 1 | 661 | 14.43 | 14.29 | 489 | 10.67 | 10.56 | 750 | 16.37 | 16.21 | 549 | 11.98 | 11.86 | 717 | 15.65 | 15.49 | 632 | 13.79 | 13.65 | 750 | 16.37 | 16.21 | 675 | 14.73 | 14.58 | 397AA on Grant Ave (Hwy 128). |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {8677D15E-3472-4CF3-9FE8-6DD233E33878}
5361 | 4100 | {872F7C70-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WILKINS SLOUGH | Bank 1 | CB 1101 | PGE\JMB4 | 2016-11-13 15:47:24.3072800 -08:00 | 0627701101 | 063321102 | 8 | 3 | 2 | 1 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 |  |  | FALSE | FALSE | 384 | 500 | 461 | 577 | {FBE04A34-2CCC-4FF7-A5F3-CA3D6D70D3B3}
5362 | 4100 | {872F7C87-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WILKINS SLOUGH | Bank 1 | CB 1102 | PGE\JMB4 | 2016-11-13 15:47:04.8484685 -08:00 | 0627701102 | 103081103 | 8 | 3 | 2 | 1 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 |  |  | FALSE | FALSE | 384 | 500 | 461 | 577 | {F1D21DF1-C790-46B1-BB21-F03A2042EFEB}
5363 | 4100 | {872F7CA5-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WILKINS SLOUGH | Bank 1 | CB 1103 | PGE\JMB4 | 2016-11-13 15:48:09.9799694 -08:00 | 0627701103 | 103081104 | 8 | 3 | 2 | 1 | 282 | 6.15 | 6.09 | 282 | 6.15 | 6.09 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 |  |  | FALSE | FALSE | 384 | 500 | 461 | 577 | {7A2C38C5-A3D8-4BE6-8C77-AE992BA709E1}
5373 | 4106 | {872F7CBB-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WILLIAMS | Bank 1 | CB 1102 | PGE\SDK6 | 2017-08-17 08:50:59.4805808 -07:00 | 0620501102 | 103081105 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | *Selector #2 Phase MTT Set to 480 Amps - This is for recloser bypass scenarios. Use caution with loading if this Group is in place. |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {8698307D-0AB5-4DF5-88B8-C549ADF97BA1}
5379 | 4112 | {872F7CE3-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WILLIAMS | Bank 2 | CB 1101 (Non-SCADA) | PGE\SDK6 | 2017-01-20 15:49:29.1099125 -08:00 | 0620501101 | 103081106 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 577 | 12.59 | 12.46 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 481 | 601 | 577 | 601 | {E0218166-E0C1-43ED-9AC0-63F22F555182}
5381 | 4115 | {872F7D0E-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WINTERS | Bank 1 | CB 1101 | PGE\SDK6 | 2017-01-20 15:49:54.4291994 -08:00 | 0633201101 | 103081107 | 8 | 3 | 3 | 1 | 274 | 5.98 | 5.92 | 260 | 5.67 | 5.61 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 |  |  | TRUE | FALSE | 274 | 357 | 329 | 412 | {9E774487-109F-4B89-996D-B189871616F8}
5382 | 4115 | {872F7D1F-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WINTERS | Bank 1 | CB 1102 | PGE\SDK6 | 2017-01-20 15:50:16.7064278 -08:00 | 0633201102 | 103321101 | 8 | 3 | 3 | 1 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 |  |  | TRUE | FALSE | 274 | 357 | 329 | 412 | {3A2B6D65-6089-4C23-B7A3-B8126FE56ACA}
5383 | 4116 | {80988FBB-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | BUTTE | Bank 2 | CB 1103 | PGE\JXF8 | 2016-12-02 14:08:59.9718990 -08:00 | 1030801103 | 103181101 | 8 | 4 | 4 | 1 | 502 | 10.43 | 10.33 | 502 | 10.43 | 10.33 | 595 | 12.37 | 12.25 | 595 | 12.37 | 12.25 | 545 | 11.33 | 11.22 | 545 | 11.33 | 11.22 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 |  |  | FALSE | FALSE | 769 | 1000 | 923 | 1153 | {7FF0945D-7F8A-47C3-917A-877E2393AEF8}
5384 | 4116 | {80988FD9-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | BUTTE | Bank 2 | CB 1104 | PGE\JXF8 | 2016-12-02 14:11:42.6593684 -08:00 | 1030801104 | 103181102 | 8 | 4 | 4 | 1 | 591 | 12.28 | 12.16 | 591 | 12.28 | 12.16 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 |  |  | FALSE | FALSE | 769 | 1000 | 923 | 1153 | {0EC580FC-785B-49A2-8E31-A8C036A66B52}
5385 | 4118 | {80989008-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | BUTTE | Bank 3 | CB 1105 | PGE\JXF8 | 2016-12-02 14:15:59.2518570 -08:00 | 1030801105 | 103091101 | 8 | 4 | 4 | 1 | 502 | 10.43 | 10.33 | 502 | 10.43 | 10.33 | 595 | 12.37 | 12.25 | 595 | 12.37 | 12.25 | 545 | 11.33 | 11.22 | 545 | 11.33 | 11.22 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 |  |  | FALSE | FALSE | 1443 | 1876 | 1732 | 2165 | {9FF358F3-C8F7-4227-BAA2-9A9C7B41C6E9}
5386 | 4118 | {8098901F-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | BUTTE | Bank 3 | CB 1106 | PGE\JXF8 | 2016-12-02 14:17:15.2627790 -08:00 | 1030801106 | 103091102 | 8 | 4 | 4 | 1 | 591 | 12.28 | 12.16 | 591 | 12.28 | 12.16 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 |  |  | FALSE | FALSE | 1443 | 1876 | 1732 | 2165 | {CC169D8F-43DF-4C81-9951-F89B044B3FFC}
5387 | 4118 | {8098902F-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | BUTTE | Bank 3 | CB 1107 | PGE\JXF8 | 2016-12-02 14:17:46.2500922 -08:00 | 1030801107 | 102171101 | 8 | 4 | 4 | 1 | 591 | 12.28 | 12.16 | 591 | 12.28 | 12.16 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 |  |  | FALSE | FALSE | 1443 | 1876 | 1732 | 2165 | {8EF88C1F-9E2C-4B26-9738-F905F0BAF643}
5389 | 4119 | {809890A3-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CEDAR CREEK | Bank 1 | CB 1101 | PGE\JXF8 | 2016-11-13 19:53:05.0059917 -08:00 | 1033201101 | 102171102 | 8 | 4 | 4 | 2 | 110 | 2.29 | 2.27 | 110 | 2.29 | 2.27 | 110 | 2.29 | 2.27 | 110 | 2.29 | 2.27 | 110 | 2.29 | 2.27 | 110 | 2.29 | 2.27 | 110 | 2.29 | 2.27 | 110 | 2.29 | 2.27 |  |  | FALSE | FALSE | 288 | 375 | 346 | 433 | {C1C43C39-6830-4C02-AB19-3316836B8844}
5390 | 4121 | {809890FA-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CHESTER | Bank 1 | CB 1101 | PGE\SDK6 | 2017-01-24 12:08:57.7708749 -08:00 | 1031801101 | 102171103 | 8 | 3 | 3 | 1 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 |  |  | TRUE | FALSE | 304 | 396 | 365 | 457 | {452C2BE1-D823-4E35-82DC-51C0E83B0822}
5391 | 4121 | {80989103-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CHESTER | Bank 1 | CB 1102 | PGE\SDK6 | 2017-01-24 12:10:29.9374473 -08:00 | 1031801102 | 163451702 | 8 | 3 | 3 | 1 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 |  |  | TRUE | FALSE | 304 | 396 | 365 | 457 | {B4383EEE-5704-491C-94EC-053FB99E738F}
5392 | 4122 | {86A61B23-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CLARK ROAD | Bank 1 | CB 1101 | PGE\JXF8 | 2016-12-02 14:22:06.0872778 -08:00 | 1030901101 | 163310401 | 8 | 4 | 4 | 1 | 250 | 5.2 | 5.15 | 250 | 5.2 | 5.15 | 250 | 5.2 | 5.15 | 250 | 5.2 | 5.15 | 250 | 5.2 | 5.15 | 250 | 5.2 | 5.15 | 250 | 5.2 | 5.15 | 250 | 5.2 | 5.15 |  |  | FALSE | FALSE | 505 | 626 | 606 | 626 | {DF6FCD55-4F58-48F9-BE51-B0C6A79F6D34}
5395 | 4122 | {86A61B2C-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CLARK ROAD | Bank 1 | CB 1102 | PGE\JXF8 | 2016-12-02 14:22:55.2610202 -08:00 | 1030901102 | 163310402 | 8 | 4 | 4 | 1 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 |  |  | FALSE | FALSE | 505 | 626 | 606 | 626 | {3E49B4FC-B76E-430B-8190-AC4CB2B1EEDB}
5396 | 4124 | {8D2988EF-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | ESQUON | Bank 1 | CB 1101 | PGE\JXF8 | 2016-11-13 21:08:48.6958188 -08:00 | 1021701101 | 163310403 | 8 | 4 | 4 | 1 | 360 | 7.48 | 7.41 | 360 | 7.48 | 7.41 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 |  |  | FALSE | FALSE | 360 | 469 | 433 | 541 | {26A8FA4B-F65E-4A9E-BA72-8FEC7ADE4B71}
5398 | 4124 | {8D298906-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | ESQUON | Bank 1 | CB 1102 | PGE\JXF8 | 2016-11-13 21:11:04.4159165 -08:00 | 1021701102 | 163310404 | 8 | 4 | 4 | 1 | 360 | 7.48 | 7.41 | 360 | 7.48 | 7.41 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 |  |  | FALSE | FALSE | 360 | 469 | 433 | 541 | {6F9A6503-9C43-4BF4-B1D3-4ABA71CF07D2}
5399 | 4124 | {8D298916-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | ESQUON | Bank 1 | CB 1103 | PGE\JXF8 | 2016-11-13 21:13:14.5188549 -08:00 | 1021701103 | 163310405 | 8 | 4 | 4 | 1 | 360 | 7.48 | 7.41 | 360 | 7.48 | 7.41 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 | 400 | 8.31 | 8.23 |  |  | FALSE | FALSE | 360 | 469 | 433 | 541 | {6F7E732F-FA44-4B9C-8232-372CB692D3E8}
5400 | 4125 | {369797A2-671D-11E5-80CA-005056A729E5} | STOCKTON | FROGTOWN | Bank 2 | CB 1702 | PGE\BXYD | 2017-01-12 14:58:36.2117769 -08:00 | 1634501702 | 163310406 | 10 | 3 | 3 | 1 | 517 | 15.98 | 15.82 | 517 | 15.98 | 15.82 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 |  |  | FALSE | FALSE | 517 | 672 | 621 | 776 | {6F3C6293-EBDF-44C8-B26E-079286A8BEE7}
5401 | 4126 | {36979806-671D-11E5-80CA-005056A729E5} | STOCKTON | HARDING | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\JLDe | 2017-03-13 12:35:12.1268473 -07:00 | 163310401 | 163881101 | 4 | 3 | 3 | 1 | 306 | 2.32 | 2.3 | 306 | 2.32 | 2.3 | 331 | 2.51 | 2.48 | 331 | 2.51 | 2.48 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 370 | 2.8 | 2.77 | 370 | 2.8 | 2.77 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {9173DE2E-2C10-4C1F-83EA-3687121C273C}
5402 | 4126 | {36979809-671D-11E5-80CA-005056A729E5} | STOCKTON | HARDING | Bank 1 (Non SCADA) | CB 402 (Non-SCADA) | PGE\BXYD | 2017-01-12 14:32:19.1820678 -08:00 | 163310402 | 162771101 | 4 | 3 | 3 | 1 | 422 | 3.19 | 3.16 | 422 | 3.19 | 3.16 | 517 | 3.91 | 3.87 | 494 | 3.74 | 3.7 | 468 | 3.54 | 3.5 | 468 | 3.54 | 3.5 | 517 | 3.91 | 3.87 | 517 | 3.91 | 3.87 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {0E8AC21E-A822-4A75-ACA7-2CD44CE03F5F}
5403 | 4126 | {3697980C-671D-11E5-80CA-005056A729E5} | STOCKTON | HARDING | Bank 1 (Non SCADA) | CB 403 (Non-SCADA) | PGE\JLDe | 2017-03-13 12:34:18.8050219 -07:00 | 163310403 | 162771102 | 4 | 3 | 3 | 1 | 324 | 2.45 | 2.43 | 324 | 2.45 | 2.43 | 356 | 2.69 | 2.66 | 356 | 2.69 | 2.66 | 367 | 2.78 | 2.75 | 367 | 2.78 | 2.75 | 403 | 3.05 | 3.02 | 403 | 3.05 | 3.02 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {27432279-23B0-44C8-963F-542B4A08D1F8}
5405 | 4127 | {36979812-671D-11E5-80CA-005056A729E5} | STOCKTON | HARDING | Bank 2 (Non SCADA) | CB 404 (Non-SCADA) | PGE\JLDe | 2017-03-13 12:28:43.5389746 -07:00 | 163310404 | 162771103 | 4 | 3 | 3 | 1 | 306 | 2.32 | 2.3 | 306 | 2.32 | 2.3 | 331 | 2.51 | 2.48 | 331 | 2.51 | 2.48 | 343 | 2.6 | 2.57 | 343 | 2.6 | 2.57 | 370 | 2.8 | 2.77 | 370 | 2.8 | 2.77 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {5D64186C-AAB0-4D50-A871-A7644E215EF7}
5406 | 4127 | {36979815-671D-11E5-80CA-005056A729E5} | STOCKTON | HARDING | Bank 2 (Non SCADA) | CB 405 (Non-SCADA) | PGE\BXYD | 2017-01-12 14:35:38.3797447 -08:00 | 163310405 | 162771105 | 4 | 3 | 3 | 1 | 434 | 3.28 | 3.25 | 412 | 3.12 | 3.09 | 486 | 3.68 | 3.64 | 461 | 3.49 | 3.46 | 517 | 3.91 | 3.87 | 517 | 3.91 | 3.87 | 517 | 3.91 | 3.87 | 517 | 3.91 | 3.87 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {921731D6-7652-44A6-8675-FE4E834F28FD}
5407 | 4127 | {36979818-671D-11E5-80CA-005056A729E5} | STOCKTON | HARDING | Bank 2 (Non SCADA) | CB 406 (Non-SCADA) | PGE\BXYD | 2017-01-12 14:37:15.3655664 -08:00 | 163310406 | 162771106 | 4 | 3 | 3 | 1 | 344 | 2.6 | 2.57 | 344 | 2.6 | 2.57 | 378 | 2.86 | 2.83 | 378 | 2.86 | 2.83 | 389 | 2.94 | 2.91 | 389 | 2.94 | 2.91 | 428 | 3.24 | 3.21 | 428 | 3.24 | 3.21 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {F179FA37-4B12-487F-A5F2-890C94E00AD1}
5408 | 4128 | {3697982D-671D-11E5-80CA-005056A729E5} | STOCKTON | IONE | Bank 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\BXYD | 2017-01-12 11:51:47.5555270 -08:00 | 1638801101 | 162771107 | 8 | 3 | 3 | 1 | 572 | 12.48 | 12.36 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {3C044880-7D1A-4ABC-95C1-CF9B2D011137}
5409 | 4129 | {36979836-671D-11E5-80CA-005056A729E5} | STOCKTON | LAMMERS | Bank 1 | CB 1101 | PGE\BXYD | 2017-01-12 11:40:52.2265262 -08:00 | 1627701101 | 162071101 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {BD1B8F24-2690-4966-AA20-5B672A214D1C}
5410 | 4129 | {3697983B-671D-11E5-80CA-005056A729E5} | STOCKTON | LAMMERS | Bank 1 | CB 1102 | PGE\BXYD | 2017-01-12 11:42:42.8000350 -08:00 | 1627701102 | 162071102 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 570 | 12.44 | 12.32 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {96DBD85E-9921-4167-B14E-0609B3F6B64F}
5411 | 4129 | {36979840-671D-11E5-80CA-005056A729E5} | STOCKTON | LAMMERS | Bank 1 | CB 1103 | PGE\ACT0 | 2016-11-14 13:58:46.9342227 -08:00 | 1627701103 | 162071103 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F570DF4C-BF46-400D-A4DA-8C5F1A787D6B}
5412 | 4130 | {3697984B-671D-11E5-80CA-005056A729E5} | STOCKTON | LAMMERS | Bank 2 | CB 1105 | PGE\BXYD | 2017-01-12 11:46:36.0215300 -08:00 | 1627701105 | 162071104 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {237E32D6-682A-43C9-8B62-F66ECF6D42E1}
5413 | 4130 | {36979850-671D-11E5-80CA-005056A729E5} | STOCKTON | LAMMERS | Bank 2 | CB 1106 | PGE\BXYD | 2017-01-12 11:48:00.2620700 -08:00 | 1627701106 | 163682101 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {59B50BE7-A900-4794-8962-6279A7B377CE}
5414 | 4130 | {36979855-671D-11E5-80CA-005056A729E5} | STOCKTON | LAMMERS | Bank 2 | CB 1107 | PGE\BXYD | 2017-01-12 11:48:46.4851663 -08:00 | 1627701107 | 163682102 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {4C20FC6D-40BE-4B39-9669-60AB8761F320}
5415 | 4131 | {36979863-671D-11E5-80CA-005056A729E5} | STOCKTON | LINDEN | Bank 1 | CB 1101 | PGE\BXYD | 2017-01-12 11:34:53.5646271 -08:00 | 1620701101 | 162111101 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {2B1293D5-1A56-462C-9F54-F1F40A869244}
5416 | 4131 | {3697986B-671D-11E5-80CA-005056A729E5} | STOCKTON | LINDEN | Bank 1 | CB 1102 | PGE\BXYD | 2017-01-12 11:35:19.6479943 -08:00 | 1620701102 | 162111102 | 8 | 3 | 3 | 1 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 | 483 | 10.54 | 10.43 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {72ACDB55-B4F4-478C-A8AE-91CBB1CA6C66}
5417 | 4131 | {36979870-671D-11E5-80CA-005056A729E5} | STOCKTON | LINDEN | Bank 1 | CB 1103 | PGE\BXYD | 2017-01-12 11:36:04.7634835 -08:00 | 1620701103 | 024091101 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {E255C2DF-CD8C-47C2-91CF-31CECE6A87C3}
5418 | 4131 | {3697987E-671D-11E5-80CA-005056A729E5} | STOCKTON | LINDEN | Bank 1 | CB 1104 | PGE\BXYD | 2017-01-12 11:36:28.5692361 -08:00 | 1620701104 | 024090404 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {5B77E307-AF21-4784-9B8C-19D250EAE8DA}
5419 | 4133 | {36979892-671D-11E5-80CA-005056A729E5} | STOCKTON | LOCKEFORD | Bank 4 | CB 2101 | PGE\BXYD | 2017-01-12 11:32:41.0105774 -08:00 | 1636802101 | 024090405 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {190CB6D1-0461-4995-98E0-0C1913FB6396}
5420 | 4133 | {369798AF-671D-11E5-80CA-005056A729E5} | STOCKTON | LOCKEFORD | Bank 4 | CB 2102 | PGE\BXYD | 2017-01-12 11:33:13.7239871 -08:00 | 1636802102 | 024090406 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 617 | 23.32 | 23.09 | 617 | 23.32 | 23.09 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 617 | 23.32 | 23.09 | 617 | 23.32 | 23.09 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {EBA3D97A-A94F-411F-A464-F2C14773E714}
5421 | 4134 | {369798E7-671D-11E5-80CA-005056A729E5} | STOCKTON | LODI | Bank 2 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\BXYD | 2017-01-12 11:30:16.0232480 -08:00 | 1621101101 | 024091102 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {39EA796D-CB5D-4359-9F5A-7222E9CF7BD0}
5422 | 4134 | {369798ED-671D-11E5-80CA-005056A729E5} | STOCKTON | LODI | Bank 2 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\BXYD | 2017-01-12 11:31:13.8684188 -08:00 | 1621101102 | 024080401 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {39D76634-08EA-48A2-B060-46446ED8BA48}
5423 | 4135 | {25CD646E-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | GLENWOOD | Bank 1 | CB 1101 | PGE\C7CF | 2016-11-14 17:43:14.9936507 -08:00 | 0240901101 | 024080402 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 842 | 842 | 842 | {AD3D0D03-29AA-4644-9BC0-B8D0F7B07E02}
5424 | 4136 | {25CD648F-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | GLENWOOD | Bank 2 | CB 404 | PGE\C7CF | 2016-11-14 17:46:44.6663031 -08:00 | 024090404 | 103341101 | 4 | 3 | 3 | 2 | 378 | 2.86 | 2.83 | 378 | 2.86 | 2.83 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 389 | 2.94 | 2.91 | 389 | 2.94 | 2.91 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {153D0E38-9DF7-4444-93F1-1E9783090E38}
5425 | 4136 | {25CD649F-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | GLENWOOD | Bank 2 | CB 405 | PGE\C7CF | 2016-11-14 17:48:13.7619369 -08:00 | 024090405 | 103541105 | 4 | 3 | 3 | 2 | 378 | 2.86 | 2.83 | 378 | 2.86 | 2.83 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 389 | 2.94 | 2.91 | 389 | 2.94 | 2.91 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {8807018E-4CDD-48E4-BF72-5DDF0E5EF420}
5426 | 4136 | {25CD64AF-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | GLENWOOD | Bank 2 | CB 406 | PGE\C7CF | 2016-11-14 17:51:22.2436427 -08:00 | 024090406 | 162611702 | 4 | 3 | 3 | 2 | 462 | 3.5 | 3.46 | 462 | 3.5 | 3.46 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 471 | 3.57 | 3.53 | 471 | 3.57 | 3.53 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {C871A074-9774-470C-81D3-3A36F2663545}
5427 | 4137 | {25CD64C9-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | GLENWOOD | Bank 3 | CB 1102 | PGE\C7CF | 2016-11-14 17:54:27.1480688 -08:00 | 0240901102 | 162611703 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 842 | 842 | 842 | {DE97AD89-DBE1-4B25-8FF3-8F58804E906F}
5428 | 4138 | {25CD645B-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | EMERALD LAKE | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2017-07-05 17:22:38.0572540 -07:00 | 024080401 | 162611704 | 4 | 3 | 3 | 2 | 336 | 2.54 | 2.51 | 319 | 2.41 | 2.39 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {F1EF2D16-18CB-4AE7-85ED-B039E93AF16B}
5429 | 4138 | {25CD645E-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | EMERALD LAKE | Bank 1 (Non SCADA) | CB 402 (Non-SCADA) | PGE\C7CF | 2017-07-05 17:22:29.3052052 -07:00 | 024080402 | 162611705 | 4 | 3 | 3 | 2 | 336 | 2.54 | 2.51 | 319 | 2.41 | 2.39 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 382 | 2.89 | 2.86 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {0A053258-E4C3-45BD-AD16-1F39E792D54A}
5430 | 4139 | {8D298844-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | DAIRYVILLE | Bank 1 | CB 1101 | PGE\CTD7 | 2017-04-19 17:02:44.7795471 -07:00 | 1033401101 | 162611701 | 8 | 3 | 3 | 1 | 206 | 4.5 | 4.46 | 206 | 4.5 | 4.46 | 248 | 5.41 | 5.36 | 235 | 5.13 | 5.08 | 247 | 5.39 | 5.34 | 247 | 5.39 | 5.34 | 300 | 6.55 | 6.48 | 286 | 6.24 | 6.18 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 206 | 268 | 247 | 309 | {A0F91578-E1F0-4ED4-A353-C6C2AF03F7E5}
5431 | 4140 | {A6861CDA-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | RED BLUFF | Bank 2 | CB 1105 | PGE\CTD7 | 2017-04-19 17:08:37.7015422 -07:00 | 1035401105 | 162611706 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.39 | 481 | 10.5 | 10.39 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 481 | 601 | 577 | 601 | {0D0D4B2A-87FC-4096-9286-76B5634397D9}
5433 | 4141 | {3C91ACFA-671D-11E5-80CA-005056A729E5} | STOCKTON | MANTECA | Bank 5 | CB 1702 | PGE\JLDe | 2017-05-22 16:24:17.7654472 -07:00 | 1626101702 | 162611707 | 10 | 1 | 1 | 1 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 |  |  | FALSE | FALSE | 898 | 1167 | 1078 | 1167 | {4DE410CB-2B0B-4EFB-9594-FA6A187C2B9B}
5434 | 4141 | {3C91ACFF-671D-11E5-80CA-005056A729E5} | STOCKTON | MANTECA | Bank 5 | CB 1703 | PGE\JLDe | 2017-05-22 16:26:17.4072155 -07:00 | 1626101703 | 162611708 | 10 | 1 | 1 | 1 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 |  |  | FALSE | FALSE | 898 | 1167 | 1078 | 1167 | {58D236C9-7E8A-4544-A07F-8DAA36479C71}
5436 | 4142 | {3C91AD19-671D-11E5-80CA-005056A729E5} | STOCKTON | MANTECA | Bank 6 | CB 1704 | PGE\BXYD | 2017-01-12 08:48:12.2916514 -08:00 | 1626101704 | 163011101 | 10 | 1 | 1 | 1 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 |  |  | FALSE | FALSE | 910 | 1183 | 1092 | 1365 | {E63B5122-A60E-490A-8FD9-5C0B918C4B31}
5437 | 4142 | {3C91AD27-671D-11E5-80CA-005056A729E5} | STOCKTON | MANTECA | Bank 6 | CB 1705 | PGE\BXYD | 2017-01-12 08:49:12.5392376 -08:00 | 1626101705 | 163011102 | 10 | 1 | 1 | 1 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 |  |  | FALSE | FALSE | 910 | 1183 | 1092 | 1365 | {AB862092-A819-4D06-9F61-BC43AB283344}
5438 | 4143 | {3C91AD3B-671D-11E5-80CA-005056A729E5} | STOCKTON | MANTECA | Bank 7 | CB 1701 | PGE\BXYD | 2017-01-12 08:58:47.4029226 -08:00 | 1626101701 | 163011103 | 10 | 1 | 1 | 1 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 |  |  | FALSE | FALSE | 970 | 1261 | 1164 | 1455 | {904AD594-66CC-4F05-97F7-FAE2EAAFD875}
5439 | 4143 | {3C91AD5B-671D-11E5-80CA-005056A729E5} | STOCKTON | MANTECA | Bank 7 | CB 1706 | PGE\BXYD | 2017-01-12 09:07:06.8245240 -08:00 | 1626101706 | 082012101 | 10 | 3 | 3 | 1 | 530 | 16.39 | 16.23 | 530 | 16.39 | 16.23 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 | 600 | 18.55 | 18.36 | 570 | 17.62 | 17.44 |  |  | FALSE | FALSE | 970 | 1261 | 1164 | 1455 | {9496F2DB-02CD-4A6F-ADE9-5BAA766549D0}
5440 | 4144 | {3C91AD78-671D-11E5-80CA-005056A729E5} | STOCKTON | MANTECA | Bank 8 | CB 1707 | PGE\JCD5 | 2017-05-22 11:29:18.5257281 -07:00 | 1626101707 | 162091101 | 10 | 1 | 1 | 1 | 636 | 19.66 | 19.46 | 636 | 19.66 | 19.46 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 |  |  | FALSE | FALSE | 970 | 1261 | 1164 | 1421 | {1E0B6574-7B79-4BFF-B47D-2CE7BE716FBB}
5441 | 4144 | {3C91AD83-671D-11E5-80CA-005056A729E5} | STOCKTON | MANTECA | Bank 8 | CB 1708 | PGE\BXYD | 2017-01-12 11:28:41.2838407 -08:00 | 1626101708 | 082012102 | 10 | 1 | 1 | 1 | 636 | 19.66 | 19.46 | 636 | 19.66 | 19.46 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 | 650 | 20.1 | 19.9 |  |  | FALSE | FALSE | 970 | 1261 | 1164 | 1421 | {B0163383-7E9C-436C-A7FD-17332BCB3FCC}
5442 | 4145 | {3C91AD9A-671D-11E5-80CA-005056A729E5} | STOCKTON | MARTELL | Bank 1 | CB 1101 | PGE\BXYD | 2017-01-12 08:17:08.3137029 -08:00 | 1630101101 | 162091102 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 489 | 10.67 | 10.56 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1440 | {BAF8CEA0-3E38-4F1D-A465-26BC504D4D10}
5443 | 4145 | {3C91ADA2-671D-11E5-80CA-005056A729E5} | STOCKTON | MARTELL | Bank 1 | CB 1102 | PGE\ACT0 | 2016-11-15 10:49:34.6730219 -08:00 | 1630101102 | 162091103 | 8 | 3 | 3 | 1 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1443 | {C256703C-6190-4D6E-B9C0-24F9C7C5EE7E}
5444 | 4145 | {3C91ADA7-671D-11E5-80CA-005056A729E5} | STOCKTON | MARTELL | Bank 1 | CB 1103 | PGE\VXRO | 2017-02-08 17:53:02.9757469 -08:00 | 1630101103 | 162300401 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 962 | 1250 | 1154 | 1440 | {F479D7BC-A01E-456D-A738-C352935777A3}
5445 | 4146 | {DC00D0DE-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | EVERGREEN | Bank 2 | CB 2101 | PGE\ALWK | 2016-11-15 12:01:41.2889737 -08:00 | 0820102101 | 162300402 | 22 | 3 | 3 | 2 | 513 | 18.46 | 18.28 | 513 | 18.46 | 18.28 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 | 528 | 19 | 18.81 | 528 | 19 | 18.81 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {801E8B12-17E9-4FF4-98E0-B6DA04F5A0A9}
5447 | 4147 | {3C91ADC5-671D-11E5-80CA-005056A729E5} | STOCKTON | MIDDLE RIVER | Bank 1 | CB 1101 | PGE\ACT0 | 2016-11-15 14:12:39.2420493 -08:00 | 1620901101 | 162300403 | 8 | 1 | 1 | 1 | 183 | 3.99 | 3.95 | 183 | 3.99 | 3.95 | 211 | 4.6 | 4.55 | 211 | 4.6 | 4.55 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 |  |  | FALSE | FALSE | 274 | 357 | 329 | 412 | {B557FB60-447D-4EB5-8BD2-208D7677219B}
5448 | 4146 | {DC00D104-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | EVERGREEN | Bank 2 | CB 2102 | PGE\ALWK | 2016-11-15 16:02:43.4125242 -08:00 | 0820102102 | 082012103 | 22 | 3 | 3 | 2 | 541 | 19.47 | 19.28 | 541 | 19.47 | 19.28 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 | 557 | 20.05 | 19.85 | 557 | 20.05 | 19.85 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {6AD70BD3-08FC-4F24-87F8-F13B2CEAD9A8}
5449 | 4147 | {3C91ADCA-671D-11E5-80CA-005056A729E5} | STOCKTON | MIDDLE RIVER | Bank 1 | CB 1102 | PGE\BXYD | 2017-01-11 17:21:21.6574249 -08:00 | 1620901102 | 163211101 | 8 | 1 | 1 | 1 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 |  |  | FALSE | FALSE | 274 | 357 | 329 | 412 | {B7E9C5A3-2708-40EA-A8DF-B287F7B844CE}
5450 | 4147 | {3C91ADD8-671D-11E5-80CA-005056A729E5} | STOCKTON | MIDDLE RIVER | Bank 1 | CB 1103 | PGE\BXYD | 2017-01-11 17:21:52.2652135 -08:00 | 1620901103 | 163211102 | 8 | 1 | 1 | 1 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 |  |  | FALSE | FALSE | 274 | 357 | 329 | 412 | {5DCDAE02-A10A-426F-8B9C-ADE54EA1F9FA}
5451 | 4148 | {3C91ADE9-671D-11E5-80CA-005056A729E5} | STOCKTON | MONARCH | Bank 2 (Non SCADA) | CB 401 (Non-SCADA) | PGE\ACT0 | 2016-11-15 14:29:44.1675079 -08:00 | 162300401 | 163211103 | 4 | 3 | 3 | 1 | 345 | 2.61 | 2.58 | 345 | 2.61 | 2.58 | 386 | 2.92 | 2.89 | 386 | 2.92 | 2.89 | 394 | 2.98 | 2.95 | 394 | 2.98 | 2.95 | 438 | 3.32 | 3.29 | 438 | 3.32 | 3.29 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {5FD9E59C-5874-4759-8654-1BF028A6C3F6}
5452 | 4148 | {3C91ADEC-671D-11E5-80CA-005056A729E5} | STOCKTON | MONARCH | Bank 2 (Non SCADA) | CB 402 (Non-SCADA) | PGE\JLDe | 2017-03-07 11:33:56.7438322 -08:00 | 162300402 | 014471102 | 4 | 3 | 3 | 1 | 323 | 2.44 | 2.42 | 323 | 2.44 | 2.42 | 368 | 2.79 | 2.76 | 368 | 2.79 | 2.76 | 394 | 2.98 | 2.95 | 394 | 2.98 | 2.95 | 438 | 3.32 | 3.29 | 438 | 3.32 | 3.29 |  |  | FALSE | FALSE | 924 | 1000 | 1000 | 1000 | {F8A5ABC3-A20B-4E68-B838-E34B491B2132}
5453 | 4148 | {3C91ADEF-671D-11E5-80CA-005056A729E5} | STOCKTON | MONARCH | Bank 2 (Non SCADA) | CB 403 (Non-SCADA) | PGE\JLDe | 2017-03-07 11:46:52.0787422 -08:00 | 162300403 | 014471103 | 4 | 3 | 3 | 1 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 924 | 1000 | 1000 | 1000 | {9103F057-2D91-4EA7-B7B2-07A85DD272AC}
5454 | 4146 | {DC00D15A-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | EVERGREEN | Bank 2 | CB 2103 | PGE\ALWK | 2016-11-15 16:07:30.5667932 -08:00 | 0820102103 | 014452107 | 22 | 3 | 3 | 2 | 541 | 19.47 | 19.28 | 541 | 19.47 | 19.28 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 | 557 | 20.05 | 19.85 | 557 | 20.05 | 19.85 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {E39CBCF0-E31E-4FDE-ACAF-906362F6EBE7}
5456 | 4149 | {3C91ADF8-671D-11E5-80CA-005056A729E5} | STOCKTON | MORMON | Bank 1 | CB 1101 | PGE\BXYD | 2017-01-11 15:27:44.3323125 -08:00 | 1632101101 | 014452108 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 570 | 12.44 | 12.32 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 721 | 721 | 721 | 721 | {44A922ED-5ED3-4FF4-885E-DD6D30C2EE2E}
5457 | 4149 | {3C91AE06-671D-11E5-80CA-005056A729E5} | STOCKTON | MORMON | Bank 1 | CB 1102 | PGE\BXYD | 2017-01-11 15:28:40.3058301 -08:00 | 1632101102 | 014471104 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 721 | 721 | 721 | 721 | {F0B68D64-531D-4808-B43D-85DA22FA2C11}
5458 | 4149 | {3C91AE1A-671D-11E5-80CA-005056A729E5} | STOCKTON | MORMON | Bank 1 | CB 1103 | PGE\JLDe | 2017-03-03 13:02:24.3694610 -08:00 | 1632101103 | 014452109 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 658 | 14.36 | 14.22 | 658 | 14.36 | 14.22 |  |  | FALSE | FALSE | 721 | 721 | 721 | 721 | {548C552B-FDA0-4DD1-94EF-6522EFC17BE8}
5460 | 4151 | {BD86D9AC-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DUMBARTON | Bank 1 | CB 1102 | PGE\RDR1 | 2017-06-13 09:58:56.4943548 -07:00 | 0144701102 | 082012104 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {17C5FAEC-8C42-4D93-A401-88216485749D}
5461 | 4151 | {BD86D9D8-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DUMBARTON | Bank 1 | CB 1103 | PGE\RDR1 | 2017-06-13 12:00:14.0178829 -07:00 | 0144701103 | 082012105 | 7 | 3 | 3 | 2 | 595 | 12.85 | 12.72 | 595 | 12.85 | 12.72 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {30CB8C7E-2EAB-43FC-8367-171EECC27E46}
5462 | 4150 | {F2DB7F06-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | KIRKER | Bank 3 | CB 2107 | PGE\WCL5 | 2016-11-15 16:18:05.9042210 -08:00 | 0144502107 | 163231101 | 22 | 3 | 3 | 1 | 573 | 20.62 | 20.41 | 573 | 20.62 | 20.41 | 728 | 26.2 | 25.94 | 728 | 26.2 | 25.94 | 634 | 22.82 | 22.59 | 634 | 22.82 | 22.59 | 768 | 27.64 | 27.36 | 768 | 27.64 | 27.36 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {0C90D9C9-D23B-4D57-B46D-CDD78F6BED2E}
5464 | 4150 | {F900A529-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | KIRKER | Bank 3 | CB 2108 | PGE\WCL5 | 2016-11-15 16:18:18.6017624 -08:00 | 0144502108 | 163270401 | 22 | 3 | 3 | 1 | 503 | 18.1 | 17.92 | 503 | 18.1 | 17.92 | 639 | 23 | 22.77 | 639 | 23 | 22.77 | 557 | 20.05 | 19.85 | 557 | 20.05 | 19.85 | 674 | 24.26 | 24.02 | 674 | 24.26 | 24.02 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {3923C232-6BE2-4402-AF3B-912BF36C97D5}
5465 | 4151 | {BD86D9F6-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DUMBARTON | Bank 1 | CB 1104 | PGE\RDR1 | 2017-06-13 12:00:30.4604937 -07:00 | 0144701104 | 163270402 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {08B6F21D-F445-46EC-BA9D-735C6AA8BF0B}
5466 | 4150 | {F900A540-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | KIRKER | Bank 3 | CB 2109 | PGE\WCL5 | 2016-11-15 16:40:44.0593147 -08:00 | 0144502109 | 163541101 | 22 | 3 | 3 | 1 | 573 | 20.62 | 20.41 | 573 | 20.62 | 20.41 | 667 | 24.01 | 23.77 | 667 | 24.01 | 23.77 | 634 | 22.82 | 22.59 | 634 | 22.82 | 22.59 | 667 | 24.01 | 23.77 | 667 | 24.01 | 23.77 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {FE3FFCEF-019E-43AB-B2FA-BAC7BF97BF56}
5469 | 4153 | {DC00D197-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | EVERGREEN | Bank 3 | CB 2104 | PGE\ALWK | 2016-11-15 16:49:22.1079400 -08:00 | 0820102104 | 163541102 | 22 | 4 | 4 | 2 | 471 | 16.95 | 16.78 | 471 | 16.95 | 16.78 | 579 | 20.84 | 20.63 | 579 | 20.84 | 20.63 | 485 | 17.46 | 17.29 | 485 | 17.46 | 17.29 | 587 | 21.13 | 20.92 | 587 | 21.13 | 20.92 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {CD9197E4-5B12-4C71-AC13-A9B256D09D1A}
5470 | 4153 | {DC00D1CB-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | EVERGREEN | Bank 3 | CB 2105 | PGE\ALWK | 2016-11-15 17:25:00.0803016 -08:00 | 0820102105 | 163751101 | 22 | 3 | 3 | 2 | 582 | 20.95 | 20.74 | 582 | 20.95 | 20.74 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {A0CD61A4-5FB2-4116-8703-83BEB524DF0A}
5472 | 4156 | {464AAEF0-671D-11E5-80CA-005056A729E5} | STOCKTON | NORTH BRANCH | Bank 1 | CB 1101 (Non-SCADA) | PGE\BXYD | 2017-01-11 14:54:42.2163920 -08:00 | 1632301101 | 163751102 | 8 | 3 | 3 | 1 | 274 | 5.98 | 5.92 | 274 | 5.98 | 5.92 | 357 | 7.79 | 7.71 | 357 | 7.79 | 7.71 | 329 | 7.18 | 7.11 | 329 | 7.18 | 7.11 | 412 | 8.99 | 8.9 | 412 | 8.99 | 8.9 |  |  | FALSE | FALSE | 274 | 357 | 329 | 412 | {5D605BD3-5D34-4D2E-9573-F1F7D5375C0A}
5473 | 4159 | {464AAF08-671D-11E5-80CA-005056A729E5} | STOCKTON | OAK PARK | Bank 1 | CB 401 (Non-SCADA) | PGE\ACT0 | 2016-11-16 10:11:20.8050599 -08:00 | 163270401 | 163692101 | 4 | 3 | 3 | 1 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 521 | 678 | 626 | 782 | {583F976D-B26C-41CB-A50B-E85AB9C1EC7E}
5474 | 4159 | {464AAF0B-671D-11E5-80CA-005056A729E5} | STOCKTON | OAK PARK | Bank 1 | CB 402 (Non-SCADA) | PGE\BXYD | 2017-01-11 14:52:01.8785642 -08:00 | 163270402 | 163692102 | 4 | 3 | 3 | 1 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 |  |  | FALSE | FALSE | 521 | 678 | 626 | 782 | {FB408442-4DD1-4F93-9566-5992E790F1D0}
5475 | 4160 | {464AAF14-671D-11E5-80CA-005056A729E5} | STOCKTON | OLETA | Bank 1 | CB 1101 | PGE\BXYD | 2017-01-11 14:45:06.9471044 -08:00 | 1635401101 | 163201101 | 8 | 3 | 3 | 1 | 570 | 12.44 | 12.32 | 231 | 5.04 | 4.99 | 570 | 12.44 | 12.32 | 252 | 5.5 | 5.45 | 570 | 12.44 | 12.32 | 287 | 6.26 | 6.2 | 570 | 12.44 | 12.32 | 303 | 6.61 | 6.54 |  |  | FALSE | FALSE | 570 | 570 | 570 | 570 | {341E327A-59E5-4433-9F66-8FB107A23818}
5476 | 4161 | {464AAF1F-671D-11E5-80CA-005056A729E5} | STOCKTON | OLETA | Bank 2 | CB 1102 | PGE\BXYD | 2017-01-11 14:47:32.3088362 -08:00 | 1635401102 | 162821701 | 8 | 3 | 3 | 1 | 258 | 5.63 | 5.57 | 245 | 5.35 | 5.3 | 335 | 7.31 | 7.24 | 318 | 6.94 | 6.87 | 310 | 6.77 | 6.7 | 294 | 6.42 | 6.36 | 384 | 8.38 | 8.3 | 364 | 7.94 | 7.86 |  |  | TRUE | FALSE | 258 | 335 | 310 | 384 | {B36C8DC2-294C-4304-A2C7-FCABC3BB3D18}
5477 | 4162 | {464AAF30-671D-11E5-80CA-005056A729E5} | STOCKTON | PINE GROVE | Bank 1 | CB 1101 | PGE\ACT0 | 2016-11-16 11:37:37.5342150 -08:00 | 1637501101 | 162821702 | 8 | 3 | 3 | 1 | 345 | 7.53 | 7.45 | 345 | 7.53 | 7.45 | 386 | 8.42 | 8.34 | 386 | 8.42 | 8.34 | 443 | 9.67 | 9.57 | 443 | 9.67 | 9.57 | 473 | 10.32 | 10.22 | 473 | 10.32 | 10.22 |  |  | FALSE | FALSE | 429 | 558 | 515 | 644 | {616A2678-6E78-4505-B5AF-2A942F98F5A3}
5478 | 4163 | {464AAF3B-671D-11E5-80CA-005056A729E5} | STOCKTON | PINE GROVE | Bank 2 | CB 1102 | PGE\BXYD | 2017-01-11 14:41:43.1161978 -08:00 | 1637501102 | 163201102 | 8 | 3 | 3 | 1 | 572 | 12.48 | 12.36 | 489 | 10.67 | 10.56 | 683 | 14.91 | 14.76 | 549 | 11.98 | 11.86 | 683 | 14.91 | 14.76 | 632 | 13.79 | 13.65 | 683 | 14.91 | 14.76 | 675 | 14.73 | 14.58 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {A9933FFC-F87A-4A2A-97BB-1AAD5096E821}
5479 | 4164 | {E36956EC-0B41-11E6-9D37-D4BED91EFF1A} | STOCKTON | SALT SPRINGS | BANK 2 (Non SCADA) | CB 2101 (Non-SCADA) | PGE\SZC1 | 2016-11-16 15:45:43.6385755 -08:00 | 1636902101 | 163281101 | 12 | 3 | 3 | 1 | 226 | 8.54 | 8.45 | 95 | 3.59 | 3.55 | 230 | 8.69 | 8.6 | 123 | 4.65 | 4.6 | 230 | 8.69 | 8.6 | 114 | 4.31 | 4.27 | 230 | 8.69 | 8.6 | 142 | 5.37 | 5.32 | *Cabbage Patch Step Down ( Beyond OCB) *Way Load (Generation) of 160A, 267A, 224A, 319A *Regulator R260 = 200A (237A, 266A, 285A, 314A) |  | FALSE | FALSE | 286 | 321 | 370 | 395 | {E1CFE227-9DE1-4D5E-8D80-A20EB87D46C6}
5480 | 4164 | {ECAB504D-0B41-11E6-9D37-D4BED91EFF1A} | STOCKTON | SALT SPRINGS | BANK 2 (Non SCADA) | CB 2102 (Non-SCADA) | PGE\SZC1 | 2016-11-17 08:46:05.4579529 -08:00 | 1636902102 | 163281102 | 12 | 3 | 3 | 1 | 167 | 6.31 | 6.25 | 167 | 6.31 | 6.25 | 217 | 8.2 | 8.12 | 217 | 8.2 | 8.12 | 200 | 7.56 | 7.48 | 200 | 7.56 | 7.48 | 230 | 8.69 | 8.6 | 230 | 8.69 | 8.6 |  |  | FALSE | FALSE | 286 | 321 | 370 | 395 | {37ED3A40-6C2B-488B-BB19-F6C3CCFC3DE6}
5481 | 4168 | {4C486F54-671D-11E5-80CA-005056A729E5} | STOCKTON | WEST POINT | Bank 2 (Non SCADA) | CB 1101 | PGE\BXYD | 2017-01-10 15:25:25.1914718 -08:00 | 1632001101 | 014161101 | 8 | 3 | 3 | 1 | 282 | 6.15 | 6.09 | 267 | 5.83 | 5.77 | 315 | 6.87 | 6.8 | 299 | 6.53 | 6.46 | 350 | 7.64 | 7.56 | 340 | 7.42 | 7.35 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 |  |  | FALSE | FALSE | 320 | 416 | 384 | 481 | {E2F8D5D7-6BA6-4201-BB39-1E9E788B90C7}
5482 | 4169 | {464AB039-671D-11E5-80CA-005056A729E5} | STOCKTON | STANISLAUS | Bank 2 | CB 1701 | PGE\BXYD | 2017-01-11 10:32:56.0357120 -08:00 | 1628201701 | 014161102 | 10 | 3 | 3 | 1 | 380 | 11.75 | 11.63 | 380 | 11.75 | 11.63 | 380 | 11.75 | 11.63 | 380 | 11.75 | 11.63 | 380 | 11.75 | 11.63 | 380 | 11.75 | 11.63 | 380 | 11.75 | 11.63 | 380 | 11.75 | 11.63 | * Hydro Turbin Fans Capability: SN 387A, SE 483A, WN 464A, WE 554 |  | FALSE | FALSE | 407 | 529 | 489 | 600 | {DEB960BD-4632-45E2-B666-51E561C39132}
5483 | 4169 | {464AB04A-671D-11E5-80CA-005056A729E5} | STOCKTON | STANISLAUS | Bank 2 | CB 1702 | PGE\BXYD | 2017-01-11 10:33:25.8631032 -08:00 | 1628201702 | 014161103 | 10 | 3 | 3 | 1 | 380 | 11.75 | 11.63 | 380 | 11.75 | 11.63 | 380 | 11.75 | 11.63 | 380 | 11.75 | 11.63 | 380 | 11.75 | 11.63 | 380 | 11.75 | 11.63 | 380 | 11.75 | 11.63 | 380 | 11.75 | 11.63 | *Hydro Turbin Fans on Bus Cap: SN 387A, SE 483A, WN 464A, WE 554A |  | FALSE | FALSE | 407 | 529 | 489 | 600 | {92743463-A930-4790-A771-2AB99259EFF7}
5484 | 4172 | {4C486F5C-671D-11E5-80CA-005056A729E5} | STOCKTON | WEST POINT | Bank 3 (Non SCADA) | CB 1102 | PGE\BXYD | 2017-01-10 16:12:35.5695011 -08:00 | 1632001102 | 014161104 | 8 | 3 | 3 | 1 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 |  |  | FALSE | FALSE | 481 | 481 | 481 | 481 | {13584DD4-1DB7-4958-8887-4B182ED637FE}
5485 | 4171 | {4C486E26-671D-11E5-80CA-005056A729E5} | STOCKTON | VICTOR | Bank 1 | CB 1101 | PGE\ACT0 | 2016-11-16 15:19:57.3164161 -08:00 | 1632801101 | 162881102 | 8 | 3 | 3 | 1 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | * Stepdown T31520 - 7500kVA 12kV to 21kV |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {1211635F-070D-4C23-9DA8-57A82176327F}
5487 | 4171 | {4C486E31-671D-11E5-80CA-005056A729E5} | STOCKTON | VICTOR | Bank 1 | CB 1102 | PGE\BXYD | 2017-01-10 17:16:34.4327373 -08:00 | 1632801102 | 162881103 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {4F10B7C1-9BA9-464A-8589-69BB94A509E2}
5489 | 4176 | {5C92B4D1-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | ROSSMOOR | Bank 1 | CB 1101 | PGE\MFN3 | 2016-11-30 14:34:17.4182807 -08:00 | 0141601101 | 162881104 | 8 | 3 | 3 | 1 | 661 | 14.43 | 14.29 | 661 | 14.43 | 14.29 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 717 | 15.65 | 15.49 | 717 | 15.65 | 15.49 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {88277ABA-3D7A-4D79-B422-BD3548D2BE3F}
5493 | 4176 | {6294E9E7-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | ROSSMOOR | Bank 1 | CB 1102 | PGE\MFN3 | 2016-11-30 14:34:32.5214935 -08:00 | 0141601102 | 162881105 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 728 | 15.89 | 15.73 | 728 | 15.89 | 15.73 | 634 | 13.84 | 13.7 | 634 | 13.84 | 13.7 | 768 | 16.76 | 16.59 | 768 | 16.76 | 16.59 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B85EA696-79F6-4FBE-8695-F41915F464DE}
5497 | 4176 | {6294E9EC-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | ROSSMOOR | Bank 1 | CB 1103 | PGE\MFN3 | 2016-11-30 14:34:45.1126303 -08:00 | 0141601103 | 162881106 | 8 | 3 | 3 | 1 | 231 | 5.04 | 4.99 | 231 | 5.04 | 4.99 | 252 | 5.5 | 5.44 | 252 | 5.5 | 5.44 | 287 | 6.26 | 6.2 | 287 | 6.26 | 6.2 | 303 | 6.61 | 6.54 | 303 | 6.61 | 6.54 | Add 100A wayload to 1/0 ACSR |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {C4A20D6E-00E4-4BE3-BA7F-6131A5C57B8A}
5502 | 4176 | {68AC548A-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | ROSSMOOR | Bank 1 | CB 1104 | PGE\MFN3 | 2016-11-30 14:34:54.3180463 -08:00 | 0141601104 | 162881107 | 8 | 3 | 3 | 1 | 745 | 16.26 | 16.1 | 745 | 16.26 | 16.1 | 838 | 18.29 | 18.11 | 838 | 18.29 | 18.11 | 900 | 19.64 | 19.44 | 900 | 19.64 | 19.44 | 900 | 19.64 | 19.44 | 900 | 19.64 | 19.44 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {EF131C06-1BEE-4EAE-B3E6-DFD374005723}
5506 | 4178 | {464AB118-671D-11E5-80CA-005056A729E5} | STOCKTON | TRACY | Bank 1 | CB 1102 | PGE\ACT0 | 2016-11-17 08:54:44.1638357 -08:00 | 1628801102 | 162880402 | 8 | 3 | 3 | 1 | 573 | 12.51 | 12.38 | 573 | 12.51 | 12.38 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {88B18C6F-6633-479A-BAD3-D215FF5E8DD2}
5507 | 4178 | {0B435C2D-1184-11E6-95F2-D4BED91EFF1A} | STOCKTON | TRACY | Bank 1 | CB 1103 | PGE\BXYD | 2017-01-11 08:49:32.2191442 -08:00 | 1628801103 | 252901104 | 8 | 3 | 3 | 1 | 512 | 11.17 | 11.06 | 512 | 11.17 | 11.06 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {884F70B0-E45B-4819-9E91-8EDCEDC22251}
5508 | 4178 | {464AB121-671D-11E5-80CA-005056A729E5} | STOCKTON | TRACY | Bank 1 | CB 1104 | PGE\ACT0 | 2016-11-17 09:17:01.9990626 -08:00 | 1628801104 | 162881109 | 8 | 3 | 3 | 1 | 512 | 11.17 | 11.06 | 512 | 11.17 | 11.06 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {3B738CD7-7945-441A-85B5-AD771C8EE6F9}
5509 | 4179 | {464AB130-671D-11E5-80CA-005056A729E5} | STOCKTON | TRACY | Bank 2 | CB 1105 | PGE\BXYD | 2017-01-11 08:49:04.9189692 -08:00 | 1628801105 | 252901106 | 8 | 3 | 3 | 1 | 512 | 11.17 | 11.06 | 512 | 11.17 | 11.06 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {2F032310-F067-4845-A9EE-A74716AE80DF}
5510 | 4179 | {4C486DD6-671D-11E5-80CA-005056A729E5} | STOCKTON | TRACY | Bank 2 | CB 1106 | PGE\ACT0 | 2016-11-17 09:53:42.3025411 -08:00 | 1628801106 | 252901108 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {1917A24C-D58F-4C03-8BEA-2E761E433F93}
5511 | 4179 | {464AB12A-671D-11E5-80CA-005056A729E5} | STOCKTON | TRACY | Bank 2 | CB 1107 | PGE\BXYD | 2017-01-11 08:50:40.0951793 -08:00 | 1628801107 | 252901110 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {98F43D51-8516-40AA-BCAA-00E024A15709}
5512 | 4179 | {52F1DF2B-DCCA-11E5-83B3-2016D89D35F7} | STOCKTON | TRACY | Bank 2 | CB 402 | PGE\ACT0 | 2016-11-17 10:19:20.3928470 -08:00 | 162880402 | 162881110 | 8 | 3 | 3 | 1 | 210 | 4.58 | 4.53 | 100 | 2.18 | 2.16 | 210 | 4.58 | 4.53 | 115 | 2.51 | 2.48 | 210 | 4.58 | 4.53 | 144 | 3.14 | 3.11 | 210 | 4.58 | 4.53 | 153 | 3.34 | 3.31 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {3436B93E-3E9D-4A3B-B29B-65D109072168}
5513 | 4180 | {EEFC7449-671D-11E5-80CA-005056A729E5} | KERN | SEMITROPIC | Bank 3 | CB 1104 | PGE\BXYD | 2016-11-17 10:19:06.0239576 -08:00 | 2529001104 | 252901112 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1099 | 1429 | 1319 | 1649 | {49303800-66EE-41D2-8999-F887E4095194}
5514 | 4181 | {4C486DEE-671D-11E5-80CA-005056A729E5} | STOCKTON | TRACY | Bank 3 | CB 1109 (Non-SCADA) | PGE\ACT0 | 2016-11-17 10:41:21.0216557 -08:00 | 1628801109 | 162881111 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {5C3D5CF5-3DA2-4990-B697-0DD99809E407}
5515 | 4180 | {EEFC744F-671D-11E5-80CA-005056A729E5} | KERN | SEMITROPIC | Bank 3 | CB 1106 | PGE\BXYD | 2016-11-17 10:41:00.8340911 -08:00 | 2529001106 | 253181101 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1099 | 1429 | 1319 | 1649 | {031A3A4A-92C5-4EA1-86B5-0249079C2CD2}
5516 | 4180 | {EEFC7455-671D-11E5-80CA-005056A729E5} | KERN | SEMITROPIC | Bank 3 | CB 1108 | PGE\BXYD | 2016-11-17 10:42:55.7857649 -08:00 | 2529001108 | 253181102 | 8 | 3 | 3 | 1 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 520 | 11.35 | 11.24 | 520 | 11.35 | 11.24 | 599 | 13.07 | 12.94 | 599 | 13.07 | 12.94 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1099 | 1429 | 1319 | 1649 | {1A52525E-F233-48DB-B25E-71B92CCEFF29}
5517 | 4180 | {EEFC7458-671D-11E5-80CA-005056A729E5} | KERN | SEMITROPIC | Bank 3 | CB 1110 | PGE\BXYD | 2016-11-17 10:44:24.4315682 -08:00 | 2529001110 | 162881112 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1099 | 1429 | 1319 | 1649 | {84CD7BC0-6E97-49DD-B2D8-5D8C5016315B}
5518 | 4181 | {4C486DF7-671D-11E5-80CA-005056A729E5} | STOCKTON | TRACY | Bank 3 | CB 1110 (Non-SCADA) | PGE\BXYD | 2017-01-11 08:59:09.2824433 -08:00 | 1628801110 | 163692101 | 8 | 3 | 3 | 1 | 573 | 12.51 | 12.38 | 573 | 12.51 | 12.38 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {EBC1037E-0191-42FB-96FE-5A0134069421}
5519 | 4180 | {EEFC7467-671D-11E5-80CA-005056A729E5} | KERN | SEMITROPIC | Bank 3 | CB 1112 | PGE\BXYD | 2016-11-17 10:45:35.9448473 -08:00 | 2529001112 | 082191103 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 575 | 12.55 | 12.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1099 | 1429 | 1319 | 1649 | {F9F5D399-47A5-4259-B35E-EC62D546319D}
5520 | 4181 | {4C486DFA-671D-11E5-80CA-005056A729E5} | STOCKTON | TRACY | Bank 3 | CB 1111 (Non-SCADA) | PGE\ACT0 | 2016-11-17 10:51:39.6310535 -08:00 | 1628801111 | 082191104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {A912AFB2-BBDE-4A7E-8651-2872EBF399E1}
5521 | 4182 | {E8FE8E12-671D-11E5-80CA-005056A729E5} | KERN | MC FARLAND | Bank 1 | CB 1101 | PGE\BXYD | 2016-11-17 11:12:43.2229530 -08:00 | 2531801101 | 082191105 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {CA86E153-5EE2-41BB-A0F4-77FFCE745856}
5522 | 4182 | {E8FE8E1D-671D-11E5-80CA-005056A729E5} | KERN | MC FARLAND | Bank 1 | CB 1102 | PGE\BXYD | 2016-11-17 11:14:08.7285357 -08:00 | 2531801102 | 153612103 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 447 | 9.76 | 9.66 | 447 | 9.76 | 9.66 | 514 | 11.22 | 11.11 | 514 | 11.22 | 11.11 | 549 | 11.98 | 11.86 | 549 | 11.98 | 11.86 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {5CA32B29-ECD0-4782-A828-1D512E7B38EA}
5523 | 4183 | {4C486E03-671D-11E5-80CA-005056A729E5} | STOCKTON | TRACY | Bank 4 | CB 1112 (Non-SCADA) | PGE\BXYD | 2017-01-11 09:01:56.7807170 -08:00 | 162881112 | 153612104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 800 | 17.46 | 17.29 | 760 | 16.59 | 16.42 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 800 | 17.46 | 17.29 | 760 | 16.59 | 16.42 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {2D084938-FDA2-482C-8976-C0392D499E10}
5524 | 4165 | {464AAF85-671D-11E5-80CA-005056A729E5} | STOCKTON | SALT SPRINGS | Bank 1 (Non SCADA) | CB 2101 (Non-SCADA) | PGE\ACT0 | 2016-11-18 09:28:42.6405755 -08:00 | 163692101 | 153612105 | 8 | 4 | 4 | 2 | 902 | 18.75 | 18.56 | 902 | 18.75 | 18.56 | 1172 | 24.36 | 24.12 | 1172 | 24.36 | 24.12 | 1082 | 22.49 | 22.27 | 1082 | 22.49 | 22.27 | 1353 | 28.12 | 27.84 | 1353 | 28.12 | 27.84 |  |  | FALSE | FALSE | 902 | 1172 | 1082 | 1353 | {00000000-0000-0000-0000-000000000000}
5525 | 4189 | {E224A233-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MABURY | Bank 2 | CB 1103 | PGE\RPBK | 2016-11-22 08:37:00.4390676 -08:00 | 0821901103 | 153612106 | 8 | 3 | 3 | 2 | 468 | 10.21 | 10.11 | 468 | 10.21 | 10.11 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 528 | 11.52 | 11.4 | 528 | 11.52 | 11.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Phase 720A; L = 4; T = 6; Inst. = 4800 Ground 180A; L = 10; T = 1.5; Inst. = NONE |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {5F8054F5-2396-4BA4-A60E-161BD9AE4D12}
5526 | 4189 | {E224A24A-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MABURY | Bank 2 | CB 1104 | PGE\RPBK | 2016-11-21 08:52:13.9007742 -08:00 | 0821901104 | 153612109 | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 582 | 12.7 | 12.57 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Phase 720A; L = 4.0; T = 6; Inst =4800 Ground 180A; L = 5.0; T = 1.5; Inst = NONE |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {45E2CC18-887A-4DAF-8F94-6B75E3A425A1}
5527 | 4189 | {3721AC5D-FDD1-11E5-9D37-D4BED91EFF1A} | SAN JOSE | MABURY | Bank 2 | CB 1105 | PGE\RPBK | 2016-11-22 08:48:12.0148336 -08:00 | 0821901105 | 153612110 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Phase 720A (Very Inverse); TD=0.6; Inst=4800, 3cycle delay Ground 180A (Very Inverse);TD=1.0; Inst=4800 |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9E4112ED-A83E-4F99-9BA4-B80E4738E51D}
5530 | 4190 | {946B52ED-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | CLARKSVILLE | Bank 1 | CB 2103 | PGE\JSKe | 2016-11-21 14:03:35.6337949 -08:00 | 1536102103 | 082191101 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 675 | 25.51 | 25.25 | 675 | 25.51 | 25.25 | 675 | 25.51 | 25.25 | 675 | 25.51 | 25.25 | 675 | 25.51 | 25.25 | 675 | 25.51 | 25.25 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {BEA537AA-3703-4BE0-9F6A-1D90F6401967}
5532 | 4190 | {946B5304-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | CLARKSVILLE | Bank 1 | CB 2104 | PGE\JSKe | 2016-11-21 14:03:07.8649162 -08:00 | 1536102104 | 082191102 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 732 | 27.66 | 27.38 | 732 | 27.66 | 27.38 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {9680A750-45E9-4CCE-8B9B-F7E1BE473F15}
5533 | 4191 | {946B5325-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | CLARKSVILLE | Bank 2 | CB 2105 | PGE\JSKe | 2016-11-21 14:00:03.6087504 -08:00 | 1536102105 | 014471105 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 675 | 25.51 | 25.25 | 675 | 25.51 | 25.25 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 675 | 25.51 | 25.25 | 675 | 25.51 | 25.25 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {799B3CF6-C8B8-48B0-8FF0-63001C97D126}
5534 | 4191 | {946B534A-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | CLARKSVILLE | Bank 2 | CB 2106 | PGE\JSKe | 2016-11-21 14:02:18.9409238 -08:00 | 1536102106 | 014471106 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 | 717 | 27.1 | 26.83 | 717 | 27.1 | 26.83 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {13AAE277-D4D5-45A8-B6B1-6B80F8641E3F}
5535 | 4192 | {946B5364-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | CLARKSVILLE | Bank 3 | CB 2109 | PGE\JSKe | 2016-11-21 14:12:03.2778099 -08:00 | 1536102109 | 014471107 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 792 | 29.93 | 29.63 | 792 | 29.93 | 29.63 | 717 | 27.1 | 26.83 | 717 | 27.1 | 26.83 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {43E6E82C-BA3D-4C64-A151-B5B0BC0003CE}
5536 | 4192 | {946B5382-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | CLARKSVILLE | Bank 3 | CB 2110 | PGE\JSKe | 2016-11-21 14:13:59.1113291 -08:00 | 1536102110 | 014471108 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 792 | 29.93 | 29.63 | 792 | 29.93 | 29.63 | 717 | 27.1 | 26.83 | 717 | 27.1 | 26.83 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {850AE905-95F9-485C-B5AA-AB7BBA3AB08A}
5541 | 4195 | {6AF46B1B-5440-11E6-8DC6-D4BED91EFF1A} | SAN JOSE | MABURY | Bank 1 | CB 1101 (Non-SCADA) | PGE\RPBK | 2017-05-04 09:55:36.9961522 -07:00 | 082191101 | 014662103 | 8 | 3 | 3 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {612DF543-D0B4-4B13-9FDD-6BD4DF544D8F}
5545 | 4195 | {27E7ADFF-FDD1-11E5-9D37-D4BED91EFF1A} | SAN JOSE | MABURY | Bank 1 | CB 1102 (Non-SCADA) | PGE\RPBK | 2016-11-22 12:42:20.4539433 -08:00 | 0821901102 | 014662104 | 8 | 3 | 3 | 2 | 524 | 11.44 | 11.33 | 524 | 11.44 | 11.33 | 591 | 12.9 | 12.77 | 591 | 12.9 | 12.77 | 599 | 13.07 | 12.94 | 599 | 13.07 | 12.94 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Phase 720A; L = 4; T = 6; Inst. = 4800 Ground 180A; L = 10; T = 1.5; Inst. = NONE |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {ABC9A89C-3341-420A-ACD3-8900C24C243A}
5547 | 4199 | {BD86DA10-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DUMBARTON | Bank 2 | CB 1105 | PGE\RDR1 | 2017-06-13 12:09:35.5314817 -07:00 | 0144701105 | 014662105 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2000 | {18FC7DDB-9E34-43ED-91E5-0EFAC2709039}
5550 | 4199 | {BD86DA19-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DUMBARTON | Bank 2 | CB 1106 | PGE\RDR1 | 2017-06-13 12:23:16.1332021 -07:00 | 0144701106 | 014662106 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2000 | {FDF7548D-0ADC-48B4-AF2A-B3A0881C6B0C}
5551 | 4199 | {BD86DA22-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DUMBARTON | Bank 2 | CB 1107 | PGE\RDR1 | 2017-06-13 12:35:47.6728371 -07:00 | 0144701107 | 182981103 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2000 | {B22A0825-4B5A-42B1-B69C-00B9D0E0551A}
5552 | 4199 | {BD86DA33-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DUMBARTON | Bank 2 | CB 1108 | PGE\RDR1 | 2017-06-13 13:27:40.5055447 -07:00 | 0144701108 | 014662107 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2000 | {D07DD5F9-6AFF-4049-8DD2-7C6343EF4743}
5553 | 4200 | {81611FF0-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | TASSAJARA | Bank 1 | CB 2103 | PGE\MFN3 | 2016-11-30 14:26:09.9816126 -08:00 | 0146602103 | 014662108 | 12 | 3 | 3 | 1 | 573 | 21.66 | 21.44 | 573 | 21.66 | 21.44 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | This is an express circuit that feeds load in the adjacent Mission Division, thus it is equipped with a feeder voltage regulator 3- 1 phase, 833/933 kVA set with a Cooper CL5 controller to SN 606, SE 751, WN 722, WE 751. Distribution Operator should place Tassajara 2103 Regulator on manual control and in neutral position when paralleling circuits. Additional limitation 1000Al PVC Riser (14625) + Wayload (108amps) : SN 638, SE 856, WN 774, WE 953 |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {3A71D4BF-F06F-4557-973B-335C7A96386E}
5559 | 4200 | {8161201C-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | TASSAJARA | Bank 1 | CB 2104 | PGE\MFN3 | 2016-11-30 14:28:30.1971431 -08:00 | 0146602104 | 014662109 | 12 | 3 | 3 | 1 | 584 | 22.07 | 21.85 | 584 | 22.07 | 21.85 | 742 | 28.04 | 27.76 | 742 | 28.04 | 27.76 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {6FE1BBB7-0415-4846-8CFD-FC66279DBF23}
5565 | 4200 | {875E9A21-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | TASSAJARA | Bank 1 | CB 2105 | PGE\MFN3 | 2016-11-30 14:28:52.9614824 -08:00 | 0146602105 | 014662110 | 12 | 3 | 3 | 1 | 584 | 22.07 | 21.85 | 584 | 22.07 | 21.85 | 742 | 28.04 | 27.76 | 742 | 28.04 | 27.76 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {168372DC-5EC7-4991-A0E3-228FE09DE039}
5568 | 4200 | {875E9A26-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | TASSAJARA | Bank 1 | CB 2106 | PGE\MFN3 | 2016-11-30 14:29:07.7684447 -08:00 | 0146602106 | 182222101 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 732 | 27.66 | 27.38 | 732 | 27.66 | 27.38 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {5CB48277-21DC-4E9C-B92D-71CF1A2104B5}
5572 | 4185 | {904AFA04-081F-11E6-9D37-D4BED91EFF1A} | CENTRAL COAST | JOLON | Bank 2 | CB 1103 | PGE\MTTA | 2016-12-29 12:37:49.0414568 -08:00 | 1829801103 | 153651103 | 8 | 3 | 3 | 1 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {4864B2F8-EC3A-4C50-9C46-3339C6BC8CC2}
5578 | 4202 | {875E9A3D-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | TASSAJARA | Bank 2 | CB 2107 | PGE\MFN3 | 2016-11-30 14:29:34.3999942 -08:00 | 0146602107 | 153651104 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 732 | 27.66 | 27.38 | 732 | 27.66 | 27.38 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {25E7D760-B279-4E05-9F4C-23ACBDA729A9}
5582 | 4202 | {875E9A5D-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | TASSAJARA | Bank 2 | CB 2108 | PGE\MFN3 | 2016-11-30 14:29:42.4810532 -08:00 | 0146602108 | 153652105 | 12 | 3 | 3 | 1 | 661 | 24.98 | 24.73 | 661 | 24.98 | 24.73 | 792 | 29.93 | 29.63 | 792 | 29.93 | 29.63 | 717 | 27.1 | 26.83 | 717 | 27.1 | 26.83 | 833 | 31.48 | 31.17 | 833 | 31.48 | 31.17 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {5722BFA2-E3A8-4583-9FDF-8E5D58D6EA1A}
5588 | 4202 | {8D7DA60D-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | TASSAJARA | Bank 2 | CB 2109 | PGE\MFN3 | 2016-11-30 14:29:54.6962447 -08:00 | 0146602109 | 014662112 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 732 | 27.66 | 27.38 | 732 | 27.66 | 27.38 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {DC9931F4-FC66-477C-80A9-0725A340B717}
5593 | 4202 | {8D7DA61B-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | TASSAJARA | Bank 2 | CB 2110 | PGE\MFN3 | 2016-11-30 14:30:11.7319907 -08:00 | 0146602110 | 014662113 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 732 | 27.66 | 27.38 | 732 | 27.66 | 27.38 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {79CB833A-9994-4FB9-821C-AA8ED6E7997C}
5600 | 1106 | {FAFA58DF-8730-11E6-841B-D4BED91EFF1A} | CENTRAL COAST | DEL MONTE | Bank 1 | CB 2101 | PGE\MTDR | 2017-07-14 11:00:56.9448125 -07:00 | 182222101 | 014662114 | 12 | 4 | 4 | 2 | 375 | 14.17 | 14.03 | 375 | 14.17 | 14.03 | 375 | 14.17 | 14.03 | 375 | 14.17 | 14.03 | 375 | 14.17 | 14.03 | 375 | 14.17 | 14.03 | 375 | 14.17 | 14.03 | 375 | 14.17 | 14.03 |  |  | FALSE | FALSE | 1190 | 1331 | 1331 | 1331 | {286D84D9-250E-4476-BFCA-91738CE3CC82}
5601 | 4212 | {AD80C04D-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | SHINGLE SPRINGS | Bank 1 | CB 1103 | PGE\JSKe | 2016-11-23 11:39:45.1575329 -08:00 | 1536501103 | 153652108 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {625EC3B2-27D0-4F85-B3A9-FF96CBDFEF3C}
5602 | 4212 | {AD80C05D-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | SHINGLE SPRINGS | Bank 1 | CB 1104 | PGE\JSKe | 2016-11-23 11:54:30.2375205 -08:00 | 1536501104 | 153652109 | 8 | 4 | 4 | 2 | 534 | 11.65 | 11.53 | 534 | 11.65 | 11.53 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {69894496-8A97-40D4-8172-D1BEC3C7A54F}
5604 | 4213 | {AD80C070-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | SHINGLE SPRINGS | Bank 2 | CB 2105 | PGE\JSKe | 2016-11-23 12:14:17.2282379 -08:00 | 1536502105 | 153652110 | 12 | 4 | 4 | 2 | 423 | 15.99 | 15.83 | 423 | 15.99 | 15.83 | 550 | 20.79 | 20.58 | 550 | 20.79 | 20.58 | 508 | 19.2 | 19.01 | 508 | 19.2 | 19.01 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 423 | 550 | 508 | 635 | {BAFE04EA-DDE8-4EC3-A52D-24BD5E43444F}
5605 | 4214 | {8D7DA623-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | TASSAJARA | Bank 3 | CB 2112 | PGE\MFN3 | 2016-11-30 14:31:15.4302946 -08:00 | 0146602112 | 082952108 | 12 | 3 | 3 | 1 | 584 | 22.07 | 21.85 | 584 | 22.07 | 21.85 | 742 | 28.04 | 27.76 | 742 | 28.04 | 27.76 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {4D4445EE-4EFF-473E-9A77-9C62EF178966}
5609 | 4214 | {938A626D-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | TASSAJARA | Bank 3 | CB 2113 | PGE\MFN3 | 2016-11-30 14:31:28.8937367 -08:00 | 0146602113 | 013801101 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 732 | 27.66 | 27.38 | 732 | 27.66 | 27.38 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {CB9FA05E-25FC-46AE-AB46-FB836BF9777D}
5613 | 4214 | {938A62A5-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | TASSAJARA | Bank 3 | CB 2114 | PGE\MFN3 | 2016-11-30 14:31:41.9203212 -08:00 | 0146602114 | 082952109 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 732 | 27.66 | 27.38 | 732 | 27.66 | 27.38 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {B766D19A-7DEE-40C0-9BA0-1757EB075F8D}
5619 | 4215 | {AD80C091-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | SHINGLE SPRINGS | Bank 3 | CB 2108 | PGE\JSKe | 2016-11-23 13:09:04.8908721 -08:00 | 1536502108 | 082952110 | 12 | 3 | 3 | 1 | 530 | 20.03 | 19.83 | 530 | 20.03 | 19.83 | 728 | 27.51 | 27.23 | 728 | 27.51 | 27.23 | 634 | 23.96 | 23.72 | 634 | 23.96 | 23.72 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {F822EC43-25FA-40F8-B91E-5DF67BDFF60A}
5620 | 4215 | {AD80C0B0-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | SHINGLE SPRINGS | Bank 3 | CB 2109 | PGE\JSKe | 2016-11-23 13:11:29.7660892 -08:00 | 1536502109 | 013801102 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 | 717 | 27.1 | 26.83 | 717 | 27.1 | 26.83 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {ACF54AFE-BF40-4F7E-8AED-27ADA167E022}
5621 | 4215 | {AD80C0F8-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | SHINGLE SPRINGS | Bank 3 | CB 2110 | PGE\JSKe | 2016-11-23 13:13:59.4388950 -08:00 | 1536502110 | 013801103 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 792 | 29.93 | 29.63 | 792 | 29.93 | 29.63 | 717 | 27.1 | 26.83 | 717 | 27.1 | 26.83 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {371BA6A2-B444-4C80-9A58-844DADE15E5E}
5623 | 4211 | {D5F176D4-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | EDENVALE | Bank 3 | CB 2108 | PGE\DVN5 | 2016-11-28 11:09:34.9887871 -08:00 | 0829502108 | 013801104 | 12 | 3 | 3 | 2 | 541 | 20.45 | 20.25 | 541 | 20.45 | 20.25 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {2980CAB5-F435-4FC2-BA8B-A813B616CB12}
5624 | 4216 | {96A9BA84-FDB8-11E5-9D37-D4BED91EFF1A} | DIABLO | MORAGA | Bank 5 | CB 1101 | PGE\MFN3 | 2016-11-30 14:46:24.7864048 -08:00 | 0138001101 | 013801105 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 477 | 10.41 | 10.31 | 639 | 13.95 | 13.81 | 607 | 13.25 | 13.12 | 557 | 12.16 | 12.04 | 529 | 11.54 | 11.42 | 667 | 14.56 | 14.41 | 633 | 13.81 | 13.67 |  |  | TRUE | FALSE | 2061 | 2680 | 2474 | 3092 | {2A1276C3-DAB7-4990-B57E-91E81505CF03}
5625 | 4211 | {D5F17723-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | EDENVALE | Bank 3 | CB 2109 | PGE\DVN5 | 2016-11-28 11:11:25.0197665 -08:00 | 0829502109 | 082952111 | 12 | 3 | 3 | 2 | 541 | 20.45 | 20.25 | 541 | 20.45 | 20.25 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {7AA740CC-AFB9-44CD-8A7A-107345936C83}
5626 | 4211 | {D5F1775D-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | EDENVALE | Bank 3 | CB 2110 | PGE\DVN5 | 2016-11-28 11:17:04.8782864 -08:00 | 0829502110 | 082952112 | 12 | 3 | 3 | 2 | 541 | 20.45 | 20.25 | 541 | 20.45 | 20.25 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {B422F36C-4CA2-47EC-863E-BC4A57658855}
5627 | 4216 | {48D4CA58-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | MORAGA | Bank 5 | CB 1102 | PGE\MFN3 | 2016-11-30 14:46:15.9251706 -08:00 | 0138001102 | 082952113 | 8 | 3 | 3 | 1 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 539 | 11.76 | 11.64 | 539 | 11.76 | 11.64 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 666 | 14.53 | 14.38 | 666 | 14.53 | 14.38 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F0A1A733-7347-4285-8B28-6956EA120261}
5629 | 4216 | {48D4CA69-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | MORAGA | Bank 5 | CB 1103 | PGE\MFN3 | 2016-11-30 14:46:03.6327646 -08:00 | 0138001103 | 014592106 | 8 | 3 | 3 | 1 | 422 | 9.21 | 9.12 | 422 | 9.21 | 9.12 | 536 | 11.7 | 11.58 | 536 | 11.7 | 11.58 | 468 | 10.21 | 10.11 | 468 | 10.21 | 10.11 | 566 | 12.35 | 12.23 | 566 | 12.35 | 12.23 | Due to 249A way load my planning capabilities are SN 671, SE 785, WN 717, WE 800 |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {7A3A20A5-6B25-4450-ADF1-8B5A79DD5EFB}
5631 | 4216 | {4ED551D1-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | MORAGA | Bank 5 | CB 1104 | PGE\MFN3 | 2016-11-30 14:45:51.7927441 -08:00 | 0138001104 | 012091101 | 8 | 3 | 3 | 1 | 440 | 9.6 | 9.5 | 440 | 9.6 | 9.5 | 566 | 12.35 | 12.23 | 566 | 12.35 | 12.23 | 525 | 11.46 | 11.35 | 525 | 11.46 | 11.35 | 583 | 12.72 | 12.59 | 583 | 12.72 | 12.59 | Limiting factor is no available on this sheet: 750Cu 3/C PL&N in metal riser SN 476, SE 543, WN 570 WE 570. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {8A0A0DA2-9470-4442-9513-8C88E66981DE}
5633 | 4216 | {4ED551EB-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | MORAGA | Bank 5 | CB 1105 | PGE\MFN3 | 2016-11-30 14:45:43.9461956 -08:00 | 0138001105 | 012091103 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 689 | 15.04 | 14.89 | 689 | 15.04 | 14.89 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 732 | 15.98 | 15.82 | 732 | 15.98 | 15.82 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {E0F5F9C0-F0D7-43B1-AC4B-B6F1795783EB}
5636 | 4217 | {DC00D08C-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | EDENVALE | Bank 4 | CB 2111 | PGE\DVN5 | 2016-11-28 11:28:30.3696323 -08:00 | 0829502111 | 012091104 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {8CC39D38-2B0D-4C28-B844-F2F8EF4E7BE7}
5640 | 4217 | {DC00D0AA-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | EDENVALE | Bank 4 | CB 2112 | PGE\DVN5 | 2016-11-28 11:37:03.1751907 -08:00 | 0829502112 | 012091105 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {9DABF673-8A7C-4064-8012-6AEC3979B119}
5642 | 4217 | {DC00D0C1-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | EDENVALE | Bank 4 | CB 2113 | PGE\DVN5 | 2016-11-28 11:48:33.1751862 -08:00 | 0829502113 | 012091109 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {CFE0318C-3C64-4CE4-817B-7FABDFE9C11B}
5828 | 4293 | {9CA8A6BA-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | BRENTWOOD | Bank 1 | CB 2106 | PGE\WCL5 | 2016-12-14 17:17:16.9529169 -08:00 | 0145902106 | 152701109 | 22 | 3 | 3 | 1 | 578 | 20.8 | 20.59 | 578 | 20.8 | 20.59 | 689 | 24.8 | 24.55 | 689 | 24.8 | 24.55 | 627 | 22.57 | 22.34 | 627 | 22.57 | 22.34 | 732 | 26.35 | 26.09 | 732 | 26.35 | 26.09 |  |  | FALSE | FALSE | 1667 | 2167 | 2000 | 2500 | {9E6D62A3-9709-4D25-837E-FD352B5561FF}
5830 | 4282 | {4D5B04D1-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 1 | CB 1101 | PGE\C7CF | 2017-05-30 15:17:28.0605388 -07:00 | 0120901101 | 152701110 | 7 | 3 | 3 | 2 | 397 | 8.57 | 8.48 | 397 | 8.57 | 8.48 | 474 | 10.24 | 10.14 | 474 | 10.24 | 10.14 | 440 | 9.5 | 9.41 | 440 | 9.5 | 9.41 | 488 | 10.54 | 10.43 | 488 | 10.54 | 10.43 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {BBE02DF8-6EB1-4D0E-9319-B7D7CD9AE764}
5831 | 4282 | {4D5B04DF-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 1 | CB 1103 | PGE\C7CF | 2017-05-30 15:31:45.0584058 -07:00 | 0120901103 | 152531101 | 7 | 3 | 3 | 2 | 435 | 9.4 | 9.31 | 413 | 8.92 | 8.83 | 496 | 10.71 | 10.6 | 471 | 10.17 | 10.07 | 525 | 11.34 | 11.23 | 525 | 11.34 | 11.23 | 583 | 12.59 | 12.46 | 579 | 12.51 | 12.38 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {35EAE5E9-1425-4425-AB8F-1FF6690608F1}
5832 | 4282 | {4D5B04E4-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 1 | CB 1104 | PGE\C7CF | 2017-05-30 15:19:54.1280203 -07:00 | 0120901104 | 152531102 | 7 | 3 | 3 | 2 | 397 | 8.57 | 8.48 | 397 | 8.57 | 8.48 | 487 | 10.52 | 10.41 | 487 | 10.52 | 10.41 | 469 | 10.13 | 10.03 | 469 | 10.13 | 10.03 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {BE5FEE13-DEC4-470B-B34C-F87243967D1D}
5833 | 4282 | {4D5B04E9-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 1 | CB 1105 | PGE\C7CF | 2016-12-15 11:44:50.7134885 -08:00 | 0120901105 | 012091112 | 8 | 3 | 3 | 2 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 574 | 12.53 | 12.4 | 574 | 12.53 | 12.4 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {299942ED-16E8-4C08-8DB6-A25B282D7ECF}
5834 | 4282 | {59AF3446-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 1 | CB 1109 | PGE\C7CF | 2016-12-15 11:49:58.8214246 -08:00 | 0120901109 | 012091102 | 8 | 3 | 3 | 2 | 426 | 9.3 | 9.21 | 426 | 9.3 | 9.21 | 479 | 10.45 | 10.35 | 479 | 10.45 | 10.35 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 1) This feeder is energized with no load. It is a back up for the Ownes Glass company that has transmission service. |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {705FD0F8-0F7A-4019-A0EA-8A3767174930}
5835 | 4301 | {8E5DEF68-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | BELL | Bank 3 | CB 1109 | PGE\MTN6 | 2016-12-15 12:11:32.9506570 -08:00 | 1527001109 | 012091116 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1223 | 1590 | 1468 | 1835 | {C0EC306A-489E-4C2A-900C-5D74AD96F0AD}
5836 | 4301 | {8E5DEF71-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | BELL | Bank 3 | CB 1110 | PGE\MTN6 | 2016-12-15 12:18:21.5409910 -08:00 | 1527001110 | 012091117 | 8 | 4 | 4 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1223 | 1590 | 1468 | 1835 | {4E809B28-5E95-4D9B-9905-242470518029}
5837 | 4302 | {9AA85C63-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | FLINT | Bank 1 | CB 1101 | PGE\MTN6 | 2016-12-15 12:36:02.0419332 -08:00 | 1525301101 | 012090403 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1289 | 1676 | 1547 | 1934 | {4840A666-C643-4B1E-A2C1-6B57F45D00C5}
5838 | 4302 | {9AA85C7A-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | FLINT | Bank 1 | CB 1102 | PGE\MTN6 | 2016-12-15 12:41:20.4817931 -08:00 | 1525301102 | 012090409 | 8 | 4 | 4 | 2 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1289 | 1676 | 1547 | 1934 | {9B8D28C1-3FAC-4C4B-8899-7179261EE2D6}
5840 | 4282 | {59AF344B-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 1 | CB 1112 | PGE\MUSF | 2017-06-09 15:00:28.6732308 -07:00 | 0120901112 | 012101101 | 7 | 3 | 3 | 2 | 560 | 12.1 | 11.98 | 560 | 12.1 | 11.98 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 577 | 12.46 | 12.34 | 577 | 12.46 | 12.34 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {0A2133C6-CD64-47FB-89AB-DD4B6B820E1D}
5841 | 2547 | {59AF345E-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 2 | CB 1102 | PGE\MUSF | 2017-06-09 14:46:47.8841243 -07:00 | 0120901102 | 012101103 | 7 | 3 | 3 | 2 | 467 | 10.09 | 9.99 | 467 | 10.09 | 9.99 | 523 | 11.3 | 11.19 | 523 | 11.3 | 11.19 | 481 | 10.39 | 10.29 | 481 | 10.39 | 10.29 | 539 | 11.64 | 11.52 | 539 | 11.64 | 11.52 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {47263202-995C-423B-A771-70983F682104}
5842 | 2547 | {6000965B-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 2 | CB 1116 | PGE\MUSF | 2017-06-09 14:54:10.7979198 -07:00 | 0120901116 | 012110406 | 7 | 3 | 3 | 2 | 475 | 10.26 | 10.16 | 475 | 10.26 | 10.16 | 584 | 12.61 | 12.48 | 570 | 12.31 | 12.19 | 489 | 10.56 | 10.45 | 489 | 10.56 | 10.45 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {F73C99DE-7BB9-4A3F-9BDC-E7E5CED4BA51}
5843 | 2547 | {60009660-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 2 | CB 1117 | PGE\MUSF | 2017-06-09 14:55:07.0533228 -07:00 | 0120901117 | 012110407 | 7 | 3 | 3 | 2 | 450 | 9.72 | 9.62 | 450 | 9.72 | 9.62 | 504 | 10.89 | 10.78 | 504 | 10.89 | 10.78 | 464 | 10.02 | 9.92 | 464 | 10.02 | 9.92 | 519 | 11.21 | 11.1 | 519 | 11.21 | 11.1 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {F188FD5A-03A0-45E7-9384-FCC4D5AFE37C}
5844 | 2547 | {B7D12457-8A62-11E6-841B-D4BED91EFF1A} | EAST BAY | OAKLAND J | Bank 2 | CB IJ 2 | PGE\C7CF | 2016-12-15 13:09:07.9110078 -08:00 |  | 012110405 | 8 | 3 | 3 | 2 | 505 | 11.02 | 10.91 | 505 | 11.02 | 10.91 | 586 | 12.79 | 12.66 | 586 | 12.79 | 12.66 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {468DB00A-AE44-44D6-8EF0-9275474C406F}
5845 | 2547 | {CDB86947-8A62-11E6-841B-D4BED91EFF1A} | EAST BAY | OAKLAND J | Bank 2 | CB IJ 3 | PGE\C7CF | 2016-12-15 13:10:31.7152762 -08:00 |  | 014321101 | 8 | 3 | 3 | 2 | 505 | 11.02 | 10.91 | 505 | 11.02 | 10.91 | 586 | 12.79 | 12.66 | 586 | 12.79 | 12.66 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {0D4F1E31-DC33-4BA6-90E2-CFC516F5A76F}
5846 | 4281 | {665B4727-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 3 | CB 403 | PGE\C7CF | 2016-12-15 13:16:37.8070706 -08:00 | 012090403 | 013232101 | 4 | 3 | 3 | 2 | 356 | 2.69 | 2.66 | 356 | 2.69 | 2.66 | 392 | 2.97 | 2.94 | 392 | 2.97 | 2.94 | 367 | 2.78 | 2.75 | 367 | 2.78 | 2.75 | 403 | 3.05 | 3.02 | 403 | 3.05 | 3.02 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {7F5F7E8C-F628-47CF-9E12-DB771F054FB9}
5847 | 4281 | {665B472A-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 3 | CB 409 | PGE\C7CF | 2016-12-15 13:28:53.0934782 -08:00 | 012090409 | 013232102 | 4 | 3 | 3 | 2 | 321 | 2.43 | 2.41 | 321 | 2.43 | 2.41 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 358 | 2.71 | 2.68 | 358 | 2.71 | 2.68 | 382 | 2.89 | 2.86 | 382 | 2.89 | 2.86 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {B229F6D5-D83D-4322-A695-32537051F125}
5848 | 4193 | {189B1B7B-BD9F-11E6-93A9-D4BED91EFF1A} | SIERRA | ALLEGHANY | MOBILE TRANSFORMER BANK NO 1 | CB 1101 (Non-SCADA) | PGE\RVS7 | 2016-12-16 14:24:05.9213471 -08:00 |  | 014692101 | 8 | 3 | 3 | 1 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 343 | 446 | 412 | 515 | {EF843E3F-AB18-4E08-BD8F-49A4CB0039D1}
5849 | 4193 | {226EEC41-BD9F-11E6-93A9-D4BED91EFF1A} | SIERRA | ALLEGHANY | MOBILE TRANSFORMER BANK NO 1 | CB 1102 (Non-SCADA) | PGE\RVS7 | 2016-12-16 14:25:22.9696016 -08:00 |  | 014692102 | 8 | 3 | 3 | 1 | 183 | 3.99 | 3.95 | 183 | 3.99 | 3.95 | 210 | 4.58 | 4.53 | 210 | 4.58 | 4.53 | 210 | 4.58 | 4.53 | 210 | 4.58 | 4.53 | 210 | 4.58 | 4.53 | 210 | 4.58 | 4.53 |  |  | FALSE | FALSE | 343 | 446 | 412 | 515 | {CB2321BF-3491-4305-BB3D-0240EA69E310}
5850 | 2682 | {F6AEA6DD-47A5-11E6-AFF0-80000BC6CD8D} | SACRAMENTO | DOBBINS | BANK 1 (Non SCADA) | CB 1101 | PGE\WRA4 | 2017-03-23 17:09:35.4686131 -07:00 |  | 014692103 | 8 | 3 | 3 | 1 | 250 | 5.46 | 5.41 | 137 | 2.99 | 2.96 | 250 | 5.46 | 5.41 | 178 | 3.88 | 3.84 | 250 | 5.46 | 5.41 | 164 | 3.58 | 3.54 | 250 | 5.46 | 5.41 | 206 | 4.5 | 4.46 |  |  | FALSE | TRUE | 137 | 178 | 164 | 206 | {507429A3-4032-4600-99BD-CA7952923AF1}
5851 | 4280 | {6C8E2516-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND K | Bank 2 | CB 1101 | PGE\MUSF | 2017-05-18 10:02:09.6764743 -07:00 | 0121001101 | 014471109 | 7 | 3 | 3 | 2 | 347 | 7.49 | 7.42 | 347 | 7.49 | 7.42 | 396 | 8.55 | 8.46 | 396 | 8.55 | 8.46 | 417 | 9.01 | 8.92 | 417 | 9.01 | 8.92 | 463 | 10 | 9.9 | 463 | 10 | 9.9 |  |  | FALSE | FALSE | 1736 | 2257 | 2083 | 2604 | {469FB090-0EBE-4FD1-BA5A-C0D93C6ED107}
5852 | 4280 | {72FF91EF-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND K | Bank 2 | CB 1103 | PGE\C7CF | 2017-05-31 16:37:41.1723523 -07:00 | 0121001103 | 014471110 | 7 | 3 | 3 | 2 | 344 | 7.43 | 7.36 | 344 | 7.43 | 7.36 | 447 | 9.65 | 9.55 | 447 | 9.65 | 9.55 | 412 | 8.9 | 8.81 | 412 | 8.9 | 8.81 | 490 | 10.58 | 10.47 | 490 | 10.58 | 10.47 |  |  | FALSE | FALSE | 1736 | 2257 | 2083 | 2604 | {5F13743A-BC81-43EB-8E8A-BA9365F181EA}
5853 | 4278 | {7F4D3229-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND L | Bank 7 (Non SCADA) | CB 406 (Non-SCADA) | PGE\C7CF | 2017-06-05 16:28:35.5233837 -07:00 | 012110406 | 014471111 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 285 | 2.16 | 2.14 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 |  |  | FALSE | FALSE | 1866 | 2425 | 2239 | 2799 | {3FEDE88B-CD4E-4664-AEB7-2A2898E13FBD}
5854 | 4278 | {7F4D322C-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND L | Bank 7 (Non SCADA) | CB 407 (Non-SCADA) | PGE\C7CF | 2017-06-05 16:31:00.9484481 -07:00 | 012110407 | 014471112 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 285 | 2.16 | 2.14 | 300 | 2.27 | 2.25 | 285 | 2.16 | 2.14 | 300 | 2.27 | 2.25 | 285 | 2.16 | 2.14 | 300 | 2.27 | 2.25 | 285 | 2.16 | 2.14 |  |  | FALSE | FALSE | 1866 | 2425 | 2239 | 2799 | {50665FF5-83CE-4412-853C-EB3AFB992525}
5855 | 4278 | {CFCB6E7D-6E52-11E6-BBF8-D4BED91EFF1A} | EAST BAY | OAKLAND L | Bank 7 (Non SCADA) | CB 408 (Non-SCADA) | PGE\C7CF | 2016-12-19 09:47:25.1583976 -08:00 |  | 152111101 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 |  |  | FALSE | FALSE | 1866 | 2425 | 2239 | 2799 | {00000000-0000-0000-0000-000000000000}
5856 | 4278 | {C3347B82-6E52-11E6-BBF8-D4BED91EFF1A} | EAST BAY | OAKLAND L | Bank 8 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2017-06-05 16:25:38.1803101 -07:00 |  | 152111102 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 285 | 2.16 | 2.14 | 300 | 2.27 | 2.25 | 285 | 2.16 | 2.14 | 300 | 2.27 | 2.25 | 285 | 2.16 | 2.14 | 300 | 2.27 | 2.25 | 285 | 2.16 | 2.14 |  |  | FALSE | FALSE | 1866 | 2425 | 2239 | 2799 | {C492A9BB-E581-4EA8-BF1A-7A3A2289947A}
5857 | 4279 | {7F4D3238-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND L | Bank 8 (Non SCADA) | CB 405 (Non-SCADA) | PGE\C7CF | 2016-12-19 09:56:19.8688570 -08:00 | 012110405 | 152111103 | 3 | 3 | 3 | 2 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 |  |  | FALSE | FALSE | 1960 | 2548 | 2352 | 2940 | {88BFAE90-6B34-4DA3-B261-B270D9E25069}
5643 | 4218 | {7CFEFA0A-6E52-11E6-BBF8-D4BED91EFF1A} | MISSION | NEWARK | Bank 21 | CB 2102 | PGE\RDR1 | 2017-05-25 13:18:53.8038081 -07:00 |  | 083371103 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  | Substation Bank | FALSE | FALSE | 2004 | 2606 | 2200 | 2640 | {8039FE2E-77C0-412E-A23C-E1FF2A4DCC64}
5644 | 4154 | {9059BE57-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | BALFOUR | Bank 1 | CB 1101 (Non-SCADA) | PGE\WCL5 | 2017-03-31 09:54:18.3339030 -07:00 | 014321101 | 083371104 | 8 | 3 | 3 | 1 | 229 | 5 | 4.95 | 229 | 5 | 4.95 | 298 | 6.5 | 6.44 | 298 | 6.5 | 6.44 | 275 | 6 | 5.94 | 275 | 6 | 5.94 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 241 amp reg limitation (Summer Normal) not in EDPI lookup tables. |  | FALSE | FALSE | 320 | 416 | 384 | 481 | {00000000-0000-0000-0000-000000000000}
5647 | 4218 | {830AAF59-6E52-11E6-BBF8-D4BED91EFF1A} | MISSION | NEWARK | Bank 21 | CB 2103 | PGE\RDR1 | 2017-05-25 10:33:26.0094423 -07:00 |  | 152851102 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 665 | 24.88 | 24.63 | 665 | 24.88 | 24.63 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 667 | 24.95 | 24.7 | 667 | 24.95 | 24.7 |  | Substation Bank | FALSE | FALSE | 2004 | 2606 | 2200 | 2640 | {5F56193A-9C75-4517-9798-E9FDC0B0C8F2}
5648 | 4218 | {8F28F048-6E52-11E6-BBF8-D4BED91EFF1A} | MISSION | NEWARK | Bank 21 | CB 2104 | PGE\RDR1 | 2017-05-25 13:03:47.9803640 -07:00 |  | 152851104 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 665 | 24.88 | 24.63 | 665 | 24.88 | 24.63 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 667 | 24.95 | 24.7 | 667 | 24.95 | 24.7 |  | Substation Bank | FALSE | FALSE | 2004 | 2606 | 2200 | 2640 | {FD0FF6DE-36C8-47B9-BAEB-7ECDD13F3FC2}
5649 | 4218 | {8F28F085-6E52-11E6-BBF8-D4BED91EFF1A} | MISSION | NEWARK | Bank 21 | CB 2105 | PGE\RDR1 | 2017-05-25 13:07:50.1968322 -07:00 |  | 082160401 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  | Substation Bank | FALSE | FALSE | 2004 | 2606 | 2200 | 2640 | {F831C5B4-B3C0-4231-BD57-189255D2168C}
5650 | 4219 | {242FDFFB-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | LONE TREE | Bank 1 | CB 2101 | PGE\WCL5 | 2017-01-12 11:04:01.6360124 -08:00 | 0132302101 | 152851105 | 22 | 3 | 3 | 1 | 578 | 20.8 | 20.59 | 570 | 20.52 | 20.31 | 689 | 24.8 | 24.55 | 689 | 24.8 | 24.55 | 600 | 21.6 | 21.38 | 570 | 20.52 | 20.31 | 732 | 26.35 | 26.09 | 732 | 26.35 | 26.09 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {189E0EA6-1CF3-4CF3-A627-ED1CE10A2B4F}
5652 | 4219 | {242FE015-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | LONE TREE | Bank 1 | CB 2102 | PGE\WCL5 | 2017-01-12 11:05:46.2828248 -08:00 | 0132302102 | 152851106 | 22 | 3 | 3 | 1 | 578 | 20.8 | 20.59 | 570 | 20.52 | 20.31 | 689 | 24.8 | 24.55 | 689 | 24.8 | 24.55 | 600 | 21.6 | 21.38 | 570 | 20.52 | 20.31 | 732 | 26.35 | 26.09 | 732 | 26.35 | 26.09 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {E245799E-FF5B-4366-8E6D-77526919225B}
5654 | 4220 | {56967315-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | RESEARCH | Bank 1 | CB 2101 | PGE\MFN3 | 2016-11-30 16:19:31.4558403 -08:00 | 0146902101 | 152851107 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 732 | 27.66 | 27.38 | 732 | 27.66 | 27.38 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {C475FFEF-97FB-4B82-96E2-49145808CCCF}
5670 | 4220 | {5C92B49F-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | RESEARCH | Bank 1 | CB 2102 | PGE\MFN3 | 2016-11-30 15:56:21.9777865 -08:00 | 0146902102 | 083371105 | 12 | 3 | 3 | 1 | 573 | 21.66 | 21.44 | 573 | 21.66 | 21.44 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 732 | 27.66 | 27.38 | 732 | 27.66 | 27.38 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {48BF4906-C0A6-4380-A0BE-58CEBEBC2279}
5671 | 4220 | {5C92B4B9-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | RESEARCH | Bank 1 | CB 2103 (Non-SCADA) | PGE\MFN3 | 2016-11-30 16:06:58.6114868 -08:00 | 0146902103 | 083371106 | 12 | 3 | 3 | 1 | 515 | 19.46 | 19.27 | 515 | 19.46 | 19.27 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 666 | 25.17 | 24.92 | 666 | 25.17 | 24.92 | 711 | 26.87 | 26.6 | 711 | 26.87 | 26.6 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {B936263B-9E58-4FD2-8F76-136A29DA3E16}
5675 | 4226 | {BD86DA3F-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DUMBARTON | Bank 3 | CB 1109 | PGE\RDR1 | 2017-06-13 13:44:50.8051535 -07:00 | 0144701109 | 083371107 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2434 | 2200 | 2640 | {6ED92D4C-23A4-4B9C-8182-0811006D127D}
5677 | 4226 | {BD86DA4F-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DUMBARTON | Bank 3 | CB 1110 | PGE\RDR1 | 2017-06-13 13:59:41.0617669 -07:00 | 0144701110 | 083371108 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2434 | 2200 | 2640 | {4A5DC079-1D03-4BA7-8F4A-AD09C718E783}
5678 | 4226 | {FD10FE6A-FDD1-11E5-9D37-D4BED91EFF1A} | MISSION | DUMBARTON | Bank 3 | CB 1111 | PGE\RDR1 | 2017-06-13 14:33:17.6684205 -07:00 | 0144701111 | 083371109 | 7 | 3 | 3 | 2 | 740 | 15.98 | 15.82 | 740 | 15.98 | 15.82 | 963 | 20.8 | 20.59 | 963 | 20.8 | 20.59 | 888 | 19.18 | 18.99 | 888 | 19.18 | 18.99 | 1000 | 21.6 | 21.38 | 1000 | 21.6 | 21.38 |  |  | FALSE | FALSE | 2083 | 2434 | 2200 | 2640 | {A9198A09-ABDF-459F-8CB7-BCA509A0503E}
5680 | 4226 | {BD86DA5F-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | DUMBARTON | Bank 3 | CB 1112 | PGE\RDR1 | 2017-06-13 14:43:24.4693999 -07:00 | 0144701112 | 083371110 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2434 | 2200 | 2640 | {8451F1B9-7624-4178-876E-AF7B330E4B20}
5681 | 4227 | {473E9D63-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | BARRY | Bank 1 | CB 1101 | PGE\HSA1 | 2016-12-02 13:59:18.6458565 -08:00 | 1521101101 | 152691103 | 8 | 3 | 3 | 1 | 229 | 5 | 4.95 | 217 | 4.74 | 4.69 | 298 | 6.5 | 6.44 | 283 | 6.18 | 6.12 | 275 | 6 | 5.94 | 261 | 5.7 | 5.64 | 300 | 6.55 | 6.48 | 285 | 6.22 | 6.16 |  |  | TRUE | FALSE | 229 | 298 | 275 | 344 | {90B5E21A-EF42-4C3D-A96C-32B71023C219}
5684 | 4227 | {473E9D6C-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | BARRY | Bank 1 | CB 1102 | PGE\HSA1 | 2016-12-02 13:55:24.8332135 -08:00 | 1521101102 | 083371111 | 8 | 3 | 3 | 1 | 229 | 5 | 4.95 | 217 | 4.74 | 4.69 | 298 | 6.5 | 6.44 | 283 | 6.18 | 6.12 | 275 | 6 | 5.94 | 261 | 5.7 | 5.64 | 300 | 6.55 | 6.48 | 285 | 6.22 | 6.16 |  |  | TRUE | FALSE | 229 | 298 | 275 | 344 | {34172AA5-AF5A-44FD-8D03-5DFC790967EF}
5685 | 4227 | {473E9D75-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | BARRY | Bank 1 | CB 1103 | PGE\HSA1 | 2016-12-02 13:54:40.2140675 -08:00 | 1521101103 | 152691104 | 8 | 3 | 3 | 1 | 229 | 5 | 4.95 | 217 | 4.74 | 4.69 | 298 | 6.5 | 6.44 | 283 | 6.18 | 6.12 | 275 | 6 | 5.94 | 261 | 5.7 | 5.64 | 344 | 7.51 | 7.43 | 326 | 7.11 | 7.04 |  |  | TRUE | FALSE | 229 | 298 | 275 | 344 | {7313371F-F8C4-40B0-9DD9-4C153254A49A}
5686 | 4230 | {AB266A85-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | SARATOGA | Bank 1 | CB 1103 | PGE\IRB2 | 2016-12-06 15:27:16.6351960 -08:00 | 0833701103 | 152691107 | 8 | 3 | 3 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2593 | 3371 | 3112 | 3890 | {7A0B91AD-AD12-4995-9E6D-3ADF01106DD4}
5687 | 4230 | {AB266ABF-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | SARATOGA | Bank 1 | CB 1104 | PGE\IRB2 | 2016-12-06 15:26:02.0029074 -08:00 | 0833701104 | 152691108 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2593 | 3371 | 3112 | 3890 | {F58D8C2D-E4EE-4AB4-89E0-376FE30378FC}
5688 | 4233 | {5A80369B-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | HARTER | Bank 1 | CB 1102 | PGE\HSA1 | 2016-12-02 19:27:48.8729211 -08:00 | 1528501102 | 152691109 | 8 | 3 | 3 | 1 | 636 | 13.88 | 13.74 | 636 | 13.88 | 13.74 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {BB73B89B-1AF4-4FB3-9458-4DD5F346F413}
5692 | 4233 | {5A8036A4-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | HARTER | Bank 1 | CB 1104 | PGE\HSA1 | 2016-12-02 16:21:53.6713976 -08:00 | 1528501104 | 152691110 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {82A6E1CF-C99D-4BCB-8E60-11CE4045A0C4}
5694 | 4235 | {AB2668B0-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LOYOLA | Bank 1 | CB 401 | PGE\MSJ9 | 2017-04-25 14:45:10.9097128 -07:00 | 082160401 | 153132101 | 3 | 3 | 3 | 2 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 |  |  | FALSE | FALSE | 693 | 902 | 832 | 1040 | {B59CA95F-499E-42E8-ABC2-9F6FC01AE2F3}
5699 | 4240 | {5A8036B7-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | HARTER | Bank 2 | CB 1105 | PGE\HSA1 | 2016-12-06 17:33:38.0164828 -08:00 | 1528501105 | 153132102 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {361C2E5B-0CD3-407D-AB10-E1BF2F9D2233}
5707 | 4240 | {5A8036C0-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | HARTER | Bank 2 | CB 1106 | PGE\HSA1 | 2016-12-05 16:02:29.8574134 -08:00 | 1528501106 | 153132104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {DC89D801-43F5-41E0-A03F-65A3F8C01B7D}
5712 | 4240 | {5A8036C9-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | HARTER | Bank 2 | CB 1107 | PGE\HSA1 | 2016-12-05 16:54:18.3162778 -08:00 | 1528501107 | 153132105 | 8 | 3 | 3 | 1 | 636 | 13.88 | 13.74 | 636 | 13.88 | 13.74 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {8C0D99B9-A77E-4002-B24E-B54977299299}
5721 | 4230 | {AB266ADD-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | SARATOGA | Bank 1 | CB 1105 | PGE\IRB2 | 2016-12-06 11:24:48.5704180 -08:00 | 0833701105 | 152201101 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2593 | 3371 | 3112 | 3890 | {33AE5676-413A-4ADC-98CD-A48478C5C715}
5722 | 4230 | {AB266AF4-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | SARATOGA | Bank 1 | CB 1106 | PGE\IRB2 | 2016-12-07 15:24:51.2845211 -08:00 | 0833701106 | 152201102 | 8 | 3 | 3 | 2 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 549 | 11.98 | 11.86 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2593 | 3371 | 3112 | 3890 | {3D46F91E-D200-48AE-A376-E874CE1F827C}
5723 | 4231 | {B124864C-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | SARATOGA | Bank 2 | CB 1107 | PGE\IRB2 | 2016-12-06 15:24:29.1359803 -08:00 | 0833701107 | 152921101 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2593 | 3371 | 3112 | 3890 | {794E48E2-6024-444A-B84D-8862FEEDAFEE}
5724 | 4231 | {B1248678-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | SARATOGA | Bank 2 | CB 1108 | PGE\IRB2 | 2016-12-06 14:41:05.2806607 -08:00 | 0833701108 | 153791101 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2593 | 3371 | 3112 | 3890 | {4263CB78-4EDE-473E-8755-09CE827512A9}
5725 | 4231 | {B124868F-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | SARATOGA | Bank 2 | CB 1109 | PGE\IRB2 | 2016-12-06 14:41:22.6750399 -08:00 | 0833701109 | 012200404 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2593 | 3371 | 3112 | 3890 | {F4C83C04-F395-4882-9023-1F93EF5E271F}
5726 | 4231 | {B12486C2-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | SARATOGA | Bank 2 | CB 1110 | PGE\IRB2 | 2016-12-06 14:37:16.8309106 -08:00 | 0833701110 | 012200403 | 8 | 3 | 3 | 2 | 581 | 12.68 | 12.55 | 581 | 12.68 | 12.55 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2593 | 3371 | 3112 | 3890 | {B90898D1-2E08-45C0-A5B6-680735CB745E}
5728 | 4243 | {A0BFD415-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | HIGGINS | Bank 1 | CB 1103 | PGE\RVS7 | 2016-12-06 14:45:05.9781188 -08:00 | 1526901103 | 013560401 | 8 | 3 | 3 | 1 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | *Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. Summer Normal = 708 Amps; Summer Emergency = 740 Amps; Winter Normal = 740 Amps; Winter Emergency = 740 Amps. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {29664D16-5069-452B-9DB5-24E8D855E1E1}
5729 | 4231 | {B12486EE-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | SARATOGA | Bank 2 | CB 1111 | PGE\IRB2 | 2016-12-06 15:21:46.7207059 -08:00 | 0833701111 | 013232105 | 8 | 3 | 3 | 2 | 581 | 12.68 | 12.55 | 581 | 12.68 | 12.55 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2593 | 3371 | 3112 | 3890 | {FCC9276E-DEAB-4FB8-9625-C29E95220467}
5730 | 4243 | {A0BFD41E-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | HIGGINS | Bank 1 | CB 1104 | PGE\RVS7 | 2016-12-07 08:57:05.2242446 -08:00 | 1526901104 | 163711701 | 8 | 3 | 3 | 1 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | *Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. Summer Normal = 708 Amps (715Al); Summer Emergency = 740 Amps; Winter Normal = 740 Amps; Winter Emergency = 740 Amps. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B4F33A53-433F-4B57-93FB-F15188733DD1}
5731 | 4245 | {A0BFD42A-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | HIGGINS | Bank 2 | CB 1107 | PGE\RVS7 | 2016-12-07 09:09:39.5163194 -08:00 | 1526901107 | 163711703 | 8 | 3 | 3 | 1 | 636 | 13.88 | 13.74 | 636 | 13.88 | 13.74 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | *Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. Summer Normal = 661 Amps; Summer Emergency = 740 Amps; Winter Normal = 717 Amps; Winter Emergency = 740 Amps. |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {94634724-B6EC-4A2F-BFCD-89894BEF9A9F}
5732 | 4245 | {A0BFD433-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | HIGGINS | Bank 2 | CB 1108 | PGE\RVS7 | 2016-12-07 09:12:48.8705133 -08:00 | 1526901108 | 163711702 | 8 | 3 | 3 | 1 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | *Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. Summer Normal = 708 Amps (715Al); Summer Emergency = 740 Amps; Winter Normal = 740 Amps; Winter Emergency = 740 Amps. |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {BFA9AAAC-9A7D-4B94-8678-9A5A12CA26A3}
5733 | 4246 | {A0BFD446-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | HIGGINS | Bank 3 | CB 1109 | PGE\RVS7 | 2016-12-07 09:16:50.9679167 -08:00 | 1526901109 | 163711704 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | * Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300 |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {212A46B6-9578-4C31-9C8D-C63375B3ABC3}
5734 | 4246 | {A0BFD44F-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | HIGGINS | Bank 3 | CB 1110 | PGE\RVS7 | 2016-12-07 09:20:59.4616122 -08:00 | 1526901110 | 163240401 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | * Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300 |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {5BDD735A-5F5F-49F4-B923-45F4F4EEB31E}
5735 | 4247 | {A7233032-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | NARROWS | Bank 1 | CB 2101 | PGE\RVS7 | 2016-12-07 10:20:22.5105203 -08:00 | 1531302101 | 163240402 | 12 | 3 | 3 | 1 | 555 | 20.98 | 20.77 | 555 | 20.98 | 20.77 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | *Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. Summer Normal = 600 Amps; Summer Emergency = 600 Amps; Winter Normal = 600 Amps; Winter Emergency = 600 Amps. |  | FALSE | FALSE | 555 | 722 | 666 | 833 | {EA856F36-A5AA-4685-B066-4FE7C53ABFAD}
5736 | 4247 | {A723303B-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | NARROWS | Bank 1 | CB 2102 | PGE\RVS7 | 2016-12-07 10:20:56.6773673 -08:00 | 1531302102 | 013531101 | 12 | 3 | 3 | 1 | 555 | 20.98 | 20.77 | 555 | 20.98 | 20.77 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | *Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. Summer Normal = 600 Amps; Summer Emergency = 600 Amps; Winter Normal = 600 Amps; Winter Emergency = 600 Amps. |  | FALSE | FALSE | 555 | 722 | 666 | 833 | {78C11BE2-B513-4265-91F4-CFDCC706BDE9}
5738 | 4248 | {A723304E-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | NARROWS | Bank 2 | CB 2104 | PGE\RVS7 | 2016-12-07 10:31:41.4225697 -08:00 | 1531302104 | 013531102 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | *Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. Summer Normal = 578 Amps; Summer Emergency = 600 Amps; Winter Normal = 600 Amps; Winter Emergency = 600 Amps. |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {30DC38EC-576B-4B0D-8FC5-68FF2052FF42}
5739 | 4248 | {A7233057-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | NARROWS | Bank 2 | CB 2105 | PGE\RVS7 | 2016-12-07 10:31:55.0421554 -08:00 | 1531302105 | 013531103 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | 583 | 22.03 | 21.81 | *Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. Summer Normal = 578 Amps; Summer Emergency = 600 Amps; Winter Normal = 600 Amps; Winter Emergency = 600 Amps. |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {89E41E8C-53CB-4264-A3CF-9C052A1F914B}
5740 | 4249 | {A72330E0-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PIKE CITY | Bank 1 | CB 1101 | PGE\RVS7 | 2016-12-07 10:39:56.9252425 -08:00 | 1522001101 | 013531104 | 8 | 3 | 3 | 1 | 154 | 3.36 | 3.33 | 154 | 3.36 | 3.33 | 173 | 3.78 | 3.74 | 173 | 3.78 | 3.74 | 190 | 4.15 | 4.11 | 190 | 4.15 | 4.11 | 190 | 4.15 | 4.11 | 190 | 4.15 | 4.11 | *Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. Summer Normal = 137 Amps; Summer Emergency = 167 Amps; Winter Normal = 165 Amps; Winter Emergency = 190 Amps. |  | FALSE | FALSE | 274 | 313 | 313 | 313 | {1F779874-A587-4E25-95AC-C93953FBF956}
5741 | 4249 | {A72330E9-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PIKE CITY | Bank 1 | CB 1102 | PGE\RVS7 | 2016-12-07 10:41:16.6807150 -08:00 | 1522001102 | 152261103 | 8 | 3 | 3 | 1 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | 70 | 1.53 | 1.51 | *Phase relay -100 amps of PMT > 600, 83.3% of PMT between 300 - 600, or -50 amps of PMT < 300. |  | FALSE | FALSE | 274 | 313 | 313 | 313 | {00413AFA-DC61-45A6-A0AD-4378B44BB3BF}
5742 | 4250 | {4D891578-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | BROWNS VALLEY | Bank 1 | CB 1101 | PGE\RVS7 | 2016-12-07 11:09:41.1866923 -08:00 | 1529201101 | 152261104 | 8 | 3 | 3 | 1 | 114 | 2.49 | 2.47 | 114 | 2.49 | 2.47 | 148 | 3.23 | 3.2 | 148 | 3.23 | 3.2 | 137 | 2.99 | 2.96 | 137 | 2.99 | 2.96 | 171 | 3.73 | 3.69 | 171 | 3.73 | 3.69 | *Browns Valley Bank #1 is 3-750/862 KVA (2586 KVA) which is the limiting factor. Summer Normal = 113 Amps; Summer Emergency = 146 Amps; Winter Normal = 141 Amps; Winter Emergency = 169 Amps. |  | FALSE | FALSE | 114 | 148 | 137 | 171 | {4216B209-E799-400C-A4F8-D5641F245565}
5743 | 4251 | {7530FE87-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | SMARTVILLE | Bank 1 | CB 1101 | PGE\RVS7 | 2016-12-07 11:24:58.6399259 -08:00 | 1537901101 | 152261105 | 8 | 3 | 3 | 1 | 100 | 2.18 | 2.16 | 100 | 2.18 | 2.16 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 120 | 2.62 | 2.59 | 120 | 2.62 | 2.59 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 |  |  | FALSE | FALSE | 114 | 148 | 137 | 171 | {6385C632-1627-4993-81B4-5B65D32DAE54}
5745 | 4252 | {B8F48014-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | WALNUT CREEK | Bank 3 (Non SCADA) | CB 404 (Non-SCADA) | PGE\MFN3 | 2016-12-07 11:30:05.2793515 -08:00 | 012200404 | 152261106 | 4 | 3 | 3 | 1 | 333 | 2.52 | 2.49 | 333 | 2.52 | 2.49 | 333 | 2.52 | 2.49 | 333 | 2.52 | 2.49 | 333 | 2.52 | 2.49 | 333 | 2.52 | 2.49 | 333 | 2.52 | 2.49 | 333 | 2.52 | 2.49 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {AB204902-5004-4E46-8053-D3DBD56D3A2C}
5747 | 4253 | {B8F4801A-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | WALNUT CREEK | Bank 4 (Non SCADA) | CB 403 (Non-SCADA) | PGE\MFN3 | 2016-12-07 11:55:31.3308510 -08:00 | 012200403 | 152261107 | 4 | 3 | 3 | 1 | 331 | 2.51 | 2.48 | 331 | 2.51 | 2.48 | 386 | 2.92 | 2.89 | 386 | 2.92 | 2.89 | 367 | 2.78 | 2.75 | 367 | 2.78 | 2.75 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {DA8F81F7-8274-41BF-A888-8008C3AED3A1}
5749 | 4255 | {752A8248-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | SARANAP | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\MFN3 | 2016-12-07 13:00:08.1482160 -08:00 | 013560401 | 152161101 | 4 | 4 | 4 | 2 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 395 | 2.99 | 2.96 | 395 | 2.99 | 2.96 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {1BF418EA-7237-4B08-89FE-04A6EB7C7F8A}
5755 | 4256 | {307BB317-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | LONE TREE | Bank 2 | CB 2105 | PGE\WCL5 | 2017-01-12 11:01:30.3287027 -08:00 | 0132302105 | 152161102 | 22 | 3 | 3 | 1 | 578 | 20.8 | 20.59 | 570 | 20.52 | 20.31 | 689 | 24.8 | 24.55 | 689 | 24.8 | 24.55 | 600 | 21.6 | 21.38 | 570 | 20.52 | 20.31 | 732 | 26.35 | 26.09 | 732 | 26.35 | 26.09 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {DE616EED-02AD-43C4-B305-4198B3C876CF}
5757 | 2425 | {523E8DA9-671D-11E5-80CA-005056A729E5} | YOSEMITE | COTTLE | Bank 1 | CB 1701 | PGE\BXYD | 2016-12-08 11:14:49.8681260 -08:00 | 1637101701 | 013660401 | 10 | 3 | 3 | 1 | 530 | 16.39 | 16.23 | 530 | 16.39 | 16.23 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 |  |  | FALSE | FALSE | 1293 | 1681 | 1552 | 1940 | {F68C625C-BFF5-4382-A33F-F8233C8AF1F0}
5758 | 2425 | {523E8DB7-671D-11E5-80CA-005056A729E5} | YOSEMITE | COTTLE | Bank 1 | CB 1703 | PGE\JCD5 | 2017-05-22 15:02:58.4900918 -07:00 | 1637101703 | 013660402 | 10 | 3 | 3 | 1 | 636 | 19.66 | 19.46 | 636 | 19.66 | 19.46 | 667 | 20.62 | 20.41 | 667 | 20.62 | 20.41 | 667 | 20.62 | 20.41 | 667 | 20.62 | 20.41 | 667 | 20.62 | 20.41 | 667 | 20.62 | 20.41 |  |  | FALSE | FALSE | 1293 | 1681 | 1552 | 1940 | {FBC07E8F-7EDA-4DA2-AE2B-FD1D3136C590}
5759 | 4260 | {523E8DD1-671D-11E5-80CA-005056A729E5} | YOSEMITE | COTTLE | Bank 2 | CB 1702 | PGE\JCD5 | 2017-05-22 15:08:52.8654050 -07:00 | 1637101702 | 152701107 | 10 | 3 | 3 | 1 | 636 | 19.66 | 19.46 | 636 | 19.66 | 19.46 | 667 | 20.62 | 20.41 | 667 | 20.62 | 20.41 | 667 | 20.62 | 20.41 | 667 | 20.62 | 20.41 | 667 | 20.62 | 20.41 | 667 | 20.62 | 20.41 |  |  | FALSE | FALSE | 1293 | 1681 | 1552 | 1940 | {CB5050AB-9836-42DE-A197-EAD0FF263B5F}
5760 | 4260 | {523E8DE2-671D-11E5-80CA-005056A729E5} | YOSEMITE | COTTLE | Bank 2 | CB 1704 | PGE\JLDe | 2017-05-25 12:26:44.7870098 -07:00 | 1637101704 | 152701108 | 10 | 3 | 3 | 1 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 | 600 | 18.55 | 18.36 |  |  | FALSE | FALSE | 1293 | 1681 | 1552 | 1940 | {4A9218D5-D845-4163-A8A6-E8501C460A1E}
5761 | 4262 | {643D9936-671D-11E5-80CA-005056A729E5} | YOSEMITE | TAR FLAT | Bank 1 | CB 401 (Non-SCADA) | PGE\BXYD | 2017-01-09 09:28:50.6997272 -08:00 | 163240401 | 012011101 | 4 | 3 | 3 | 1 | 325 | 2.46 | 2.44 | 308 | 2.33 | 2.31 | 363 | 2.75 | 2.72 | 344 | 2.6 | 2.57 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 |  |  | FALSE | FALSE | 613 | 613 | 613 | 613 | {9AC0F50C-85A8-4E6C-A031-53D98BC6C855}
5762 | 4262 | {643D9939-671D-11E5-80CA-005056A729E5} | YOSEMITE | TAR FLAT | Bank 1 | CB 402 (Non-SCADA) | PGE\BXYD | 2016-12-08 12:53:26.2203312 -08:00 | 163240402 | 012011102 | 4 | 3 | 3 | 1 | 325 | 2.46 | 2.44 | 325 | 2.46 | 2.44 | 363 | 2.75 | 2.72 | 363 | 2.75 | 2.72 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 613 | 613 | 613 | 613 | {9D4785D8-DFF3-47E9-919E-25EB2712062D}
5763 | 4254 | {17719C51-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | LAKEWOOD | Bank 5 | CB 1101 | PGE\MFN3 | 2016-12-08 16:37:32.4345704 -08:00 | 0135301101 | 012011103 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 447 | 9.76 | 9.66 | 447 | 9.76 | 9.66 | 514 | 11.22 | 11.11 | 514 | 11.22 | 11.11 | 549 | 11.98 | 11.86 | 549 | 11.98 | 11.86 |  |  | FALSE | FALSE | 1145 | 1488 | 1374 | 1717 | {0DD58DB5-2587-4731-B3FA-98BB446639CF}
5765 | 4254 | {17719C56-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | LAKEWOOD | Bank 5 | CB 1102 | PGE\MFN3 | 2016-12-08 16:43:35.8429828 -08:00 | 0135301102 | 012011104 | 8 | 3 | 3 | 1 | 422 | 9.21 | 9.12 | 422 | 9.21 | 9.12 | 536 | 11.7 | 11.58 | 536 | 11.7 | 11.58 | 468 | 10.21 | 10.11 | 468 | 10.21 | 10.11 | 566 | 12.35 | 12.23 | 566 | 12.35 | 12.23 |  |  | FALSE | FALSE | 1145 | 1488 | 1374 | 1717 | {D559568B-A7A0-4E2E-99AF-B3D28EF35A92}
5766 | 4254 | {17719C64-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | LAKEWOOD | Bank 5 | CB 1103 | PGE\MFN3 | 2016-12-08 16:47:34.2677413 -08:00 | 0135301103 | 012011105 | 8 | 3 | 3 | 1 | 434 | 9.47 | 9.38 | 434 | 9.47 | 9.38 | 486 | 10.61 | 10.5 | 486 | 10.61 | 10.5 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 |  |  | FALSE | FALSE | 1145 | 1488 | 1374 | 1717 | {B587750E-063D-4763-981F-4BFEA44E7E12}
5768 | 4254 | {17719C69-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | LAKEWOOD | Bank 5 | CB 1104 | PGE\MFN3 | 2016-12-08 17:29:20.3689413 -08:00 | 0135301104 | 012011106 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 639 | 13.95 | 13.81 | 639 | 13.95 | 13.81 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 674 | 14.71 | 14.56 | 674 | 14.71 | 14.56 |  |  | FALSE | FALSE | 1145 | 1488 | 1374 | 1717 | {4F56B627-E896-4A3A-918C-3AF9DF2BD0D1}
5769 | 4244 | {946B5444-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | DIAMOND SPRINGS | Bank 1 | CB 1103 | PGE\JSKe | 2016-12-09 09:55:58.2909390 -08:00 | 1522601103 | 012011110 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {BE616E51-84EC-4E77-B160-6DDE2D404949}
5770 | 4244 | {946B544D-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | DIAMOND SPRINGS | Bank 1 | CB 1104 | PGE\JSKe | 2016-12-09 09:55:43.1578720 -08:00 | 1522601104 | 012011112 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {289ACC5A-1CF2-4822-A070-94F334ACC995}
5771 | 4263 | {9AA85B2A-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | DIAMOND SPRINGS | Bank 2 | CB 1105 | PGE\JSKe | 2016-12-09 10:22:04.5598791 -08:00 | 1522601105 | 012011116 | 8 | 3 | 3 | 1 | 565 | 12.33 | 12.21 | 565 | 12.33 | 12.21 | 625 | 13.64 | 13.5 | 625 | 13.64 | 13.5 | 712 | 15.54 | 15.38 | 712 | 15.54 | 15.38 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {699613D7-4507-4F55-9379-CC650384C02B}
5772 | 4263 | {9AA85B3A-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | DIAMOND SPRINGS | Bank 2 | CB 1106 | PGE\JSKe | 2016-12-09 10:25:12.2886712 -08:00 | 1522601106 | 012011121 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {AB58B07C-36A0-4A47-9BA7-E2535408076D}
5774 | 4263 | {9AA85B66-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | DIAMOND SPRINGS | Bank 2 | CB 1107 | PGE\JSKe | 2016-12-09 10:38:16.2462816 -08:00 | 1522601107 | 012040406 | 8 | 3 | 3 | 1 | 650 | 14.19 | 14.05 | 650 | 14.19 | 14.05 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 | 750 | 16.37 | 16.21 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {84961554-6EAA-4078-807F-8CBB78FA98E2}
5776 | 4264 | {83929CB0-BC14-11E6-93A9-D4BED91EFF1A} | MISSION | BANCROFT | UNIT SUB 401 | CB 401/2 (Non-SCADA) | PGE\GMK5 | 2016-12-09 13:44:56.4877740 -08:00 |  | 012040407 | 1 | 4 | 4 | 2 | 400 | 1.66 | 1.64 | 400 | 1.66 | 1.64 | 400 | 1.66 | 1.64 | 400 | 1.66 | 1.64 | 400 | 1.66 | 1.64 | 400 | 1.66 | 1.64 | 400 | 1.66 | 1.64 | 400 | 1.66 | 1.64 |  |  | FALSE | FALSE | 505 | 505 | 505 | 505 | {00000000-0000-0000-0000-000000000000}
5777 | 4265 | {96348270-BC14-11E6-93A9-D4BED91EFF1A} | MISSION | BANCROFT | UNIT SUB 402 | CB 402/2 (Non-SCADA) | PGE\GMK5 | 2016-12-09 13:51:48.3323157 -08:00 |  | 012040408 | 1 | 4 | 4 | 2 | 397 | 1.65 | 1.63 | 397 | 1.65 | 1.63 | 400 | 1.66 | 1.64 | 400 | 1.66 | 1.64 | 400 | 1.66 | 1.64 | 400 | 1.66 | 1.64 | 400 | 1.66 | 1.64 | 400 | 1.66 | 1.64 |  |  | FALSE | FALSE | 505 | 505 | 505 | 505 | {00000000-0000-0000-0000-000000000000}
5778 | 4267 | {8E5DEF26-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | AUBURN | Bank 1 | CB 1101 | PGE\MTN6 | 2016-12-09 16:08:43.0407788 -08:00 | 1521601101 | 012040410 | 8 | 3 | 3 | 1 | 384 | 8.38 | 8.3 | 384 | 8.38 | 8.3 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 461 | 10.06 | 9.96 | 461 | 10.06 | 9.96 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 384 | 500 | 461 | 577 | {B1B4719E-39AE-44A8-977A-432D98790C64}
5779 | 4267 | {8E5DEF2F-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | AUBURN | Bank 1 | CB 1102 | PGE\MTN6 | 2016-12-09 16:13:52.2225303 -08:00 | 1521601102 | 013532223 | 8 | 3 | 3 | 1 | 384 | 8.38 | 8.3 | 384 | 8.38 | 8.3 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 461 | 10.06 | 9.96 | 461 | 10.06 | 9.96 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 384 | 500 | 461 | 577 | {BDE1C189-6C50-4F29-8A3D-DBB87F6E80D1}
5780 | 3982 | {F9CFCC8C-0E48-11E6-95F2-D4BED91EFF1A} | MISSION | PARSONS | BANK 401 (Non SCADA) | CB 401 (Non-SCADA) | PGE\RDR1 | 2017-05-09 14:25:27.5428476 -07:00 | 013660401 | 013111151 | 3 | 3 | 3 | 2 | 277 | 2 | 1.98 | 277 | 2 | 1.98 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 277 | 360 | 333 | 416 | {9E2BC283-C7E9-4D21-A867-7F170A0BF85C}
5781 | 3983 | {FFFFBF46-0E48-11E6-95F2-D4BED91EFF1A} | MISSION | PARSONS | BANK 402 (Non SCADA) | CB 402 (Non-SCADA) | PGE\RDR1 | 2017-05-10 07:46:30.8204645 -07:00 | 013660402 | 013532224 | 3 | 3 | 3 | 2 | 277 | 2 | 1.98 | 277 | 2 | 1.98 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 277 | 360 | 333 | 416 | {141397C4-3004-4206-945E-FB3983064962}
5782 | 4275 | {8E5DEF45-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | BELL | Bank 2 | CB 1107 | PGE\MTN6 | 2016-12-12 12:07:42.8630028 -08:00 | 1527001107 | 013532110 | 8 | 3 | 3 | 1 | 573 | 12.51 | 12.38 | 573 | 12.51 | 12.38 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 1937 | {B95D018E-187D-46A0-AFD8-67C269C9DBCC}
5783 | 4275 | {8E5DEF55-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | BELL | Bank 2 | CB 1108 | PGE\MTN6 | 2016-12-12 14:19:12.0666816 -08:00 | 1527001108 | 013532111 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 1937 | {3C2D3C1D-9138-4D79-ADF2-6863F391A8D6}
5785 | 4272 | {4273FA69-22D0-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND C | Bank 3 | CB 1101 | PGE\C7CF | 2016-12-12 16:56:14.6069243 -08:00 | 0120101101 | 013532112 | 8 | 3 | 3 | 2 | 423 | 9.23 | 9.14 | 423 | 9.23 | 9.14 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 436 | 9.52 | 9.42 | 436 | 9.52 | 9.42 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B3A68C17-4580-4003-9211-3F5DD69E8292}
5786 | 4272 | {609C97E0-22D0-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND C | Bank 3 | CB 1102 | PGE\C7CF | 2016-12-12 16:59:24.2874829 -08:00 | 0120101102 | 014592105 | 8 | 3 | 3 | 2 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {67F4B276-61C0-4EC0-8BA4-F7D26AEB6FEA}
5787 | 4272 | {7F494AE7-22D0-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND C | Bank 3 | CB 1103 | PGE\C7CF | 2016-12-12 17:07:09.9930512 -08:00 | 0120101103 | 012541107 | 8 | 3 | 3 | 2 | 423 | 9.23 | 9.14 | 423 | 9.23 | 9.14 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 436 | 9.52 | 9.42 | 436 | 9.52 | 9.42 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {EABEBB1D-B32F-4D00-A9E0-683C5C9E8F4E}
5788 | 4272 | {88DB1402-22D0-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND C | Bank 3 | CB 1104 | PGE\C7CF | 2016-12-12 17:10:33.2307343 -08:00 | 0120101104 | 012541109 | 8 | 3 | 3 | 2 | 423 | 9.23 | 9.14 | 423 | 9.23 | 9.14 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 436 | 9.52 | 9.42 | 436 | 9.52 | 9.42 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {8DAEE8C6-BAE2-4FFE-B3B4-24ADB2EE5503}
5789 | 4272 | {9AB22651-22D0-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND C | Bank 3 | CB 1105 | PGE\C7CF | 2016-12-12 17:14:15.3596764 -08:00 | 0120101105 | 012541110 | 8 | 3 | 3 | 2 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {70FA37CA-090B-44A8-AA14-F8AAEB1E6A89}
5790 | 4272 | {9AB22654-22D0-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND C | Bank 3 | CB 1106 | PGE\C7CF | 2016-12-12 17:18:34.5549367 -08:00 | 0120101106 | 012541111 | 8 | 3 | 3 | 2 | 490 | 10.69 | 10.58 | 490 | 10.69 | 10.58 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {7294BECC-6379-4E15-AF97-AE197D501DAE}
5791 | 4272 | {F4276526-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND C | Bank 3 | CB 1110 | PGE\C7CF | 2016-12-12 17:22:07.3334400 -08:00 | 0120101110 | 012541112 | 8 | 3 | 3 | 2 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {806C53CB-1E04-4D03-863E-B2EBBE4C8AED}
5792 | 4273 | {E1F1F9BF-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND C | Bank 7 | CB 1112 | PGE\C7CF | 2016-12-13 07:51:10.6549659 -08:00 | 0120101112 | 012541114 | 7 | 3 | 3 | 2 | 446 | 9.63 | 9.53 | 446 | 9.63 | 9.53 | 533 | 11.51 | 11.39 | 490 | 10.58 | 10.47 | 459 | 9.91 | 9.81 | 459 | 9.91 | 9.81 | 533 | 11.51 | 11.39 | 490 | 10.58 | 10.47 | 40 Amps to be reserved for Post Office, circuit C1121- ATS |  | FALSE | FALSE | 2777 | 3611 | 3333 | 4166 | {9C126AF1-17F2-40DB-AFA9-E04CF250AB6D}
5793 | 4477 | {E1F1F9C8-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND C | Bank 7 | CB 1116 | PGE\MUSF | 2017-06-24 23:06:06.4869702 -07:00 | 0120101116 | 012541104 | 7 | 3 | 3 | 2 | 263 | 5.68 | 5.62 | 263 | 5.68 | 5.62 | 343 | 7.41 | 7.34 | 343 | 7.41 | 7.34 | 316 | 6.83 | 6.76 | 316 | 6.83 | 6.76 | 395 | 8.53 | 8.44 | 395 | 8.53 | 8.44 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {6E6D0285-D81A-4A00-8A26-54BE45BEEAD3}
5794 | 4273 | {E1F1F9D4-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND C | Bank 7 | CB 1121 | PGE\C7CF | 2016-12-13 08:59:09.1860031 -08:00 | 0120101121 | 012541105 | 7 | 3 | 3 | 2 | 446 | 9.63 | 9.53 | 446 | 9.63 | 9.53 | 549 | 11.86 | 11.74 | 549 | 11.86 | 11.74 | 459 | 9.91 | 9.81 | 459 | 9.91 | 9.81 | 556 | 12.01 | 11.89 | 556 | 12.01 | 11.89 |  |  | FALSE | FALSE | 2777 | 3611 | 3333 | 4166 | {2631408D-D7E8-469E-8767-AEC5F5DBC2E8}
5795 | 4285 | {FBCC6D16-22D0-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND D | Bank 4 - 4kV | CB 406 (Non-SCADA) | PGE\C7CF | 2016-12-13 09:46:11.3197307 -08:00 | 012040406 | 012541101 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 |  |  | FALSE | FALSE | 1321 | 1717 | 1585 | 1981 | {C204453C-B0BE-43D1-BBBC-974619EED4B1}
5796 | 4285 | {FBCC6D19-22D0-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND D | Bank 4 - 4kV | CB 407 (Non-SCADA) | PGE\C7CF | 2016-12-13 09:56:05.7360667 -08:00 | 012040407 | 012541106 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 1321 | 1717 | 1585 | 1981 | {433C7408-0360-449A-8D73-0EF2B36F18CA}
5797 | 4285 | {E019E54D-22D0-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND D | Bank 4 - 4kV | CB 408 (Non-SCADA) | PGE\C7CF | 2016-12-13 10:00:26.0469148 -08:00 | 012040408 | 012541115 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 1321 | 1717 | 1585 | 1981 | {BB7E4D7A-8F95-4680-B751-6BD9CC36D150}
5798 | 4285 | {EB21667D-22D0-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND D | Bank 4 - 4kV | CB 410 (Non-SCADA) | PGE\C7CF | 2016-12-13 10:03:33.8836903 -08:00 | 012040410 | 043251101 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 |  |  | FALSE | FALSE | 1321 | 1717 | 1585 | 1981 | {4BB6BCAF-BCDD-4C79-9FC2-A6ACDD64425A}
5799 | 2526 | {924A0EB7-8A65-11E6-841B-D4BED91EFF1A} | EAST BAY | OAKLAND D | Bank 3 | CB DWF-1 | PGE\MUSF | 2017-03-29 10:24:07.4046192 -07:00 |  | 043251104 | 7 | 3 | 3 | 2 | 505 | 10.91 | 10.8 | 505 | 10.91 | 10.8 | 586 | 12.66 | 12.53 | 586 | 12.66 | 12.53 | 515 | 11.12 | 11.01 | 515 | 11.12 | 11.01 | 598 | 12.92 | 12.79 | 598 | 12.92 | 12.79 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {132D5154-4AF0-4E3A-BCE9-3900510319E7}
5800 | 2526 | {AFCA3E17-8A65-11E6-841B-D4BED91EFF1A} | EAST BAY | OAKLAND D | Bank 3 | CB DWF-2 | PGE\MUSF | 2017-03-29 10:25:50.1653186 -07:00 |  | 043251105 | 7 | 3 | 3 | 2 | 347 | 7.49 | 7.42 | 347 | 7.49 | 7.42 | 385 | 8.32 | 8.24 | 385 | 8.32 | 8.24 | 357 | 7.71 | 7.63 | 357 | 7.71 | 7.63 | 397 | 8.57 | 8.48 | 397 | 8.57 | 8.48 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {DCB3B43E-8218-45F4-B02B-0163C3038FC4}
5801 | 2526 | {AFCA3E2D-8A65-11E6-841B-D4BED91EFF1A} | EAST BAY | OAKLAND D | Bank 3 | CB DWF-3 | PGE\C7CF | 2016-12-13 10:14:18.5699992 -08:00 |  | 043251102 | 8 | 3 | 3 | 2 | 308 | 6.72 | 6.65 | 308 | 6.72 | 6.65 | 342 | 7.46 | 7.39 | 342 | 7.46 | 7.39 | 317 | 6.92 | 6.85 | 317 | 6.92 | 6.85 | 352 | 7.68 | 7.6 | 352 | 7.68 | 7.6 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {02853DBA-3703-472B-B215-0193584105E5}
5803 | 2526 | {AFCA3E43-8A65-11E6-841B-D4BED91EFF1A} | EAST BAY | OAKLAND D | Bank 3 | CB DWF-4 | PGE\C7CF | 2016-12-13 10:16:24.0395526 -08:00 |  | 043251103 | 8 | 3 | 3 | 2 | 308 | 6.72 | 6.65 | 308 | 6.72 | 6.65 | 342 | 7.46 | 7.39 | 342 | 7.46 | 7.39 | 317 | 6.92 | 6.85 | 317 | 6.92 | 6.85 | 352 | 7.68 | 7.6 | 352 | 7.68 | 7.6 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {01A7C0C7-60DD-4774-B471-ECA1ADB02AE1}
5804 | 4286 | {0507CECD-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | LAKEWOOD | Bank 2 | CB 2223 | PGE\MFN3 | 2016-12-14 11:18:19.3418335 -08:00 | 0135302223 | 042042204 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {89D20A1B-3CBD-4225-AF9A-77644AC0FFEA}
5805 | 2410 | {CFDD35E0-D1CA-11E5-8ECE-9CB70D532D7F} | MISSION | SAN LEANDRO | Bank 1 | CB 1151 | PGE\RDR1 | 2017-05-11 10:15:05.1972289 -07:00 | 013111151 | 042042201 | 7 | 3 | 3 | 2 | 492 | 10.63 | 10.52 | 492 | 10.63 | 10.52 | 554 | 11.97 | 11.85 | 554 | 11.97 | 11.85 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 598 | 12.92 | 12.79 | 598 | 12.92 | 12.79 | The 750Cu UG cable will be replaced under 30866455 & the 4/0Cu will be replaced with Rule 20 under 30616108 |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {3EE35F6E-3ED4-49B7-B9A6-3DBC162DBBDA}
5808 | 4286 | {0B349602-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | LAKEWOOD | Bank 2 | CB 2224 | PGE\MFN3 | 2016-12-14 15:37:25.5859351 -08:00 | 0135302224 | 042450411 | 12 | 3 | 3 | 1 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 792 | 29.93 | 29.63 | 792 | 29.93 | 29.63 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {0EEDB900-95BD-4484-9B1D-B681936F19B8}
5817 | 4290 | {1DD3CB50-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | LAKEWOOD | Bank 6 | CB 2110 | PGE\MFN3 | 2016-12-14 16:08:25.4658974 -08:00 | 0135302110 | 042450412 | 12 | 4 | 4 | 2 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {DF0037D8-8E3F-482B-8B62-B68112A42F36}
5821 | 4290 | {1DD3CB79-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | LAKEWOOD | Bank 6 | CB 2111 | PGE\MFN3 | 2016-12-14 16:12:48.9875959 -08:00 | 0135302111 | 042450413 | 12 | 3 | 3 | 1 | 573 | 21.66 | 21.44 | 573 | 21.66 | 21.44 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 634 | 23.96 | 23.72 | 634 | 23.96 | 23.72 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {FC78E2A6-A755-40C2-A540-21CA9427CD3B}
5823 | 4290 | {1DD3CB7E-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | LAKEWOOD | Bank 6 | CB 2112 | PGE\FCR1 | 2017-04-21 16:01:07.1868616 -07:00 | 0135302112 | 042450414 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {FE69DE10-1F7E-49E1-81ED-E0D3090EF4FD}
5825 | 4293 | {9059BE72-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | BRENTWOOD | Bank 1 | CB 2105 | PGE\WCL5 | 2016-12-14 17:12:24.3391966 -08:00 | 0145902105 | 042450415 | 22 | 3 | 3 | 1 | 578 | 20.8 | 20.59 | 578 | 20.8 | 20.59 | 689 | 24.8 | 24.55 | 689 | 24.8 | 24.55 | 627 | 22.57 | 22.34 | 627 | 22.57 | 22.34 | 732 | 26.35 | 26.09 | 732 | 26.35 | 26.09 |  |  | FALSE | FALSE | 1667 | 2167 | 2000 | 2500 | {25734284-7B62-4058-A513-AF266F4BA5F4}
5858 | 4269 | {85756193-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND X | Bank 2 | CB 1107 | PGE\C7CF | 2016-12-19 11:07:44.9522175 -08:00 | 012541107 | 014592112 | 7 | 3 | 3 | 2 | 555 | 11.99 | 11.87 | 555 | 11.99 | 11.87 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 566 | 12.22 | 12.1 | 566 | 12.22 | 12.1 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {42292D38-779C-4CC7-BA46-B335CD2E8F19}
5859 | 4269 | {85756198-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND X | Bank 2 | CB 1109 | PGE\C7CF | 2016-12-19 11:10:02.2183878 -08:00 | 0125401109 | 014592113 | 7 | 3 | 3 | 2 | 555 | 11.99 | 11.87 | 555 | 11.99 | 11.87 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 566 | 12.22 | 12.1 | 566 | 12.22 | 12.1 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {6AF8B9F5-C5E8-4AA7-B40A-9B259143B606}
5860 | 4269 | {857561A0-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND X | Bank 2 | CB 1110 | PGE\C7CF | 2016-12-19 11:11:30.9804114 -08:00 | 0125401110 | 152762101 | 7 | 3 | 3 | 2 | 555 | 11.99 | 11.87 | 555 | 11.99 | 11.87 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 566 | 12.22 | 12.1 | 566 | 12.22 | 12.1 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {DA0711F3-8365-4DD9-B404-FBEAD17E4E22}
5861 | 4269 | {857561A5-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND X | Bank 2 | CB 1111 | PGE\C7CF | 2016-12-19 11:13:48.8132028 -08:00 | 0125401111 | 152762102 | 7 | 3 | 3 | 2 | 555 | 11.99 | 11.87 | 555 | 11.99 | 11.87 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 566 | 12.22 | 12.1 | 566 | 12.22 | 12.1 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {09F10912-4647-4D15-BF75-F132C2AC7D24}
5862 | 4269 | {857561AA-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND X | Bank 2 | CB 1112 | PGE\C7CF | 2016-12-19 11:15:25.9282247 -08:00 | 0125401112 | 152282101 | 7 | 3 | 3 | 2 | 555 | 11.99 | 11.87 | 555 | 11.99 | 11.87 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 566 | 12.22 | 12.1 | 566 | 12.22 | 12.1 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {9711D763-47B9-409F-86E5-A5C271D0FC52}
5863 | 4269 | {8BEB896A-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND X | Bank 2 | CB 1114 | PGE\C7CF | 2016-12-19 11:18:11.7703503 -08:00 | 0125401114 | 083332101 | 7 | 3 | 3 | 2 | 545 | 11.77 | 11.65 | 545 | 11.77 | 11.65 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 556 | 12.01 | 11.89 | 556 | 12.01 | 11.89 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {50075835-8FFA-4147-BEED-D19F7BF42D25}
5864 | 4270 | {92C33179-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND X | Bank 4 | CB 1104 | PGE\C7CF | 2016-12-19 11:28:05.0013939 -08:00 | 0125401104 | 014592108 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {E93105B9-8068-41BC-B01D-C7A888AAAB7F}
5865 | 4271 | {92C33190-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND X | Bank 4 | CB 1105 | PGE\MUSF | 2017-06-09 15:25:50.9076188 -07:00 | 0125401105 | 014592109 | 7 | 3 | 3 | 2 | 426 | 9.2 | 9.11 | 426 | 9.2 | 9.11 | 479 | 10.35 | 10.25 | 479 | 10.35 | 10.25 | 482 | 10.41 | 10.31 | 482 | 10.41 | 10.31 | 515 | 11.12 | 11.01 | 515 | 11.12 | 11.01 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {328FEEDF-3C42-458A-A709-1C47274D2730}
5866 | 4271 | {98DF5332-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND X | Bank 5 | CB 1101 | PGE\C7CF | 2016-12-19 11:33:58.3035586 -08:00 | 0125401101 | 014592110 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {3B92940F-AA94-48BB-A068-776747656383}
5867 | 4271 | {98DF5343-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND X | Bank 5 | CB 1106 | PGE\C7CF | 2016-12-19 11:36:20.1041762 -08:00 | 0125401106 | 014592111 | 8 | 3 | 3 | 2 | 555 | 12.11 | 11.99 | 555 | 12.11 | 11.99 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 566 | 12.35 | 12.23 | 566 | 12.35 | 12.23 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {0E48573F-8F43-4AE7-A346-F91F921A5B36}
5868 | 4271 | {9EFE5AFD-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND X | Bank 5 | CB 1115 | PGE\C7CF | 2016-12-19 11:38:03.5991752 -08:00 | 0125401115 | 083001106 | 8 | 3 | 3 | 2 | 555 | 12.11 | 11.99 | 555 | 12.11 | 11.99 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 566 | 12.35 | 12.23 | 566 | 12.35 | 12.23 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {E535FBB2-91D6-4622-B634-520550151C56}
5870 | 4303 | {CEDE006B-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | BAHIA | Bank 1 | CB 1101 | PGE\C7CF | 2016-12-19 13:02:26.1932224 -08:00 | 0432501101 | 083001107 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2593 | 3371 | 3112 | 3890 | {AA66AB5B-A0DB-4DD2-B253-9929C7BB8F70}
5871 | 4303 | {CEDE0079-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | BAHIA | Bank 1 | CB 1104 | PGE\C7CF | 2016-12-19 13:06:49.8535341 -08:00 | 0432501104 | 083001108 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2593 | 3371 | 3112 | 3890 | {0D882725-BFCC-4CB1-86F7-8D9B59B22BE1}
5872 | 4303 | {D530E910-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | BAHIA | Bank 1 | CB 1105 | PGE\C7CF | 2016-12-19 13:10:19.8262539 -08:00 | 0432501105 | 252321102 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 665 | 14.51 | 14.36 | 665 | 14.51 | 14.36 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2593 | 3371 | 3112 | 3890 | {BC101543-1884-41F5-AF10-9DF9E54DDE86}
5873 | 4304 | {D530E91B-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | BAHIA | Bank 2 | CB 1102 | PGE\C7CF | 2016-12-19 13:15:45.0700988 -08:00 | 0432501102 | 252321103 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 665 | 14.51 | 14.36 | 665 | 14.51 | 14.36 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2593 | 3371 | 3112 | 3890 | {A269A3F3-DFB5-4F22-8E82-76DB76029BD2}
5874 | 4304 | {D530E923-78E5-11E5-8C7B-9CB70D532D7F} | NORTH BAY | BAHIA | Bank 2 | CB 1103 | PGE\C7CF | 2016-12-19 13:19:05.0511973 -08:00 | 0432501103 | 253142101 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 665 | 14.51 | 14.36 | 665 | 14.51 | 14.36 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2593 | 3371 | 3112 | 3890 | {A496E89A-B6F0-49CA-899C-631DB7CC5F82}
5881 | 4305 | {2CD474FB-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | NORTH TOWER | Bank 2 | CB 2204 (Non-SCADA) | PGE\C7CF | 2016-12-19 14:29:51.8302759 -08:00 | 0420402204 | 083001103 | 12 | 3 | 3 | 2 | 396 | 14.97 | 14.82 | 396 | 14.97 | 14.82 | 479 | 18.1 | 17.92 | 479 | 18.1 | 17.92 | 476 | 17.99 | 17.81 | 476 | 17.99 | 17.81 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 |  |  | FALSE | FALSE | 396 | 515 | 476 | 595 | {455E9E17-C49E-4DC0-B57E-9D323CF203E7}
5882 | 4307 | {F2EAF892-E7E2-11E5-9614-9CB70D532D7F} | NORTH BAY | NORTH TOWER | Bank 3 | CB 2201 (Non-SCADA) | PGE\C7CF | 2016-12-19 14:35:03.1676934 -08:00 | 0420402201 | 252461101 | 12 | 3 | 3 | 2 | 369 | 13.95 | 13.81 | 369 | 13.95 | 13.81 | 414 | 15.65 | 15.49 | 414 | 15.65 | 15.49 | 415 | 15.68 | 15.52 | 415 | 15.68 | 15.52 | 443 | 16.74 | 16.57 | 443 | 16.74 | 16.57 |  |  | FALSE | FALSE | 396 | 515 | 476 | 595 | {8BE9B14F-8A4A-449A-9D89-2DF872AE92B8}
5885 | 4308 | {C7A53984-FDD3-11E5-9D37-D4BED91EFF1A} | NORTH BAY | VALLEJO STA B | BANK 2 (Non SCADA) | CB 411 (Non-SCADA) | PGE\C7CF | 2016-12-19 15:59:28.7402015 -08:00 | 042450411 | 252461102 | 4 | 3 | 3 | 2 | 200 | 1.51 | 1.49 | 200 | 1.51 | 1.49 | 260 | 1.97 | 1.95 | 260 | 1.97 | 1.95 | 240 | 1.82 | 1.8 | 240 | 1.82 | 1.8 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 |  |  | FALSE | FALSE | 396 | 515 | 475 | 594 | {27723893-AC19-49ED-A163-2EB8A3BF9B3B}
5886 | 4308 | {CEB35E97-FDD3-11E5-9D37-D4BED91EFF1A} | NORTH BAY | VALLEJO STA B | BANK 2 (Non SCADA) | CB 412 (Non-SCADA) | PGE\C7CF | 2016-12-19 16:06:30.9538877 -08:00 | 042450412 | 252461103 | 4 | 3 | 3 | 2 | 200 | 1.51 | 1.49 | 200 | 1.51 | 1.49 | 260 | 1.97 | 1.95 | 260 | 1.97 | 1.95 | 240 | 1.82 | 1.8 | 240 | 1.82 | 1.8 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 |  |  | FALSE | FALSE | 396 | 515 | 475 | 594 | {2D655DA2-1D43-4018-AB9A-3E222FC07C34}
5887 | 4308 | {CEB35E9A-FDD3-11E5-9D37-D4BED91EFF1A} | NORTH BAY | VALLEJO STA B | BANK 2 (Non SCADA) | CB 413 (Non-SCADA) | PGE\C7CF | 2016-12-19 16:15:25.5789978 -08:00 | 042450413 | 252461105 | 4 | 3 | 3 | 2 | 200 | 1.51 | 1.49 | 200 | 1.51 | 1.49 | 260 | 1.97 | 1.95 | 260 | 1.97 | 1.95 | 240 | 1.82 | 1.8 | 240 | 1.82 | 1.8 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 |  |  | FALSE | FALSE | 396 | 515 | 475 | 594 | {6EA88543-CDEB-4BCA-ADB6-FE84314E60ED}
5888 | 4308 | {CEB35E9D-FDD3-11E5-9D37-D4BED91EFF1A} | NORTH BAY | VALLEJO STA B | BANK 2 (Non SCADA) | CB 414 (Non-SCADA) | PGE\C7CF | 2016-12-19 16:23:19.8954296 -08:00 | 042450414 | 252461107 | 4 | 3 | 3 | 2 | 200 | 1.51 | 1.49 | 200 | 1.51 | 1.49 | 260 | 1.97 | 1.95 | 260 | 1.97 | 1.95 | 240 | 1.82 | 1.8 | 240 | 1.82 | 1.8 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 |  |  | FALSE | FALSE | 396 | 515 | 475 | 594 | {DBD7BD6E-F2F1-4741-9B74-311EBC51E41D}
5889 | 4308 | {D66B5163-FDD3-11E5-9D37-D4BED91EFF1A} | NORTH BAY | VALLEJO STA B | BANK 2 (Non SCADA) | CB 415 (Non-SCADA) | PGE\C7CF | 2016-12-19 16:29:36.8534115 -08:00 | 042450415 | 253151102 | 4 | 3 | 3 | 2 | 200 | 1.51 | 1.49 | 200 | 1.51 | 1.49 | 260 | 1.97 | 1.95 | 260 | 1.97 | 1.95 | 240 | 1.82 | 1.8 | 240 | 1.82 | 1.8 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 |  |  | FALSE | FALSE | 396 | 515 | 475 | 594 | {2F462FD9-7F60-4E61-8890-EFAC6064CA77}
5890 | 4310 | {A8AD190C-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | BRENTWOOD | Bank 3 | CB 2112 | PGE\WCL5 | 2016-12-20 12:06:02.9248225 -08:00 | 0145902112 | 253151103 | 22 | 3 | 3 | 1 | 745 | 26.81 | 26.54 | 745 | 26.81 | 26.54 | 838 | 30.16 | 29.86 | 838 | 30.16 | 29.86 | 972 | 34.98 | 34.63 | 972 | 34.98 | 34.63 | 1000 | 35.99 | 35.63 | 1000 | 35.99 | 35.63 | The UG Cable limitation (not selectable) is parallel sets of 1000Al XLP Cable at station outlet. SN=1006A, SE=1278A, WN=1114A, WE=1348A. |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {DABA263F-B574-40C6-B52F-11CA914E361D}
5892 | 4310 | {AF1B8144-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | BRENTWOOD | Bank 3 | CB 2113 | PGE\WCL5 | 2016-12-20 12:08:17.2269443 -08:00 | 0145902113 | 253151106 | 22 | 3 | 3 | 1 | 745 | 26.81 | 26.54 | 745 | 26.81 | 26.54 | 838 | 30.16 | 29.86 | 838 | 30.16 | 29.86 | 972 | 34.98 | 34.63 | 972 | 34.98 | 34.63 | 1000 | 35.99 | 35.63 | 1000 | 35.99 | 35.63 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1875 | {1EBE489D-F351-4D20-BD06-15EB77F4B8A1}
5894 | 4268 | {9AA85BEF-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | EL DORADO PH | Bank 1 | CB 2101 | PGE\JSKe | 2016-12-21 11:37:42.5300694 -08:00 | 1527602101 | 253151107 | 12 | 3 | 3 | 1 | 373 | 14.1 | 13.96 | 373 | 14.1 | 13.96 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 | 400 | 15.12 | 14.97 |  |  | FALSE | FALSE | 373 | 485 | 448 | 560 | {C29EA7BF-DF88-4014-95BD-84B3484A07E2}
5895 | 4268 | {9AA85C54-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | EL DORADO PH | Bank 1 | CB 2102 | PGE\JSKe | 2016-12-21 11:02:56.7989296 -08:00 | 1527602102 | 252062109 | 12 | 4 | 4 | 2 | 201 | 7.6 | 7.52 | 201 | 7.6 | 7.52 | 227 | 8.58 | 8.49 | 227 | 8.58 | 8.49 | 266 | 10.05 | 9.95 | 266 | 10.05 | 9.95 | 284 | 10.73 | 10.62 | 284 | 10.73 | 10.62 |  |  | FALSE | FALSE | 373 | 485 | 448 | 560 | {43FBAFDB-3BC5-4097-AAF8-87FE7E6B8752}
5897 | 4311 | {A0BFD53D-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | MOUNTAIN QUARRIES | Bank 1 | CB 2101 | PGE\JSKe | 2016-12-21 14:08:30.5414202 -08:00 | 1522802101 | 013652203 | 12 | 3 | 3 | 1 | 336 | 12.7 | 12.57 | 336 | 12.7 | 12.57 | 437 | 16.52 | 16.35 | 437 | 16.52 | 16.35 | 403 | 15.23 | 15.08 | 403 | 15.23 | 15.08 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 |  |  | FALSE | FALSE | 423 | 550 | 508 | 635 | {B0EED2FC-5B5D-41F0-AD2B-F9E89FBE409B}
5898 | 1054 | {703C567D-900D-11E6-841B-D4BED91EFF1A} | CENTRAL COAST | WATSONVILLE | BANK 3 (Non SCADA) | CB 2101 | PGE\MTDR | 2017-07-13 10:21:09.4255499 -07:00 | 0833302101 | 013652204 | 12 | 4 | 4 | 2 | 423 | 15.99 | 15.83 | 423 | 15.99 | 15.83 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 | 500 | 18.9 | 18.71 |  |  | FALSE | FALSE | 423 | 550 | 508 | 635 | {C05703C7-F4C2-4430-A142-CCE58AB99414}
5899 | 4313 | {9CA8A6DA-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | BRENTWOOD | Bank 2 | CB 2108 | PGE\WCL5 | 2016-12-28 13:46:34.1355159 -08:00 | 0145902108 | 013652205 | 22 | 3 | 3 | 1 | 578 | 20.8 | 20.59 | 578 | 20.8 | 20.59 | 689 | 24.8 | 24.55 | 689 | 24.8 | 24.55 | 627 | 22.57 | 22.34 | 627 | 22.57 | 22.34 | 732 | 26.35 | 26.09 | 732 | 26.35 | 26.09 |  |  | FALSE | FALSE | 1667 | 2167 | 2000 | 2500 | {E342058D-A6F9-46D5-A19F-3A9204FC42C3}
5901 | 4313 | {A2A9321F-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | BRENTWOOD | Bank 2 | CB 2109 | PGE\WCL5 | 2016-12-28 13:49:11.9179615 -08:00 | 0145902109 | 255451101 | 22 | 3 | 3 | 1 | 503 | 18.1 | 17.92 | 503 | 18.1 | 17.92 | 639 | 23 | 22.77 | 639 | 23 | 22.77 | 557 | 20.05 | 19.85 | 557 | 20.05 | 19.85 | 674 | 24.26 | 24.02 | 674 | 24.26 | 24.02 |  |  | FALSE | FALSE | 1667 | 2167 | 2000 | 2500 | {4DC6501A-C223-4781-B5AF-D0AE16D72977}
5903 | 4313 | {A2A93248-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | BRENTWOOD | Bank 2 | CB 2110 | PGE\WCL5 | 2016-12-28 13:52:33.2567239 -08:00 | 0145902110 | 255451102 | 22 | 3 | 3 | 1 | 503 | 18.1 | 17.92 | 503 | 18.1 | 17.92 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 | 557 | 20.05 | 19.85 | 557 | 20.05 | 19.85 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 |  |  | FALSE | FALSE | 1667 | 2167 | 2000 | 2500 | {40046078-3C61-43CA-B261-AB6BA96F9002}
5905 | 4313 | {A2A9324D-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | BRENTWOOD | Bank 2 | CB 2111 | PGE\WCL5 | 2016-12-28 14:07:43.1656543 -08:00 | 0145902111 | 255451103 | 22 | 3 | 3 | 1 | 578 | 20.8 | 20.59 | 578 | 20.8 | 20.59 | 689 | 24.8 | 24.55 | 689 | 24.8 | 24.55 | 600 | 21.6 | 21.38 | 600 | 21.6 | 21.38 | 732 | 26.35 | 26.09 | 732 | 26.35 | 26.09 | OH Disc's #21232 have 9 amps of wayload to be factored in: Summer Normal = 579A, Summer EMG = 795A, Winter Normal = 579A, Winter EMG = 795A. |  | FALSE | FALSE | 1667 | 2167 | 2000 | 2500 | {FADC7897-7992-42CD-B67F-91D9BA422031}
5910 | 4312 | {A4FD4474-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LOCKHEED NO.2 | Bank 1 | CB 1106 | PGE\MTTA | 2016-12-29 12:27:16.8976484 -08:00 | 0830001106 | 253461101 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {D1929A16-C1C9-44D7-8B2A-F76AB3E2475F}
5911 | 4312 | {A4FD447D-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LOCKHEED NO.2 | Bank 1 | CB 1107 | PGE\MTTA | 2016-12-29 12:33:56.0650832 -08:00 | 0830001107 | 253871104 | 8 | 3 | 3 | 2 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {CC8D35B6-9002-479E-8BA1-DFE04B861E5A}
5912 | 4312 | {A4FD4486-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LOCKHEED NO.2 | Bank 1 | CB 1108 | PGE\MTTA | 2016-12-29 12:35:26.0169896 -08:00 | 0830001108 | 254242103 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {879EC3CD-549C-499F-BF51-506206883311}
5913 | 4315 | {DD0642E0-671D-11E5-80CA-005056A729E5} | KERN | CARNERAS | Bank 1 | CB 1102 | PGE\EXVH | 2016-12-28 15:41:17.0287123 -08:00 | 2523201102 | 254242104 | 8 | 3 | 3 | 2 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 |  |  | TRUE | FALSE | 733 | 953 | 879 | 1099 | {09E6A49F-64B1-4140-92C5-A08241018EF2}
5915 | 4315 | {DD0642E6-671D-11E5-80CA-005056A729E5} | KERN | CARNERAS | Bank 1 | CB 1103 | PGE\EXVH | 2016-12-28 15:45:56.3988847 -08:00 | 2523201103 | 253141103 | 8 | 4 | 4 | 2 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {B5E2A81B-29A5-4C5B-B4D8-1B27ADD81CBC}
5916 | 2633 | {DD0643A4-671D-11E5-80CA-005056A729E5} | KERN | CUYAMA | Bank 2 | CB 2101 | PGE\BXYD | 2017-02-01 09:20:48.1151117 -08:00 | 2531402101 | 253141104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {34735687-CDBC-4828-A3CF-BF240A2BC492}
5919 | 4316 | {A4FD4499-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LOCKHEED NO.2 | Bank 2 | CB 1103 | PGE\MTTA | 2016-12-29 12:24:33.8890688 -08:00 | 0830001103 | 253142102 | 8 | 3 | 3 | 2 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 948 | 20.69 | 20.48 | 900 | 19.64 | 19.44 | 879 | 19.18 | 18.99 | 879 | 19.18 | 18.99 | 1000 | 21.82 | 21.6 | 987 | 21.54 | 21.32 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {11C70524-AD0E-458E-B96A-62BF521AFD33}
5920 | 4317 | {DD0643CB-671D-11E5-80CA-005056A729E5} | KERN | FAMOSO | Bank 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\EXVH | 2016-12-29 10:18:56.8274181 -08:00 | 2524601101 | 253391101 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {D483B60B-9A39-43E8-BEE9-4DBE70C03880}
5921 | 4317 | {DD0643D1-671D-11E5-80CA-005056A729E5} | KERN | FAMOSO | Bank 1 (Non SCADA) | CB 1102 (Non-SCADA) | PGE\EXVH | 2016-12-29 10:25:12.2174370 -08:00 | 2524601102 | 253391103 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {CB4015C8-545E-4C0C-9C53-4EF5DF947899}
5922 | 4317 | {DD0643D4-671D-11E5-80CA-005056A729E5} | KERN | FAMOSO | Bank 1 (Non SCADA) | CB 1103 (Non-SCADA) | PGE\EXVH | 2016-12-29 10:49:35.7283809 -08:00 | 2524601103 | 253391105 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {AC2109D9-6233-4A49-8E99-7786CE08917B}
5924 | 4317 | {DD0643DD-671D-11E5-80CA-005056A729E5} | KERN | FAMOSO | Bank 1 (Non SCADA) | CB 1105 (Non-SCADA) | PGE\EXVH | 2016-12-29 11:13:51.6887796 -08:00 | 2524601105 | 254541103 | 8 | 3 | 3 | 2 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 |  |  | FALSE | FALSE | 1272 | 1490 | 1649 | 2061 | {1FF6B667-17B1-4928-B36B-51376DF77D63}
5925 | 4317 | {DD0643E0-671D-11E5-80CA-005056A729E5} | KERN | FAMOSO | Bank 1 (Non SCADA) | CB 1107 (Non-SCADA) | PGE\EXVH | 2016-12-29 13:03:40.0074756 -08:00 | 2524601107 | 254541104 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {193EE6AE-32FC-4948-B80D-99DD112F2A9B}
5926 | 4319 | {C511400A-671D-11E5-80CA-005056A729E5} | FRESNO | GIFFEN | Bank 1 | CB 1102 | PGE\SJJ8 | 2016-12-30 14:12:05.2048901 -08:00 | 2531501102 | 252261105 | 8 | 4 | 4 | 1 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1200 | {5C172C49-CF93-4243-9DEC-DC43FFD4D79C}
5928 | 4319 | {C5114015-671D-11E5-80CA-005056A729E5} | FRESNO | GIFFEN | Bank 1 | CB 1103 | PGE\BXYD | 2017-01-24 09:30:46.3103043 -08:00 | 2531501103 | 252261104 | 8 | 4 | 4 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1200 | {C62E840D-7F6C-4652-8BD5-01AE721984E7}
5929 | 4319 | {C5114020-671D-11E5-80CA-005056A729E5} | FRESNO | GIFFEN | Bank 1 | CB 1106 | PGE\BXYD | 2017-01-24 09:32:16.8376846 -08:00 | 2531501106 | 083871101 | 8 | 1 | 1 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1200 | {87F0F9C3-C7DD-4920-9B5B-60D1BF758519}
5930 | 4319 | {C5114025-671D-11E5-80CA-005056A729E5} | FRESNO | GIFFEN | Bank 1 | CB 1107 | PGE\BXYD | 2017-01-24 09:36:12.1183928 -08:00 | 2531501107 | 083871109 | 8 | 4 | 4 | 1 | 591 | 12.9 | 12.77 | 591 | 12.9 | 12.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1200 | {A2EE26AF-29BD-493C-AC9F-D7D98935D566}
5932 | 1232 | {B134AF8D-2758-11E6-B38D-D4BED91EFF1A} | FRESNO | SHEPHERD | Bank 3 | CB 2109 | PGE\BXYD | 2017-01-03 14:56:04.3133454 -08:00 | 2520602109 | 083871110 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {30D98714-B09A-4885-B993-DBB3D56AC7B9}
5933 | 4320 | {CDB1044D-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CONTRA COSTA | Bank 4 | CB 2203 | PGE\WCL5 | 2017-01-04 16:46:17.9607829 -08:00 | 0136502203 | 083871111 | 22 | 3 | 3 | 1 | 700 | 25.19 | 24.94 | 700 | 25.19 | 24.94 | 700 | 25.19 | 24.94 | 700 | 25.19 | 24.94 | 700 | 25.19 | 24.94 | 700 | 25.19 | 24.94 | 700 | 25.19 | 24.94 | 700 | 25.19 | 24.94 |  |  | FALSE | FALSE | 1175 | 1527 | 1410 | 1762 | {8F86F5A3-E175-44C7-B493-5B576A136962}
5935 | 4320 | {D414BDF6-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CONTRA COSTA | Bank 4 | CB 2204 | PGE\WCL5 | 2017-01-04 17:13:03.2004523 -08:00 | 0136502204 | 013652114 | 22 | 3 | 3 | 1 | 503 | 18.1 | 17.92 | 489 | 17.6 | 17.42 | 578 | 20.8 | 20.59 | 549 | 19.76 | 19.56 | 557 | 20.05 | 19.85 | 557 | 20.05 | 19.85 | 600 | 21.6 | 21.38 | 570 | 20.52 | 20.31 |  |  | FALSE | FALSE | 1175 | 1527 | 1410 | 1762 | {A096F333-CC4E-44EE-B9C9-1EDC904C545C}
5938 | 4320 | {D414BE02-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CONTRA COSTA | Bank 4 | CB 2205 | PGE\WCL5 | 2017-01-04 17:05:13.7874253 -08:00 | 0136502205 | 013652115 | 22 | 3 | 3 | 1 | 600 | 21.6 | 21.38 | 570 | 20.52 | 20.31 | 600 | 21.6 | 21.38 | 570 | 20.52 | 20.31 | 600 | 21.6 | 21.38 | 570 | 20.52 | 20.31 | 600 | 21.6 | 21.38 | 570 | 20.52 | 20.31 |  |  | FALSE | FALSE | 1175 | 1527 | 1410 | 1762 | {FAF6DB8A-93B6-4AA9-8444-1DF0CF19084A}
5943 | 4324 | {DD0642C4-671D-11E5-80CA-005056A729E5} | KERN | CAL WATER | Bank 1 | CB 1101 | PGE\BXYD | 2017-01-06 11:17:21.7986290 -08:00 | 2554501101 | 013652116 | 8 | 3 | 3 | 1 | 661 | 14.43 | 14.29 | 661 | 14.43 | 14.29 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2000 | {D9E9970F-A003-4EA3-B50B-1FF1346AA0A6}
5944 | 4324 | {DD0642C9-671D-11E5-80CA-005056A729E5} | KERN | CAL WATER | Bank 1 | CB 1102 | PGE\BXYD | 2017-01-20 15:21:59.0817818 -08:00 | 2554501102 | 024012101 | 8 | 3 | 3 | 1 | 636 | 13.88 | 13.74 | 636 | 13.88 | 13.74 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2000 | {46154F9B-CA80-4C91-B519-5618246ADA92}
5945 | 4324 | {2717D549-A5BE-11E5-A1F0-D4BED91EFF1A} | KERN | CAL WATER | Bank 1 | CB 1103 | PGE\BXYD | 2017-01-06 11:21:40.5106874 -08:00 | 255451103 | 024012102 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2000 | {AB1D185E-E0DE-4156-A41A-A01CC4CA55C5}
5946 | 4325 | {DD0642F8-671D-11E5-80CA-005056A729E5} | KERN | CARRIZO PLAINS | Bank 1 (Non SCADA) | CB 1101 | PGE\BXYD | 2017-02-02 15:04:12.9159702 -08:00 | 253461101 | 024012103 | 8 | 4 | 4 | 1 | 91 | 1.99 | 1.97 | 91 | 1.99 | 1.97 | 119 | 2.6 | 2.57 | 119 | 2.6 | 2.57 | 109 | 2.38 | 2.36 | 109 | 2.38 | 2.36 | 137 | 2.99 | 2.96 | 137 | 2.99 | 2.96 |  |  | FALSE | FALSE | 91 | 119 | 109 | 137 | {00000000-0000-0000-0000-000000000000}
5947 | 4326 | {DD06437B-671D-11E5-80CA-005056A729E5} | KERN | COPUS | Bank 2 | CB 1104 | PGE\BXYD | 2017-01-06 12:50:09.1467169 -08:00 | 2538701104 | 024011107 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 842 | 842 | 842 | {D20ADFA9-9BB4-42DB-9BCA-29DD568ED5B0}
5948 | 4327 | {DD0643EC-671D-11E5-80CA-005056A729E5} | KERN | FELLOWS | Bank 1 (Non SCADA) | CB 2103 (Non-SCADA) | PGE\BXYD | 2017-01-06 13:33:33.7550130 -08:00 | 2542402103 | 024011108 | 12 | 3 | 3 | 1 | 745 | 28.16 | 27.88 | 707 | 26.72 | 26.45 | 800 | 30.23 | 29.93 | 796 | 30.08 | 29.78 | 800 | 30.23 | 29.93 | 760 | 28.72 | 28.43 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {99B23D34-83C0-4AC9-9A41-2E39A3BD3EF5}
5949 | 4328 | {DD0643F8-671D-11E5-80CA-005056A729E5} | KERN | FELLOWS | Bank 2 (Non SCADA) | CB 2104 (Non-SCADA) | PGE\BXYD | 2017-01-06 13:40:15.4419879 -08:00 | 2542402104 | 024011102 | 12 | 4 | 4 | 1 | 745 | 28.16 | 27.88 | 707 | 26.72 | 26.45 | 800 | 30.23 | 29.93 | 796 | 30.08 | 29.78 | 800 | 30.23 | 29.93 | 760 | 28.72 | 28.43 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {E2CEC4B8-1CBE-4581-A8BA-C6A1B4F05D6B}
5950 | 4329 | {DD06438F-671D-11E5-80CA-005056A729E5} | KERN | CUYAMA | Bank 1 | CB 1103 | PGE\BXYD | 2017-01-06 13:53:21.7026280 -08:00 | 2531401103 | 024011103 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {15AEBA18-7DD5-4C0A-BCF4-1B34604AF6BC}
5951 | 4329 | {DD064395-671D-11E5-80CA-005056A729E5} | KERN | CUYAMA | Bank 1 | CB 1104 | PGE\BXYD | 2017-01-06 13:55:39.4515110 -08:00 | 2531401104 | 024011104 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {D16BF3BA-0D54-46B7-9939-C630C70EF0D6}
5952 | 4329 | {DD064398-671D-11E5-80CA-005056A729E5} | KERN | CUYAMA | Bank 1 | CB 2102 | PGE\BXYD | 2017-01-06 14:02:23.6501020 -08:00 | 2531402102 | 024011105 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {97CB9B57-3391-4195-BD21-BE7004FA1F33}
5953 | 4330 | {E300587D-671D-11E5-80CA-005056A729E5} | KERN | FRUITVALE | Bank 1 | CB 1101 | PGE\BXYD | 2017-01-06 15:10:52.0612378 -08:00 | 2533901101 | 024011106 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 634 | 13.84 | 13.7 | 632 | 13.79 | 13.65 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {85DDB584-2555-42C1-845B-17CC919F096E}
5954 | 4330 | {E3005882-671D-11E5-80CA-005056A729E5} | KERN | FRUITVALE | Bank 1 | CB 1103 | PGE\BXYD | 2017-01-06 15:05:38.1716257 -08:00 | 2533901103 | 153082106 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 666 | 14.53 | 14.38 | 632 | 13.79 | 13.65 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {2FF22ED4-6EF3-47F3-B47E-0503AEBD50C9}
5955 | 4330 | {E300588D-671D-11E5-80CA-005056A729E5} | KERN | FRUITVALE | Bank 1 | CB 1105 | PGE\BXYD | 2017-01-06 15:10:16.5710103 -08:00 | 2533901105 | 024012104 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 634 | 13.84 | 13.7 | 634 | 13.84 | 13.7 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {7738BFEA-6C7B-4633-B182-3C8A1266F9C4}
5956 | 4331 | {E30058BD-671D-11E5-80CA-005056A729E5} | KERN | GANSO | Bank 1 | CB 1103 | PGE\BXYD | 2017-01-06 15:18:33.8709981 -08:00 | 2545401103 | 024012105 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 489 | 10.67 | 10.56 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {F747FB96-3960-4F58-A0A6-2C6CD8922BB3}
5957 | 4331 | {E30058C6-671D-11E5-80CA-005056A729E5} | KERN | GANSO | Bank 1 | CB 1104 | PGE\BXYD | 2017-01-06 15:22:53.5814629 -08:00 | 2545401104 | 153081109 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {87F3EB4E-3668-42EA-8DC8-FCB1535BA8A7}
5958 | 2296 | {58406CBC-671D-11E5-80CA-005056A729E5} | YOSEMITE | LIVINGSTON | Bank 1 | CB 1105 | PGE\BXYD | 2017-01-10 09:46:14.7575163 -08:00 | 2522601105 | 153081110 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1200 | 1200 | 1200 | 1200 | {0B28A2C3-6BF5-4941-9E1F-2DD611774F22}
5959 | 2296 | {58406CB3-671D-11E5-80CA-005056A729E5} | YOSEMITE | LIVINGSTON | Bank 1 | CB 1104 | PGE\BXYD | 2017-01-10 12:50:45.0722114 -08:00 | 2522601104 | 153081111 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 700 | 15.28 | 15.13 | 665 | 14.51 | 14.36 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 700 | 15.28 | 15.13 | 665 | 14.51 | 14.36 |  |  | FALSE | FALSE | 1200 | 1200 | 1200 | 1200 | {30E94921-C47E-4DCC-952D-04487377E2D1}
5960 | 4333 | {DC00D1FD-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | FMC | Bank 1 | CB 1101 (Non-SCADA) | PGE\ALWK | 2017-01-11 10:24:20.0903136 -08:00 | 0838701101 | 153081112 | 7 | 3 | 3 | 2 | 925 | 19.98 | 19.78 | 925 | 19.98 | 19.78 | 1000 | 21.6 | 21.38 | 1000 | 21.6 | 21.38 | 1000 | 21.6 | 21.38 | 1000 | 21.6 | 21.38 | 1000 | 21.6 | 21.38 | 1000 | 21.6 | 21.38 |  |  | FALSE | FALSE | 925 | 1203 | 1111 | 1388 | {F6581C75-3410-4EB1-AE4F-CB04FD0F9A22}
5961 | 4334 | {DC00D23B-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | FMC | Bank 3 | CB 1109 | PGE\ALWK | 2017-01-11 10:35:34.1168754 -08:00 | 0838701109 | 024020401 | 7 | 3 | 3 | 2 | 582 | 12.57 | 12.44 | 582 | 12.57 | 12.44 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {5710827F-736F-4F38-8A30-D02AAB864335}
5963 | 4334 | {DC00D244-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | FMC | Bank 3 | CB 1110 | PGE\ALWK | 2017-01-11 11:00:01.7051941 -08:00 | 0838701110 | 024020402 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 |  |  | TRUE | FALSE | 1388 | 1805 | 1666 | 2083 | {8D33C46F-699B-42D4-8E4F-784931D4FD53}
5964 | 4334 | {DC00D254-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | FMC | Bank 3 | CB 1111 | PGE\ALWK | 2017-01-11 11:46:02.5901272 -08:00 | 0838701111 | 024020403 | 7 | 3 | 3 | 2 | 524 | 11.32 | 11.21 | 497 | 10.73 | 10.62 | 591 | 12.76 | 12.63 | 561 | 12.12 | 12 | 599 | 12.94 | 12.81 | 569 | 12.29 | 12.17 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {5FEE606A-0512-43CE-8636-36329B863D7D}
5966 | 4335 | {C7A136A4-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CONTRA COSTA | Bank 10 | CB 2114 | PGE\WCL5 | 2017-01-12 10:32:02.0034971 -08:00 | 0136502114 | 024020404 | 22 | 3 | 3 | 1 | 503 | 18.1 | 17.92 | 503 | 18.1 | 17.92 | 639 | 23 | 22.77 | 639 | 23 | 22.77 | 557 | 20.05 | 19.85 | 557 | 20.05 | 19.85 | 674 | 24.26 | 24.02 | 674 | 24.26 | 24.02 |  |  | FALSE | FALSE | 1667 | 2167 | 2000 | 2500 | {96D50121-106E-427A-8A17-AF8390E5ACD3}
5969 | 4335 | {CDB1040E-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CONTRA COSTA | Bank 10 | CB 2115 | PGE\WCL5 | 2017-01-12 10:42:29.9935736 -08:00 | 0136502115 | 024020405 | 22 | 3 | 3 | 1 | 503 | 18.1 | 17.92 | 489 | 17.6 | 17.42 | 578 | 20.8 | 20.59 | 549 | 19.76 | 19.56 | 557 | 20.05 | 19.85 | 557 | 20.05 | 19.85 | 674 | 24.26 | 24.02 | 674 | 24.26 | 24.02 |  |  | FALSE | FALSE | 1667 | 2167 | 2000 | 2500 | {894164F0-5E2C-4B0B-AB1E-8206F0328ACC}
5971 | 4335 | {CDB1041D-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CONTRA COSTA | Bank 10 | CB 2116 | PGE\WCL5 | 2017-01-12 10:47:17.8191086 -08:00 | 0136502116 | 024020406 | 22 | 3 | 3 | 1 | 578 | 20.8 | 20.59 | 578 | 20.8 | 20.59 | 689 | 24.8 | 24.55 | 689 | 24.8 | 24.55 | 627 | 22.57 | 22.34 | 627 | 22.57 | 22.34 | 732 | 26.35 | 26.09 | 732 | 26.35 | 26.09 |  |  | FALSE | FALSE | 1667 | 2167 | 2000 | 2500 | {1AC2F248-D6A0-4948-A1F8-17ADA27FCDAA}
5975 | 2660 | {13EDBCBB-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BAY MEADOWS | Bank 1 | CB 2101 | PGE\C7CF | 2017-01-12 12:26:54.0756344 -08:00 | 0240102101 | 024020407 | 12 | 3 | 3 | 2 | 481 | 18.18 | 18 | 481 | 18.18 | 18 | 592 | 22.37 | 22.15 | 592 | 22.37 | 22.15 | 495 | 18.71 | 18.52 | 495 | 18.71 | 18.52 | 599 | 22.64 | 22.41 | 599 | 22.64 | 22.41 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {8B8CDB3B-72D1-4D1C-A715-CFBE98795CB3}
5976 | 2660 | {13EDBCEE-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BAY MEADOWS | Bank 1 | CB 2102 | PGE\C7CF | 2017-01-12 12:31:10.7629706 -08:00 | 0240102102 | 024020408 | 12 | 3 | 3 | 2 | 545 | 20.6 | 20.39 | 545 | 20.6 | 20.39 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 556 | 21.01 | 20.8 | 556 | 21.01 | 20.8 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {6C842010-4350-43FE-B6B6-A44B3195677B}
5977 | 2660 | {13EDBD36-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BAY MEADOWS | Bank 1 | CB 2103 | PGE\C7CF | 2017-01-12 13:40:17.0887061 -08:00 | 0240102103 | 024020409 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {5916083B-95B5-44DE-98B8-290C68E51BE5}
5978 | 4337 | {13EDBD49-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BAY MEADOWS | Bank 2 | CB 1107 | PGE\C7CF | 2017-01-12 13:46:42.2601131 -08:00 | 0240101107 | 024021103 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {EEE0344C-B0D7-4E6E-83D5-23BBC1B51054}
5979 | 4337 | {13EDBD59-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BAY MEADOWS | Bank 2 | CB 1108 | PGE\C7CF | 2017-01-12 13:56:34.3694996 -08:00 | 0240101108 | 024021104 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {36774C84-DED7-47FB-AAA8-EB380A747BDD}
5981 | 4338 | {13EDBD6C-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BAY MEADOWS | Bank 3 | CB 1102 | PGE\C7CF | 2017-01-12 14:03:05.2818170 -08:00 | 0240101102 | 024021101 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {D490F14A-0387-4AAF-B8E8-E15986320CEC}
5982 | 4338 | {13EDBD75-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BAY MEADOWS | Bank 3 | CB 1103 | PGE\C7CF | 2017-01-12 14:07:47.6940479 -08:00 | 0240101103 | 024021102 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {12445855-2884-41EB-B9AA-82B379612679}
5983 | 4338 | {13EDBD8C-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BAY MEADOWS | Bank 3 | CB 1104 | PGE\C7CF | 2017-01-12 14:15:01.0484429 -08:00 | 0240101104 | 024021105 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {0F37CAD3-0EE1-4C6D-947C-F255490C0DFE}
5984 | 4338 | {13EDBDC6-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BAY MEADOWS | Bank 3 | CB 1105 | PGE\C7CF | 2017-01-12 14:19:15.2639418 -08:00 | 0240101105 | 024021106 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {678010D5-A310-437D-AC69-5C2F470EEE68}
5985 | 4338 | {13EDBDD6-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BAY MEADOWS | Bank 3 | CB 1106 | PGE\C7CF | 2017-01-12 14:24:24.6906218 -08:00 | 0240101106 | 024021107 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {3514D449-9353-4825-96EB-98634D5A523D}
5986 | 4339 | {A7233148-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PLACERVILLE | Bank 2 | CB 2106 | PGE\JSKe | 2017-01-12 14:31:11.7500534 -08:00 | 1530802106 | 024031101 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 345 | 13.04 | 12.91 | 533 | 20.14 | 19.94 | 386 | 14.59 | 14.44 | 533 | 20.14 | 19.94 | 443 | 16.74 | 16.57 | 533 | 20.14 | 19.94 | 473 | 17.88 | 17.7 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {ABFDC3D6-4224-41B9-9706-6F600BD772B0}
5987 | 4341 | {13EDBDF0-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BAY MEADOWS | Bank 5 | CB 2104 | PGE\C7CF | 2017-01-12 14:33:20.8443105 -08:00 | 0240102104 | 024031102 | 12 | 3 | 3 | 2 | 545 | 20.6 | 20.39 | 545 | 20.6 | 20.39 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 556 | 21.01 | 20.8 | 556 | 21.01 | 20.8 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {264D66D5-27EC-4F88-809E-0DD76F1239DD}
5988 | 4341 | {13EDBDF9-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BAY MEADOWS | Bank 5 | CB 2105 | PGE\C7CF | 2017-01-12 14:35:24.3378685 -08:00 | 0240102105 | 024031103 | 12 | 3 | 3 | 2 | 545 | 20.6 | 20.39 | 545 | 20.6 | 20.39 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 556 | 21.01 | 20.8 | 556 | 21.01 | 20.8 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {A095DD9E-DB4D-4D88-98FA-4B3A873559D6}
5989 | 4342 | {A72331BD-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PLACERVILLE | Bank 3 | CB 1109 | PGE\JSKe | 2017-01-12 14:44:02.0501519 -08:00 | 1530801109 | 024031104 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {1BF69195-F862-4FD2-9588-F7DEE171012E}
5990 | 4342 | {A72331C6-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PLACERVILLE | Bank 3 | CB 1110 | PGE\JSKe | 2017-01-12 14:43:50.5059299 -08:00 | 1530801110 | 024031105 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {920A512D-AD3E-430B-8AD2-C4F22F84083E}
5991 | 4342 | {A72331DD-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PLACERVILLE | Bank 3 | CB 1111 | PGE\JSKe | 2017-01-12 14:43:32.6591867 -08:00 | 1530801111 | 024031106 | 8 | 4 | 4 | 2 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {ABBBAD02-BA27-44E6-875E-0F37AC9F4469}
5992 | 4342 | {A72331E6-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PLACERVILLE | Bank 3 | CB 1112 | PGE\JSKe | 2017-01-12 14:47:04.4332592 -08:00 | 1530801112 | 024031107 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 593 | 12.94 | 12.81 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {9129DBBB-8427-4065-A5A6-C335809C9F58}
5994 | 4343 | {DC7BD3C9-FDD3-11E5-9D37-D4BED91EFF1A} | PENINSULA | BELLEHAVEN | Bank 1 | CB 401 (Non-SCADA) | PGE\C7CF | 2017-06-08 16:09:02.4626690 -07:00 | 02402401 | 024031108 | 4 | 3 | 3 | 2 | 365 | 2.76 | 2.73 | 365 | 2.76 | 2.73 | 394 | 2.98 | 2.95 | 394 | 2.98 | 2.95 | 376 | 2.85 | 2.82 | 376 | 2.85 | 2.82 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 990 | 1288 | 1189 | 1486 | {587AFCDF-A675-471C-9C27-03C881E86274}
5995 | 4343 | {13EDBE12-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELLEHAVEN | Bank 1 | CB 402 | PGE\C7CF | 2017-01-12 15:04:31.2289895 -08:00 | 024020402 | 024031109 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 3 single-phase 100/112kVA, 400/448A, 2.5kV, +/-10% regs |  | FALSE | FALSE | 990 | 1288 | 1189 | 1486 | {D63D9B93-BDCE-4AD1-9369-895E2B4E222D}
5996 | 4343 | {E277B8B9-FDD3-11E5-9D37-D4BED91EFF1A} | PENINSULA | BELLEHAVEN | Bank 1 | CB 403 (Non-SCADA) | PGE\C7CF | 2017-06-08 16:15:36.1412865 -07:00 | 02402403 | 024031110 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 990 | 1288 | 1189 | 1486 | {032E542E-9D9E-4E4C-B9A7-198CA4B64AC7}
5997 | 4343 | {E277B8BC-FDD3-11E5-9D37-D4BED91EFF1A} | PENINSULA | BELLEHAVEN | Bank 1 | CB 404 (Non-SCADA) | PGE\C7CF | 2017-06-08 16:16:33.9723400 -07:00 | 024020404 | 024031111 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 990 | 1288 | 1189 | 1486 | {9DD1FC49-2D66-43AB-B8E9-971B784663A2}
5998 | 4344 | {13EDBE2B-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELLEHAVEN | Bank 2 | CB 405 | PGE\C7CF | 2017-01-12 15:21:49.8345623 -08:00 | 024020405 | 024040401 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 3 single-phase 100/112kVA, 400/448A, 2.5kV, +/-10% regs |  | FALSE | FALSE | 990 | 1288 | 1189 | 1486 | {988D5A4A-4405-42DF-A1F4-EA265FD5F1EE}
5999 | 4344 | {E896BCC0-FDD3-11E5-9D37-D4BED91EFF1A} | PENINSULA | BELLEHAVEN | Bank 2 | CB 406 (Non-SCADA) | PGE\C7CF | 2017-06-08 16:18:16.4988260 -07:00 | 024020406 | 024040402 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 380 | 2.88 | 2.85 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 |  |  | FALSE | FALSE | 990 | 1288 | 1189 | 1486 | {AEE2DF6F-B888-4B55-8185-D8EEFAB9DBC1}
6000 | 4344 | {E896BCC3-FDD3-11E5-9D37-D4BED91EFF1A} | PENINSULA | BELLEHAVEN | Bank 2 | CB 407 (Non-SCADA) | PGE\C7CF | 2017-06-08 16:19:55.3903955 -07:00 | 024020407 | 024040403 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 3-1 phase regs 100/112kVA 400/448A 2.5/4.33kV |  | FALSE | FALSE | 990 | 1288 | 1189 | 1486 | {2F4FEDB5-BDF5-40B1-ADD8-0D25E931DBEE}
6001 | 4344 | {EF7F5169-FDD3-11E5-9D37-D4BED91EFF1A} | PENINSULA | BELLEHAVEN | Bank 2 | CB 408 (Non-SCADA) | PGE\C7CF | 2017-01-12 15:44:51.8495390 -08:00 | 024020408 | 024040404 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 285 | 2.16 | 2.14 | 390 | 2.95 | 2.92 | 370 | 2.8 | 2.77 | 360 | 2.72 | 2.69 | 342 | 2.59 | 2.56 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 990 | 1288 | 1189 | 1486 | {8A59E0FB-9405-4CAE-8D8A-5E3128D9E620}
6002 | 4344 | {EF7F516C-FDD3-11E5-9D37-D4BED91EFF1A} | PENINSULA | BELLEHAVEN | Bank 2 | CB 409 (Non-SCADA) | PGE\C7CF | 2017-06-08 16:22:55.8725800 -07:00 | 02402409 | 024040405 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 3-1p regs 100/112kVA 400/448A 2.5/4.33kV |  | FALSE | FALSE | 990 | 1288 | 1189 | 1486 | {037C93A2-5840-4B61-AF2D-EFD41C28755D}
6003 | 4345 | {13EDBE4A-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELLEHAVEN | Bank 3 | CB 1103 | PGE\C7CF | 2017-01-12 16:19:12.2123606 -08:00 | 0240201103 | 253391106 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {92DC1108-1D59-4F4C-9053-98F7FB15FDD9}
6004 | 4345 | {13EDBE61-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELLEHAVEN | Bank 3 | CB 1104 | PGE\C7CF | 2017-01-12 16:22:02.9420438 -08:00 | 0240201104 | 253391104 | 8 | 3 | 3 | 2 | 560 | 12.22 | 12.1 | 552 | 12.05 | 11.93 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 577 | 12.59 | 12.46 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {05A85290-BC86-4404-9E42-BD725D68AADB}
6005 | 4346 | {13EDBE7B-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELLEHAVEN | Bank 4 | CB 1101 | PGE\C7CF | 2017-01-12 16:33:40.3378550 -08:00 | 0240201101 | 253392108 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 577 | 12.59 | 12.46 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {1571C33C-B923-487E-BB7E-FDE7F4020658}
6006 | 4346 | {13EDBE8B-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELLEHAVEN | Bank 4 | CB 1102 | PGE\C7CF | 2017-01-12 16:43:18.5473742 -08:00 | 0240201102 | 013652106 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 528 | 11.52 | 11.4 | 528 | 11.52 | 11.4 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {E460415A-E0CB-455D-9B67-EDF8007D3CB7}
6007 | 4347 | {13EDBE9E-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELLEHAVEN | Bank 5 | CB 1105 | PGE\C7CF | 2017-01-12 16:54:37.0980230 -08:00 | 0240201105 | 013652107 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {42538026-DEFE-45AA-B1D0-C3BFB2CA85AA}
6008 | 4347 | {13EDBED1-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELLEHAVEN | Bank 5 | CB 1106 | PGE\C7CF | 2017-01-12 16:59:01.5543086 -08:00 | 0240201106 | 013652108 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {3D06A7B1-57B7-4BA9-A46F-47385744B4E8}
6009 | 4347 | {13EDBEF7-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELLEHAVEN | Bank 5 | CB 1107 | PGE\C7CF | 2017-01-12 17:10:48.9499121 -08:00 | 0240201107 | 013652110 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {99990E1E-15D0-4365-AEE1-295652374C44}
6010 | 4348 | {13EDBF06-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELMONT | Bank 1 | CB 1101 | PGE\C7CF | 2017-01-12 17:26:06.4035551 -08:00 | 0240301101 | 082160403 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {0E4BD28E-6E02-43B7-B662-020C5FCDD261}
6011 | 4348 | {13EDBF0F-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELMONT | Bank 1 | CB 1102 | PGE\C7CF | 2017-01-12 17:32:34.4610176 -08:00 | 0240301102 | 082161101 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {0042B7F9-C244-4CC6-9F2B-690E58E29055}
6012 | 4348 | {13EDBF34-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELMONT | Bank 1 | CB 1103 | PGE\C7CF | 2017-01-12 17:39:53.5470614 -08:00 | 0240301103 | 252951108 | 8 | 3 | 3 | 2 | 490 | 10.69 | 10.58 | 490 | 10.69 | 10.58 | 549 | 11.98 | 11.86 | 549 | 11.98 | 11.86 | 505 | 11.02 | 10.91 | 505 | 11.02 | 10.91 | 565 | 12.33 | 12.21 | 565 | 12.33 | 12.21 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {56194881-59DE-4A4B-B627-A40BAE8343F9}
6013 | 4348 | {13EDBF52-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELMONT | Bank 1 | CB 1104 | PGE\C7CF | 2017-01-12 17:45:42.4945718 -08:00 | 0240301104 | 082161102 | 8 | 3 | 3 | 2 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 527 | 11.5 | 11.39 | 527 | 11.5 | 11.39 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {D00A2E5D-3BD6-4545-B4D1-E3466BF18DB6}
6015 | 4349 | {13EDBF65-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELMONT | Bank 2 | CB 1105 | PGE\C7CF | 2017-01-12 17:54:14.2156124 -08:00 | 0240301105 | 255292107 | 8 | 3 | 3 | 2 | 505 | 11.02 | 10.91 | 505 | 11.02 | 10.91 | 586 | 12.79 | 12.66 | 586 | 12.79 | 12.66 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {CA114249-B712-4E90-AABA-8C3F913DBADA}
6016 | 4349 | {13EDBF6E-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELMONT | Bank 2 | CB 1106 | PGE\C7CF | 2017-01-12 17:57:29.0789597 -08:00 | 0240301106 | 255292108 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {3A3BDBBA-777E-45E4-8672-2AA7805213C1}
6017 | 4350 | {13EDBF81-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELMONT | Bank 3 | CB 1107 | PGE\C7CF | 2017-01-13 08:38:01.7154897 -08:00 | 0240301107 | 255292109 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {FA8205B2-92C5-4156-B1AF-D779077878DA}
6018 | 4350 | {13EDBF8A-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELMONT | Bank 3 | CB 1108 | PGE\C7CF | 2017-01-13 08:40:15.6187430 -08:00 | 0240301108 | 254531106 | 8 | 3 | 3 | 2 | 446 | 9.73 | 9.63 | 446 | 9.73 | 9.63 | 549 | 11.98 | 11.86 | 549 | 11.98 | 11.86 | 459 | 10.02 | 9.92 | 459 | 10.02 | 9.92 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {588969AC-7F94-4940-8ADC-15CD110D968B}
6019 | 4350 | {13EDBF93-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELMONT | Bank 3 | CB 1109 | PGE\C7CF | 2017-01-13 08:43:08.1167886 -08:00 | 0240301109 | 254531107 | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 556 | 12.13 | 12.01 | 556 | 12.13 | 12.01 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {FC4B2CE3-E572-456E-B1AE-3D9C07DD64AB}
6020 | 4350 | {13EDBF9C-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELMONT | Bank 3 | CB 1110 | PGE\C7CF | 2017-01-13 08:45:43.1083135 -08:00 | 0240301110 | 152251101 | 8 | 3 | 3 | 2 | 505 | 11.02 | 10.91 | 505 | 11.02 | 10.91 | 586 | 12.79 | 12.66 | 570 | 12.44 | 12.32 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 598 | 13.05 | 12.92 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {475BD993-F767-470C-9ED1-63DB78EDB364}
6021 | 4350 | {13EDBFC8-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BELMONT | Bank 3 | CB 1111 | PGE\C7CF | 2017-01-13 08:47:55.5097570 -08:00 | 0240301111 | 103211101 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {30ABBC97-76BD-4A6F-947E-2493D257D17B}
6030 | 4353 | {13EDBFF7-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BERESFORD | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2017-01-17 17:19:20.0568016 -08:00 | 02404401 | 254531108 | 4 | 3 | 3 | 2 | 368 | 2.79 | 2.76 | 368 | 2.79 | 2.76 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 379 | 2.87 | 2.84 | 379 | 2.87 | 2.84 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 |  |  | FALSE | FALSE | 660 | 858 | 792 | 990 | {0FFFB9C6-C1D5-4E57-BB82-4A6E29D0BAA9}
6031 | 4353 | {13EDBFFA-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BERESFORD | Bank 1 (Non SCADA) | CB 402 (Non-SCADA) | PGE\C7CF | 2017-01-17 17:26:49.8076846 -08:00 | 02404402 | 103211102 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 |  |  | FALSE | FALSE | 660 | 858 | 792 | 990 | {25200746-4E69-4EB1-ABCC-AC77D246A208}
6032 | 4353 | {13EDBFFD-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BERESFORD | Bank 1 (Non SCADA) | CB 403 (Non-SCADA) | PGE\C7CF | 2017-01-17 17:34:18.8397474 -08:00 | 02404403 | 152591101 | 4 | 3 | 3 | 2 | 368 | 2.79 | 2.76 | 368 | 2.79 | 2.76 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 379 | 2.87 | 2.84 | 379 | 2.87 | 2.84 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 |  |  | FALSE | FALSE | 660 | 858 | 792 | 990 | {8FCDF51B-8729-4502-AFE2-D4D71C5A024F}
6033 | 4354 | {13EDC003-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BERESFORD | Bank 2 | CB 404 (Non-SCADA) | PGE\C7CF | 2017-01-17 17:40:10.4549091 -08:00 | 024040404 | 152591102 | 4 | 3 | 3 | 2 | 356 | 2.69 | 2.66 | 356 | 2.69 | 2.66 | 392 | 2.97 | 2.94 | 392 | 2.97 | 2.94 | 367 | 2.78 | 2.75 | 367 | 2.78 | 2.75 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 521 | 678 | 626 | 782 | {96FF8679-1339-4947-A042-2D9F85E95793}
6034 | 4354 | {13EDC00D-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BERESFORD | Bank 2 | CB 405 (Non-SCADA) | PGE\C7CF | 2017-01-17 17:42:09.5007984 -08:00 | 02404405 | 103241102 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 521 | 678 | 626 | 782 | {D4CE976D-6A03-49FB-AE5E-CCDD999ACEC4}
6035 | 4184 | {E30058A9-671D-11E5-80CA-005056A729E5} | KERN | FRUITVALE | Bank 2 | CB 1106 | PGE\BXYD | 2017-01-18 14:21:00.5583026 -08:00 | 2533901106 | 103241103 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 634 | 13.84 | 13.7 | 634 | 13.84 | 13.7 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {A3904071-3517-4A41-AE02-DEE14F3C3A68}
6036 | 4184 | {E3005898-671D-11E5-80CA-005056A729E5} | KERN | FRUITVALE | Bank 2 | CB 1104 | PGE\BXYD | 2017-01-18 14:11:41.8179578 -08:00 | 2533901104 | 103241101 | 8 | 3 | 3 | 1 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {A63222BC-82CE-46CA-A97A-89EA998E28CC}
6037 | 4184 | {E30058B1-671D-11E5-80CA-005056A729E5} | KERN | FRUITVALE | Bank 2 | CB 1108 (Non-SCADA) | PGE\BXYD | 2017-01-18 14:27:04.4196998 -08:00 | 253392108 | 082311101 | 8 | 3 | 3 | 1 | 463 | 10.1 | 10 | 463 | 10.1 | 10 | 581 | 12.68 | 12.55 | 570 | 12.44 | 12.32 | 526 | 11.48 | 11.37 | 526 | 11.48 | 11.37 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {83F9C40D-DD74-4483-BB0B-EA9F7EB53953}
6038 | 4355 | {D414BE0B-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CONTRA COSTA | Bank 8 | CB 2106 | PGE\WCL5 | 2017-01-19 14:38:53.6871784 -08:00 | 0136502106 | 082311102 | 22 | 3 | 3 | 1 | 503 | 18.1 | 17.92 | 489 | 17.6 | 17.42 | 578 | 20.8 | 20.59 | 549 | 19.76 | 19.56 | 557 | 20.05 | 19.85 | 557 | 20.05 | 19.85 | 674 | 24.26 | 24.02 | 674 | 24.26 | 24.02 | *Actual MTT setting is 850A, but is not selectable from menu. Primary: SEL-351, Backup: BE1-51 |  | FALSE | FALSE | 1667 | 2167 | 2000 | 2500 | {C6A2E41E-8B59-4C0B-9F3C-B6C55BF7AB42}
6040 | 4355 | {D414BE0E-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CONTRA COSTA | Bank 8 | CB 2107 | PGE\WCL5 | 2017-01-19 14:41:33.6058537 -08:00 | 0136502107 | 082311103 | 22 | 3 | 3 | 1 | 503 | 18.1 | 17.92 | 503 | 18.1 | 17.92 | 639 | 23 | 22.77 | 639 | 23 | 22.77 | 557 | 20.05 | 19.85 | 557 | 20.05 | 19.85 | 674 | 24.26 | 24.02 | 674 | 24.26 | 24.02 |  |  | FALSE | FALSE | 1667 | 2167 | 2000 | 2500 | {9BAA7920-CD86-4D9A-97A3-F57217B7845D}
6042 | 4355 | {DA5EAE41-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CONTRA COSTA | Bank 8 | CB 2108 | PGE\WCL5 | 2017-01-19 14:43:38.2210501 -08:00 | 0136502108 | 082311110 | 22 | 3 | 3 | 1 | 503 | 18.1 | 17.92 | 503 | 18.1 | 17.92 | 639 | 23 | 22.77 | 639 | 23 | 22.77 | 557 | 20.05 | 19.85 | 557 | 20.05 | 19.85 | 674 | 24.26 | 24.02 | 674 | 24.26 | 24.02 |  |  | FALSE | FALSE | 1667 | 2167 | 2000 | 2500 | {F226A433-2203-4501-BACF-CD6F59D87EE3}
6044 | 4355 | {E0730FB9-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CONTRA COSTA | Bank 8 | CB 2110 | PGE\WCL5 | 2017-01-19 14:46:04.2086575 -08:00 | 0136502110 | 082311111 | 22 | 3 | 3 | 1 | 503 | 18.1 | 17.92 | 503 | 18.1 | 17.92 | 639 | 23 | 22.77 | 639 | 23 | 22.77 | 557 | 20.05 | 19.85 | 557 | 20.05 | 19.85 | 674 | 24.26 | 24.02 | 674 | 24.26 | 24.02 | ** Please Watch Emergency Loading on 3-700Al UG Cable past Switch 26250. |  | FALSE | FALSE | 1667 | 2167 | 2000 | 2500 | {C29D728D-2D19-4B87-873F-0E855D25308E}
6046 | 4235 | {AB2668C7-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LOYOLA | Bank 1 | CB 403 (Under Construction) | PGE\MSJ9 | 2017-04-25 14:52:44.1764293 -07:00 | 082160403 | 083432101 | 3 | 3 | 3 | 2 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 |  |  | FALSE | FALSE | 693 | 902 | 832 | 1040 | {26E56D3C-9DAB-4C79-A1DF-10382FE92961}
6049 | 4357 | {AB2668DA-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LOYOLA | Bank 2 | CB 1101 (Under Construction) | PGE\MSJ9 | 2017-04-25 16:30:50.8278613 -07:00 | 0821601101 | 083432102 | 7 | 3 | 3 | 2 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | SW 9463 - 8 hour emergency rating of 800 Amps Relay Minimum Phase: __600___A, T 6 L 2 CT Ratio: 500:5 To Operate Ground: __151___A, T___1.5__ L 2.5 Ammeter Range 0 to ________ |  | FALSE | FALSE | 972 | 1263 | 1166 | 1440 | {55E6FB4E-3648-49F6-A8D8-20F3D5253CE4}
6052 | 1242 | {D7085B9E-671D-11E5-80CA-005056A729E5} | FRESNO | TULARE LAKE | Bank 2 | CB 1108 | PGE\T1SI | 2017-01-19 16:38:20.0125897 -08:00 | 252951108 | 083432103 | 8 | 3 | 3 | 1 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 |  |  | FALSE | FALSE | 572 | 744 | 687 | 842 | {9FF2F62A-EDA4-4B22-B234-13D3FB7D8F74}
6056 | 4357 | {AB26690D-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LOYOLA | Bank 2 | CB 1102 (Under Construction) | PGE\MSJ9 | 2017-04-25 16:39:23.9970778 -07:00 | 0821601102 | 083432105 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 467 | 10.09 | 9.99 | 720 | 15.55 | 15.39 | 526 | 11.36 | 11.25 | 600 | 12.96 | 12.83 | 532 | 11.49 | 11.38 | 720 | 15.55 | 15.39 | 568 | 12.27 | 12.15 | Relay Minimum Phase: __720___A, T___6____ L___15__ CT Ratio:___ 600:5___ To Operate Ground: __180___A, T___1.5__ L___16___ Ammeter Range 0 to ________ |  | FALSE | FALSE | 972 | 1263 | 1166 | 1440 | {E5D41C88-EC62-4A0F-8292-F79C238BC987}
6065 | 4358 | {D7085D11-671D-11E5-80CA-005056A729E5} | FRESNO | WOODWARD | Bank 3 | CB 2107 | PGE\BXYD | 2017-01-26 08:21:39.1983327 -08:00 | 2552902107 | 083432111 | 11 | 3 | 3 | 1 | 477 | 17.85 | 17.67 | 477 | 17.85 | 17.67 | 600 | 22.45 | 22.23 | 570 | 21.33 | 21.12 | 528 | 19.75 | 19.55 | 528 | 19.75 | 19.55 | 600 | 22.45 | 22.23 | 570 | 21.33 | 21.12 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {7A326A64-B926-45BB-B806-59C840EC83DC}
6066 | 4358 | {D7085D22-671D-11E5-80CA-005056A729E5} | FRESNO | WOODWARD | Bank 3 | CB 2108 | PGE\BXYD | 2017-01-20 14:11:03.9283535 -08:00 | 2552902108 | 083431108 | 11 | 3 | 3 | 1 | 578 | 21.62 | 21.4 | 570 | 21.33 | 21.12 | 600 | 22.45 | 22.23 | 570 | 21.33 | 21.12 | 600 | 22.45 | 22.23 | 570 | 21.33 | 21.12 | 600 | 22.45 | 22.23 | 570 | 21.33 | 21.12 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {CEA959C9-FE8B-40BF-BD52-703D8E8A9694}
6067 | 4358 | {D7085D33-671D-11E5-80CA-005056A729E5} | FRESNO | WOODWARD | Bank 3 | CB 2109 | PGE\BXYD | 2017-01-20 14:16:31.8466595 -08:00 | 2552902109 | 083431109 | 11 | 3 | 3 | 1 | 512 | 19.16 | 18.97 | 512 | 19.16 | 18.97 | 600 | 22.45 | 22.23 | 570 | 21.33 | 21.12 | 556 | 20.8 | 20.59 | 556 | 20.8 | 20.59 | 600 | 22.45 | 22.23 | 570 | 21.33 | 21.12 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {2DC25AA9-17C9-44AF-A95D-121751E54E1B}
6068 | 4362 | {D7085BBE-671D-11E5-80CA-005056A729E5} | FRESNO | WAHTOKE | Bank 2 | CB 1106 | PGE\BXYD | 2017-01-20 15:55:43.9539209 -08:00 | 2545301106 | 083431110 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1525 | 1960 | 1831 | 2288 | {778C2494-A87D-46C9-AF63-432051092791}
6069 | 4362 | {D7085BC3-671D-11E5-80CA-005056A729E5} | FRESNO | WAHTOKE | Bank 2 | CB 1107 | PGE\BXYD | 2017-01-20 16:05:25.8607112 -08:00 | 2545301107 | 083431111 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1525 | 1960 | 1831 | 2288 | {9BC9BCD8-0B0B-4831-B8F6-3BAF0832FBC4}
6070 | 4365 | {1143FD0F-0E4A-11E6-95F2-D4BED91EFF1A} | SIERRA | SPAULDING | BANK 2 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\JSKe | 2017-01-20 16:14:58.3385559 -08:00 | 152251101 | 083431112 | 8 | 3 | 3 | 1 | 105 | 2.29 | 2.27 | 105 | 2.29 | 2.27 | 110 | 2.4 | 2.38 | 110 | 2.4 | 2.38 | 110 | 2.4 | 2.38 | 110 | 2.4 | 2.38 | 110 | 2.4 | 2.38 | 110 | 2.4 | 2.38 |  |  | FALSE | FALSE | 105 | 137 | 122 | 147 | {977BA5FC-DB61-47DB-99AB-EA6BA44ED917}
6071 | 4364 | {941FA172-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | HONCUT | Bank 1 | CB 1101 | PGE\SDK6 | 2017-02-01 12:56:13.3417538 -08:00 | 1032101101 | 083431113 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {48558D14-7126-472B-9940-3079E352933A}
6072 | 4362 | {D7085BC8-671D-11E5-80CA-005056A729E5} | FRESNO | WAHTOKE | Bank 2 | CB 1108 | PGE\BXYD | 2017-01-20 16:11:19.8471185 -08:00 | 2545301108 | 083431114 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1525 | 1960 | 1831 | 2288 | {FA0A4A33-1E4A-4624-9249-9226B279D915}
6073 | 4364 | {941FA197-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | HONCUT | Bank 1 | CB 1102 | PGE\SDK6 | 2017-02-01 12:57:21.7793925 -08:00 | 1032101102 | 083431115 | 8 | 3 | 3 | 1 | 530 | 11.57 | 11.45 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {714801BC-ACF9-4495-BC07-9A5DF118FBCF}
6074 | 4367 | {B413E640-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | SUMMIT | Bank 1 | CB 1101 | PGE\JSKe | 2017-01-20 16:19:48.3444149 -08:00 | 1525901101 | 083431116 | 8 | 3 | 3 | 1 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 429 | 558 | 515 | 601 | {EBAFE129-D192-4E50-8063-D6FE74ACB7D1}
6075 | 4367 | {B413E673-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | SUMMIT | Bank 1 | CB 1102 | PGE\JSKe | 2017-01-20 16:26:50.2335193 -08:00 | 1525901102 | 083431117 | 8 | 3 | 3 | 1 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 429 | 558 | 515 | 601 | {A2A26D85-0035-4455-894A-6E18A2BC6432}
6077 | 4368 | {A086501F-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | PEACHTON | Bank 1 | CB 1102 | PGE\SDK6 | 2017-01-20 17:03:28.7836892 -08:00 | 1032401102 | 083182101 | 8 | 3 | 3 | 1 | 429 | 9.36 | 9.27 | 407 | 8.88 | 8.79 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 |  |  | TRUE | FALSE | 429 | 558 | 515 | 601 | {FE0B476E-43C9-4285-9BF3-6EC61696DD6A}
6078 | 4368 | {A0865036-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | PEACHTON | Bank 1 | CB 1103 | PGE\SDK6 | 2017-02-01 12:17:07.6349287 -08:00 | 1032401103 | 083182102 | 8 | 3 | 3 | 1 | 417 | 9.1 | 9.01 | 407 | 8.88 | 8.79 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 | 417 | 9.1 | 9.01 |  |  | TRUE | FALSE | 429 | 558 | 515 | 601 | {D2F64836-4288-43EE-9743-EB14A7FE180D}
6079 | 4369 | {A6861BED-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | PEACHTON | Bank 2 | CB 1101 | PGE\SDK6 | 2017-01-20 17:29:12.1525688 -08:00 | 1032401101 | 083182103 | 8 | 3 | 3 | 1 | 219 | 4.78 | 4.73 | 208 | 4.54 | 4.49 | 285 | 6.22 | 6.16 | 270 | 5.89 | 5.83 | 263 | 5.74 | 5.68 | 249 | 5.43 | 5.38 | 329 | 7.18 | 7.11 | 312 | 6.81 | 6.74 |  |  | TRUE | FALSE | 219 | 285 | 263 | 329 | {707470D9-F06D-4008-9A15-2CF21B3B67BD}
6080 | 4370 | {D5F175A1-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | ALMADEN | Bank 1 | CB 1101 | PGE\INM2 | 2017-01-22 04:31:24.0985619 -08:00 | 0823101101 | 083182104 | 7 | 3 | 3 | 2 | 582 | 12.57 | 12.44 | 552 | 11.92 | 11.8 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {2BE0B829-6067-4D03-AA65-0138063A78BB}
6081 | 4370 | {D5F175AA-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | ALMADEN | Bank 1 | CB 1102 | PGE\INM2 | 2017-01-22 04:21:58.4701361 -08:00 | 0823101102 | 083182105 | 7 | 3 | 3 | 2 | 582 | 12.57 | 12.44 | 582 | 12.57 | 12.44 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {AD440BE8-3CED-4925-8D69-10EE6E429A0D}
6082 | 4370 | {357DD6F2-FDBE-11E5-9D37-D4BED91EFF1A} | SAN JOSE | ALMADEN | Bank 1 | CB 1103 (Non-SCADA) | PGE\INM2 | 2017-01-22 04:47:58.5113363 -08:00 | 0823101103 | 083182106 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {C6D8EC2D-EE1F-4C6F-8CF4-F79443180B95}
6083 | 4371 | {D5F175CB-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | ALMADEN | Bank 3 | CB 1110 | PGE\INM2 | 2017-01-22 04:47:44.7676482 -08:00 | 0823101110 | 083182107 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {58C6231B-FE26-40DF-86BB-FC927E9F779D}
6084 | 4371 | {D5F175E2-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | ALMADEN | Bank 3 | CB 1111 | PGE\INM2 | 2017-01-22 04:47:28.9647469 -08:00 | 0823101111 | 252941106 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {4E028F4B-D6DE-42A5-823C-BC69C3CC7710}
6085 | 4372 | {DC00D2A3-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | HICKS | Bank 1 | CB 2101 | PGE\INM2 | 2017-01-22 05:56:52.6823847 -08:00 | 0834302101 | 252941107 | 11 | 2 | 2 | 2 | 564 | 21.1 | 20.89 | 564 | 21.1 | 20.89 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 2004 | 2606 | 2405 | 3007 | {88AB79C1-755D-4AD6-AE93-63CEC999867C}
6086 | 4372 | {DC00D2D6-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | HICKS | Bank 1 | CB 2102 | PGE\INM2 | 2017-01-22 06:07:56.1512799 -08:00 | 0834302102 | 253661101 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 2004 | 2606 | 2405 | 3007 | {141DD339-0B40-45DD-BD4B-260FCD98071B}
6087 | 4372 | {DC00D2F4-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | HICKS | Bank 1 | CB 2103 | PGE\INM2 | 2017-01-22 06:19:17.3424752 -08:00 | 0834302103 | 253661102 | 11 | 3 | 3 | 2 | 564 | 21.1 | 20.89 | 564 | 21.1 | 20.89 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 2004 | 2606 | 2405 | 3007 | {4DA24DEF-5E4D-4B71-BF46-0BD9852CB446}
6088 | 4372 | {DC00D343-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | HICKS | Bank 1 | CB 2105 | PGE\INM2 | 2017-01-22 07:29:42.3781838 -08:00 | 0834302105 | 253661104 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 2004 | 2606 | 2405 | 3007 | {1B763845-704F-422B-9ED7-86BFA113E4B6}
6089 | 4373 | {E2249FCD-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | HICKS | Bank 5 | CB 2111 | PGE\INM2 | 2017-01-22 07:44:53.9817143 -08:00 | 0834302111 | 253661107 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 2004 | 2606 | 2405 | 3007 | {0A73F13A-5112-4EF9-B51F-5677D6C5BE4B}
6091 | 4374 | {DC00D3B9-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | HICKS | Bank 2 | CB 1108 | PGE\INM2 | 2017-01-22 08:10:12.1717097 -08:00 | 0834301108 | 253661108 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {B0B794F1-616E-4386-857D-F5F1433D1DE5}
6092 | 4374 | {DC00D3C2-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | HICKS | Bank 2 | CB 1109 | PGE\INM2 | 2017-01-22 09:52:36.9894770 -08:00 | 0834301109 | 252891112 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {E97C67C3-8A6D-4F87-9323-279772AD22FA}
6093 | 4374 | {DC00D3D9-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | HICKS | Bank 2 | CB 1110 | PGE\INM2 | 2017-01-22 09:52:22.0287893 -08:00 | 0834301110 | 103251101 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {8532F9C8-3683-49B5-AD5A-F97F6E20F08B}
6096 | 4374 | {DC00D3E9-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | HICKS | Bank 2 | CB 1111 | PGE\INM2 | 2017-01-22 08:53:12.6173327 -08:00 | 0834301111 | 252291105 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {E8D1E805-16DF-4425-8225-B5C9A916F6DC}
6097 | 4374 | {E2249F59-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | HICKS | Bank 2 | CB 1112 | PGE\INM2 | 2017-01-22 08:58:05.4661643 -08:00 | 0834301112 | 254121108 | 7 | 3 | 3 | 2 | 582 | 12.57 | 12.44 | 582 | 12.57 | 12.44 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {3A8CBFB1-D5F6-4DF5-AA91-F3AFE000CA4F}
6099 | 4375 | {E2249F65-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | HICKS | Bank 3 | CB 1113 | PGE\INM2 | 2017-01-22 09:15:17.2544060 -08:00 | 0834301113 | 152241101 | 7 | 3 | 3 | 2 | 564 | 12.18 | 12.06 | 564 | 12.18 | 12.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {9658AE99-678B-4E06-882A-5BC88841830E}
6100 | 4375 | {E2249F7C-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | HICKS | Bank 3 | CB 1114 | PGE\INM2 | 2017-01-22 09:22:30.1783313 -08:00 | 0834301114 | 152241102 | 7 | 3 | 3 | 2 | 564 | 12.18 | 12.06 | 564 | 12.18 | 12.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {E0D9E4A2-8F68-4514-8FDA-EB4AF3838F74}
6101 | 4375 | {E2249F8C-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | HICKS | Bank 3 | CB 1115 | PGE\INM2 | 2017-01-22 09:30:39.5285417 -08:00 | 0834301115 | 013471126 | 7 | 3 | 3 | 2 | 564 | 12.18 | 12.06 | 564 | 12.18 | 12.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {05B6B240-85A6-4969-AC4C-44E151351117}
6102 | 4375 | {E2249F9C-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | HICKS | Bank 3 | CB 1116 | PGE\INM2 | 2017-01-22 09:36:30.3012872 -08:00 | 0834301116 | 022031119 | 7 | 3 | 3 | 2 | 582 | 12.57 | 12.44 | 582 | 12.57 | 12.44 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {A67A43B3-A644-460E-98A1-EA5431B11002}
6103 | 4375 | {E2249FBA-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | HICKS | Bank 3 | CB 1117 | PGE\INM2 | 2017-01-22 09:51:48.9561533 -08:00 | 0834301117 | 022871113 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {CD6CEACB-A19E-4621-8AC0-1A8BC4D33CC3}
6104 | 4376 | {E224A014-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | LLAGAS | Bank 1 | CB 2101 | PGE\INM2 | 2017-01-22 11:04:18.2580708 -08:00 | 0831802101 | 022871114 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 801 | 1042 | 962 | 1202 | {D952BCBD-6F85-4E73-AD26-D97ACDF92AD0}
6105 | 4376 | {E224A080-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | LLAGAS | Bank 1 | CB 2102 | PGE\INM2 | 2017-01-22 11:04:04.2480136 -08:00 | 0831802102 | 022871115 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 801 | 1042 | 962 | 1202 | {B2AC044D-4230-4A18-817F-A0D91E00D50F}
6107 | 4377 | {E224A0A8-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | LLAGAS | Bank 2 | CB 2103 | PGE\INM2 | 2017-01-22 11:03:25.9465766 -08:00 | 0831802103 | 022871117 | 11 | 3 | 3 | 2 | 564 | 21.1 | 20.89 | 564 | 21.1 | 20.89 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 668 | 868 | 801 | 1002 | {DE3CE9DE-26B6-4635-ADAE-9F55D00A487F}
6108 | 4377 | {E224A106-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | LLAGAS | Bank 2 | CB 2104 | PGE\INM2 | 2017-01-22 11:02:44.4624540 -08:00 | 0831802104 | 022871118 | 11 | 3 | 3 | 2 | 468 | 17.51 | 17.33 | 468 | 17.51 | 17.33 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 528 | 19.75 | 19.55 | 528 | 19.75 | 19.55 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 668 | 868 | 801 | 1002 | {73BA1FCA-AD8A-4BEC-A354-18DCBDCE9643}
6109 | 4378 | {E224A127-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | LLAGAS | Bank 3 | CB 2105 | PGE\INM2 | 2017-01-22 11:16:59.0710813 -08:00 | 0831802105 | 022530403 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {E80A59DF-A014-4A1D-B971-704D19774C04}
6110 | 4378 | {E224A161-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | LLAGAS | Bank 3 | CB 2106 | PGE\INM2 | 2017-01-22 11:25:35.8950059 -08:00 | 0831802106 | 103132101 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {F55BB182-CF30-429F-8EA0-36B9B6178DED}
6111 | 4378 | {E224A1B1-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | LLAGAS | Bank 3 | CB 2107 | PGE\INM2 | 2017-01-22 11:31:56.4799247 -08:00 | 0831802107 | 103071103 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {856EED84-29B6-4153-8290-9FB6D8620AFB}
6112 | 1238 | {D10E206C-671D-11E5-80CA-005056A729E5} | FRESNO | TIVY VALLEY | Bank 1 | CB 1106 (Non-SCADA) | PGE\BXYD | 2017-01-23 08:33:12.4023220 -08:00 | 2529401106 | 012091110 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {2BDC58AE-F703-4F25-9366-B791DDC1B4B2}
6113 | 1238 | {D10E206F-671D-11E5-80CA-005056A729E5} | FRESNO | TIVY VALLEY | Bank 1 | CB 1107 (Non-SCADA) | PGE\BXYD | 2017-01-23 08:34:32.8374688 -08:00 | 2529401107 | 012091111 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 489 | 10.67 | 10.56 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {3BB72C13-EDC8-43B4-8A06-9DF532D04237}
6114 | 4379 | {D10E204D-671D-11E5-80CA-005056A729E5} | FRESNO | STROUD | Bank 1 | CB 1101 (Non-SCADA) | PGE\BXYD | 2017-01-23 08:59:07.7678323 -08:00 | 2536601101 | 012091118 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 447 | 9.76 | 9.66 | 424 | 9.25 | 9.16 | 500 | 10.91 | 10.8 | 488 | 10.65 | 10.54 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 954 | 1125 | 1154 | 1200 | {D1112947-FD2A-4EB4-B558-C38F960CB3C2}
6115 | 4379 | {D10E2053-671D-11E5-80CA-005056A729E5} | FRESNO | STROUD | Bank 1 | CB 1102 (Non-SCADA) | PGE\BXYD | 2017-01-23 09:01:30.2765728 -08:00 | 2536601102 | 012091115 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 954 | 1125 | 1154 | 1200 | {9487FD50-562F-45F6-AA0B-94BF52703F4F}
6116 | 4379 | {D10E2056-671D-11E5-80CA-005056A729E5} | FRESNO | STROUD | Bank 1 | CB 1104 (Non-SCADA) | PGE\BXYD | 2017-01-23 09:03:34.1585551 -08:00 | 2536601104 | 012091114 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 489 | 10.67 | 10.56 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 954 | 1125 | 1154 | 1200 | {3BFECCA9-622C-48DE-BB23-71570C28CF8D}
6117 | 4379 | {D10E2059-671D-11E5-80CA-005056A729E5} | FRESNO | STROUD | Bank 1 | CB 1107 | PGE\BXYD | 2017-01-23 09:05:53.9060425 -08:00 | 2536601107 | 012091108 | 8 | 1 | 1 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 954 | 1125 | 1154 | 1200 | {1CCF3A55-6ABE-46B7-933D-5A95578005EC}
6118 | 4379 | {D10E205E-671D-11E5-80CA-005056A729E5} | FRESNO | STROUD | Bank 1 | CB 1108 | PGE\BXYD | 2017-01-23 09:07:30.7059040 -08:00 | 2536601108 | 012091106 | 8 | 1 | 1 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 954 | 1125 | 1154 | 1200 | {F0064322-0B05-43CD-ADDC-F9EE0131ED11}
6119 | 1230 | {2717D5B8-A5BE-11E5-A1F0-D4BED91EFF1A} | FRESNO | SCHINDLER | Bank 3 | CB 1112 | PGE\BXYD | 2017-01-23 09:50:31.0579252 -08:00 | 2528901112 | 022070409 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Limiting Factor Parallel 1/0 Cu : Summer Norm/Emerg=564/630; Winter Norm/Emerg=716/764 |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {9BA3C96E-C8DE-4D21-8CD8-2ACBB6CE55DA}
6121 | 4380 | {ACCC4E32-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | TRES VIAS | Bank 2 | CB 1101 | PGE\SDK6 | 2017-01-23 12:38:40.4716469 -08:00 | 1032501101 | 103351101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Note that Group 1 Phase MTT is 408A. Do not use this unless instructed to be an Operations DE. |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {C0081E97-419C-49FE-814F-2354D55CD1ED}
6123 | 1206 | {D59C3EB9-0B42-11E6-9D37-D4BED91EFF1A} | FRESNO | PARLIER | Bank 2 | CB 1105 (Non-SCADA) | PGE\BXYD | 2017-01-23 13:22:36.3786382 -08:00 | 2522901105 | 103351104 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {676840E2-AEC6-468A-AEF9-804EFBCD66C4}
6124 | 1197 | {0003E025-1181-11E6-95F2-D4BED91EFF1A} | FRESNO | MC CALL | Bank 5 | CB 1108 | PGE\BXYD | 2017-01-23 14:05:03.2368153 -08:00 | 2541201108 | 103401101 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {D00471B7-C46C-4901-96BA-02516CC4632A}
6360 | 4474 | {67F61AF2-BD96-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 1 (Banks 11, 15, 16) | CB ZJ-1 | PGE\DMAL | 2017-02-13 14:20:13.9870315 -08:00 |  | 103401102 | 7 | 3 | 3 | 2 | 480 | 10.37 | 10.27 | 480 | 10.37 | 10.27 | 559 | 12.07 | 11.95 | 559 | 12.07 | 11.95 | 490 | 10.58 | 10.47 | 490 | 10.58 | 10.47 | 570 | 12.31 | 12.19 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {ED429153-8DAF-46E1-81E5-6CFC2EBE8782}
6361 | 4474 | {74DEE10A-BD96-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 1 (Banks 11, 15, 16) | CB ZJ-2 (Under Construction) | PGE\DMAL | 2017-02-22 11:37:30.3375873 -08:00 |  | 103441101 | 7 | 3 | 3 | 2 | 480 | 10.37 | 10.27 | 480 | 10.37 | 10.27 | 559 | 12.07 | 11.95 | 559 | 12.07 | 11.95 | 490 | 10.58 | 10.47 | 490 | 10.58 | 10.47 | 570 | 12.31 | 12.19 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {73A06E3C-B1E5-47E7-963B-F30218BBE456}
6362 | 4474 | {7F47F0C2-BD96-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 1 (Banks 11, 15, 16) | CB ZJ-3 | PGE\DMAL | 2017-02-22 11:40:23.3605146 -08:00 |  | 103441102 | 7 | 3 | 3 | 2 | 480 | 10.37 | 10.27 | 480 | 10.37 | 10.27 | 559 | 12.07 | 11.95 | 559 | 12.07 | 11.95 | 490 | 10.58 | 10.47 | 490 | 10.58 | 10.47 | 570 | 12.31 | 12.19 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {AB6F1A2B-9555-47B1-9804-D367DDAAD430}
6363 | 4474 | {8A3DB3B4-BD96-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 1 (Banks 11, 15, 16) | CB ZJ-4 | PGE\DMAL | 2017-02-13 14:24:47.3198878 -08:00 |  | 103441103 | 7 | 3 | 3 | 2 | 480 | 10.37 | 10.27 | 480 | 10.37 | 10.27 | 559 | 12.07 | 11.95 | 559 | 12.07 | 11.95 | 490 | 10.58 | 10.47 | 490 | 10.58 | 10.47 | 570 | 12.31 | 12.19 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {5434CB7A-10BC-43AC-B6EB-D63B6632377C}
6364 | 4474 | {932E4A99-BD96-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 1 (Banks 11, 15, 16) | CB ZJ-5 | PGE\DMAL | 2017-02-22 14:37:36.6185964 -08:00 |  | 103451101 | 7 | 3 | 3 | 2 | 480 | 10.37 | 10.27 | 480 | 10.37 | 10.27 | 559 | 12.07 | 11.95 | 559 | 12.07 | 11.95 | 490 | 10.58 | 10.47 | 490 | 10.58 | 10.47 | 570 | 12.31 | 12.19 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {CB5F98B3-B02F-456C-9E75-D335AFDA6DAE}
6365 | 4478 | {A0BFD3F6-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | HALSEY | Bank 1 | CB 1101 | PGE\MTN6 | 2017-02-14 16:08:43.5465000 -08:00 | 1522401101 | 103461101 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 859 | 900 | 900 | 900 | {5B22F071-0998-458F-84A5-EA3A265E93D5}
6366 | 4478 | {A0BFD3FF-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | HALSEY | Bank 1 | CB 1102 | PGE\MTN6 | 2017-02-14 16:10:58.1918262 -08:00 | 1522401102 | 152291101 | 8 | 4 | 4 | 2 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 859 | 900 | 900 | 900 | {087FC2E8-4FE0-459E-B0BD-D648B9889469}
6367 | 3850 | {00DE4D5C-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | RICHMOND R | Bank 2 | CB 1126 | PGE\C7CF | 2017-05-24 09:49:41.0902227 -07:00 | 0134701126 | 152291102 | 7 | 3 | 3 | 2 | 543 | 11.73 | 11.61 | 517 | 11.17 | 11.06 | 600 | 12.96 | 12.83 | 583 | 12.59 | 12.46 | 554 | 11.97 | 11.85 | 554 | 11.97 | 11.85 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {1F37C568-EFF9-45E7-9403-65A51C36510D}
6368 | 4457 | {66585507-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 2 | CB 1119 | PGE\DMAL | 2017-03-08 13:50:44.4210480 -08:00 | 0220301119 | 252701104 | 7 | 3 | 3 | 2 | 383 | 8.27 | 8.19 | 383 | 8.27 | 8.19 | 425 | 9.18 | 9.09 | 425 | 9.18 | 9.09 | 394 | 8.51 | 8.42 | 394 | 8.51 | 8.42 | 438 | 9.46 | 9.37 | 438 | 9.46 | 9.37 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {FE0163B6-0543-4BA5-BFA1-04D7E889AD9D}
6369 | 4474 | {41887E8E-3D5B-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 1 (Banks 11, 15, 16) | CB 1113 | PGE\DMAL | 2017-03-15 12:06:38.2189517 -07:00 | 0228701113 | 252701106 | 7 | 3 | 3 | 2 | 445 | 9.61 | 9.51 | 445 | 9.61 | 9.51 | 494 | 10.67 | 10.56 | 494 | 10.67 | 10.56 | 458 | 9.89 | 9.79 | 458 | 9.89 | 9.79 | 509 | 10.99 | 10.88 | 509 | 10.99 | 10.88 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {D8575A84-16BA-49BE-962C-2A9C7C5516F6}
6370 | 4474 | {C4126434-687A-11E6-9BE4-80000BC6CD8D} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 1 (Banks 11, 15, 16) | CB 1114 | PGE\DMAL | 2017-03-15 12:06:57.7224517 -07:00 | 022871114 | 252701110 | 7 | 3 | 3 | 2 | 445 | 9.61 | 9.51 | 445 | 9.61 | 9.51 | 494 | 10.67 | 10.56 | 494 | 10.67 | 10.56 | 458 | 9.89 | 9.79 | 458 | 9.89 | 9.79 | 509 | 10.99 | 10.88 | 509 | 10.99 | 10.88 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {FC3EFB1A-6D98-48EE-9A6A-75D1CE222459}
6371 | 4474 | {65864963-60B5-11E6-9BE4-80000BC6CD8D} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 1 (Banks 11, 15, 16) | CB 1115 | PGE\DMAL | 2017-03-15 12:07:16.9451013 -07:00 | 022871115 | 253161106 | 7 | 3 | 3 | 2 | 481 | 10.39 | 10.29 | 481 | 10.39 | 10.29 | 592 | 12.79 | 12.66 | 592 | 12.79 | 12.66 | 493 | 10.65 | 10.54 | 493 | 10.65 | 10.54 | 599 | 12.94 | 12.81 | 599 | 12.94 | 12.81 | Branch SW-11644_500T PL&N_3ELC (SN=360/SE=400/WN=371/WE=412). Branch SW-11520_250T PL&N_3ELC (SN=245/SE=272/WN=252/WE=280). 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {48C410FB-C9BC-4D14-A5DA-12226C92207B}
6372 | 4474 | {4EEAAF94-60B5-11E6-9BE4-80000BC6CD8D} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 1 (Banks 11, 15, 16) | CB 1117 | PGE\DMAL | 2017-03-09 12:52:50.5336384 -08:00 | 022871117 | 253161107 | 7 | 3 | 3 | 2 | 483 | 10.43 | 10.33 | 483 | 10.43 | 10.33 | 633 | 13.67 | 13.53 | 633 | 13.67 | 13.53 | 493 | 10.65 | 10.54 | 493 | 10.65 | 10.54 | 646 | 13.95 | 13.81 | 646 | 13.95 | 13.81 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {CDD3B336-4B90-43CC-9378-D6D76F250F87}
6373 | 4474 | {497E3E8B-3D5B-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 1 (Banks 11, 15, 16) | CB 1118 | PGE\DMAL | 2017-03-09 12:54:28.7531272 -08:00 | 0228701118 | 253161108 | 7 | 3 | 3 | 2 | 483 | 10.43 | 10.33 | 483 | 10.43 | 10.33 | 586 | 12.66 | 12.53 | 586 | 12.66 | 12.53 | 493 | 10.65 | 10.54 | 493 | 10.65 | 10.54 | 598 | 12.92 | 12.79 | 598 | 12.92 | 12.79 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {8074228B-BE91-4188-B040-F2C83876A0B3}
6596 | 4554 | {5A011854-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | 6TH AVENUE | Bank 3 (Non SCADA) | CB 403 (Non-SCADA) | PGE\DMAL | 2017-03-28 17:30:19.0399437 -07:00 | 022530403 | 253161109 | 3 | 3 | 3 | 2 | 277 | 2 | 1.98 | 277 | 2 | 1.98 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | Bank Limited |  | FALSE | FALSE | 277 | 360 | 333 | 400 | {27E4FF42-8CAB-4632-A467-0251AAF5A9D0}
6598 | 4556 | {8D29882E-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CRESCENT MILLS | Bank 1 | CB 2101 | PGE\JBJ8 | 2017-03-21 17:01:33.4977053 -07:00 | 1031302101 | 253161116 | 11 | 4 | 4 | 1 | 150 | 5.61 | 5.55 | 150 | 5.61 | 5.55 | 150 | 5.61 | 5.55 | 150 | 5.61 | 5.55 | 150 | 5.61 | 5.55 | 150 | 5.61 | 5.55 | 150 | 5.61 | 5.55 | 150 | 5.61 | 5.55 | transferred from sharepoint | Crescent Mills Bank 1 Net Capability | FALSE | FALSE | 150 | 150 | 150 | 150 | {0AA99ECA-E79A-4CEF-831C-28CCA2EE3822}
6601 | 4565 | {9A705D0F-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | NORD | Bank 1 | CB 1103 | PGE\DRN3 | 2017-03-24 15:50:45.7120424 -07:00 | 1030701103 | 252681104 | 7 | 4 | 4 | 1 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 740 | 963 | 888 | 1111 | {DA72C6B3-FAB6-4A09-A788-780CB708EF28}
6602 | 2549 | {665B473F-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 5 | CB 1110 | PGE\MUSF | 2017-06-09 14:56:54.8683783 -07:00 | 0120901110 | 252681108 | 7 | 3 | 3 | 2 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {4A596071-6356-4532-8204-459167C03D5E}
6603 | 2549 | {6C8E24EF-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 5 | CB 1111 | PGE\C7CF | 2017-05-30 17:11:50.2524738 -07:00 | 0120901111 | 102551101 | 7 | 3 | 3 | 2 | 383 | 8.27 | 8.19 | 383 | 8.27 | 8.19 | 429 | 9.27 | 9.18 | 429 | 9.27 | 9.18 | 394 | 8.51 | 8.42 | 394 | 8.51 | 8.42 | 442 | 9.55 | 9.45 | 442 | 9.55 | 9.45 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {8DABF330-7900-43B7-82B0-83E4A9BB6834}
6604 | 2549 | {6C8E24F8-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 5 | CB 1118 | PGE\C7CF | 2017-05-30 17:29:46.7337753 -07:00 | 0120901118 | 102781101 | 7 | 3 | 3 | 2 | 383 | 8.27 | 8.19 | 383 | 8.27 | 8.19 | 429 | 9.27 | 9.18 | 429 | 9.27 | 9.18 | 394 | 8.51 | 8.42 | 394 | 8.51 | 8.42 | 442 | 9.55 | 9.45 | 442 | 9.55 | 9.45 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {7B70FE49-FB88-41DF-8C0C-0A58D8FB2FB6}
6605 | 2549 | {6C8E24F2-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 5 | CB 1115 | PGE\C7CF | 2017-05-30 17:16:21.5451688 -07:00 | 0120901115 | 083531103 | 7 | 3 | 3 | 2 | 505 | 10.91 | 10.8 | 505 | 10.91 | 10.8 | 586 | 12.66 | 12.53 | 586 | 12.66 | 12.53 | 515 | 11.12 | 11.01 | 515 | 11.12 | 11.01 | 598 | 12.92 | 12.79 | 598 | 12.92 | 12.79 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {171D96A8-7E02-4303-8C41-A6E94BFC4068}
6606 | 2549 | {67C67837-5FFB-11E6-9BE4-80000BC6CD8D} | EAST BAY | OAKLAND J | Bank 5 | CB 1114 | PGE\C7CF | 2017-05-30 17:13:52.7007983 -07:00 | 012091114 | 083531104 | 7 | 3 | 3 | 2 | 525 | 11.34 | 11.23 | 525 | 11.34 | 11.23 | 588 | 12.7 | 12.57 | 588 | 12.7 | 12.57 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {83920F9A-2B42-47EF-B261-CEA4963DD537}
6607 | 2549 | {59AF343E-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 5 | CB 1108 | PGE\MUSF | 2017-06-09 14:38:21.8351053 -07:00 | 0120901108 | 083531105 | 7 | 3 | 3 | 2 | 383 | 8.27 | 8.19 | 383 | 8.27 | 8.19 | 425 | 9.18 | 9.09 | 425 | 9.18 | 9.09 | 394 | 8.51 | 8.42 | 394 | 8.51 | 8.42 | 438 | 9.46 | 9.37 | 438 | 9.46 | 9.37 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {6BD75710-5CBE-486C-80E5-BCF2B18810C7}
6608 | 2549 | {5377747D-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 5 | CB 1106 | PGE\MUSF | 2017-04-20 09:49:07.7084487 -07:00 | 0120901106 | 083531106 | 7 | 3 | 3 | 2 | 360 | 7.78 | 7.7 | 360 | 7.78 | 7.7 | 400 | 8.64 | 8.55 | 400 | 8.64 | 8.55 | 371 | 8.01 | 7.93 | 371 | 8.01 | 7.93 | 412 | 8.9 | 8.81 | 412 | 8.9 | 8.81 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {8D8E4A30-2EC9-4F1F-9E52-EC91233AA60E}
6609 | 4500 | {9A1BD0E6-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF E | Bank 2 | CB 409 (Non-SCADA) | PGE\DMAL | 2017-05-02 17:07:58.5987691 -07:00 | 02207409 | 083531107 | 3 | 3 | 3 | 2 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 500EPRcu SPLIT: West Branch is limited by 500T cable 4ELC. Soutch Branch is limited by 250T cable 2ELC. |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2185 | {D902E502-FDCA-46AE-B2C7-FE819458CA3B}
6610 | 4500 | {68B119E7-B748-11E6-B077-D4BED91EFF1A} | SAN FRANCISCO | SF E | Bank 2 | CB E405-410/2 (Non-SCADA) | PGE\DMAL | 2017-03-28 13:04:19.3016207 -07:00 |  | 083531108 | 3 | 3 | 3 | 2 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 |  |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2185 | {6096B3D4-74A2-4A2D-B9AC-FDC03CFA33BC}
6611 | 4568 | {8D298877-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | DESCHUTES | Bank 1 | CB 1101 | PGE\AxDj | 2017-03-27 16:35:15.8342504 -07:00 | 1033501101 | 083531109 | 8 | 4 | 4 | 1 | 572 | 12.48 | 12.36 | 572 | 12.48 | 12.36 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | AXDJ: circuit capability is 570A any season - use at your own risk |  | FALSE | FALSE | 572 | 600 | 600 | 600 | {2A10EFCB-54C6-43C4-A87C-CEC0CCE45D06}
6612 | 4569 | {8D29888A-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | DESCHUTES | Bank 2 | CB 1104 | PGE\AxDj | 2017-03-27 16:36:57.3603520 -07:00 | 1033501104 | 103021101 | 8 | 4 | 4 | 1 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 |  |  | FALSE | FALSE | 700 | 700 | 700 | 700 | {41272DAC-47B9-4F8D-A86A-DE2BB3E7DC62}
6616 | 4570 | {8D29899C-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | GIRVAN | Bank 1 | CB 1101 | PGE\AxDj | 2017-03-27 16:44:40.0622840 -07:00 | 1034001101 | 083531110 | 8 | 4 | 4 | 2 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 916 | 1191 | 1099 | 1374 | {DA5FA498-9975-4A96-A7B9-ED9383B9E055}
6618 | 4570 | {8D2989A5-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | GIRVAN | Bank 1 | CB 1102 | PGE\AxDj | 2017-03-27 16:46:22.5087974 -07:00 | 1034001102 | 083531111 | 8 | 4 | 4 | 2 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 916 | 1191 | 1099 | 1374 | {54A0BF2B-E7A3-474C-B59D-586ADCFD9F98}
6620 | 4571 | {941FA227-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | JESSUP | Bank 1 | CB 1101 | PGE\AxDj | 2017-03-27 19:55:59.3159887 -07:00 | 1034401101 | 083531112 | 8 | 4 | 4 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | AXDJ notes : capabilities : use at your own risk Summer Winter Nor Emg Nor Emg 565 700 600 700 |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {C15A1199-6300-4FED-8BDE-87D05CC151AE}
6622 | 4571 | {941FA23E-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | JESSUP | Bank 1 | CB 1102 | PGE\AxDj | 2017-03-27 20:00:26.3284164 -07:00 | 1034401102 | 082831101 | 8 | 4 | 4 | 1 | 591 | 12.9 | 12.77 | 591 | 12.9 | 12.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Axdj notes: capability : use at your own risk Summer Winter Nor Emg Nor Emg 530 600 570 600 |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {B04E5D9C-A511-4F3E-A5E7-FBFDDE72FA60}
6623 | 4571 | {941FA272-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | JESSUP | Bank 1 | CB 1103 | PGE\AxDj | 2017-03-27 20:02:29.0920336 -07:00 | 1034401103 | 102520402 | 8 | 4 | 4 | 1 | 514 | 11.22 | 11.11 | 514 | 11.22 | 11.11 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {AB060123-97C6-4D37-804A-12144FF3537D}
6624 | 4573 | {941FA2D2-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | KESWICK | Bank 1 | CB 1101 | PGE\AxDj | 2017-03-27 20:11:47.6290449 -07:00 | 1034501101 | 082831103 | 8 | 4 | 4 | 1 | 224 | 4.89 | 4.84 | 224 | 4.89 | 4.84 | 291 | 6.35 | 6.29 | 291 | 6.35 | 6.29 | 269 | 5.87 | 5.81 | 269 | 5.87 | 5.81 | 336 | 7.33 | 7.26 | 336 | 7.33 | 7.26 | axdj notes: capabilities use at your own risk Summer Winter Nor Emg Nor Emg 218 284 262 327 |  | FALSE | FALSE | 224 | 291 | 269 | 336 | {0B45F0CD-1AE2-4221-9FC5-2A23EF12076F}
6626 | 4574 | {A0864F1E-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | PANORAMA | Bank 1 | CB 1101 | PGE\AxDj | 2017-03-27 20:32:57.0341802 -07:00 | 1034601101 | 102520403 | 8 | 4 | 4 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 500 | 500 | 500 | 500 | {3009BEF0-BAA0-485C-B7B6-B6858CEB2249}
6125 | 4381 | {B413E69E-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | TAMARACK | Bank 1 | CB 1101 | PGE\JSKe | 2017-01-23 14:12:59.1338823 -08:00 | 1522901101 | 082831105 | 8 | 3 | 3 | 1 | 154 | 3.36 | 3.33 | 146 | 3.19 | 3.16 | 173 | 3.78 | 3.74 | 164 | 3.58 | 3.54 | 210 | 4.58 | 4.53 | 205 | 4.47 | 4.43 | 210 | 4.58 | 4.53 | 210 | 4.58 | 4.53 |  |  | FALSE | FALSE | 481 | 481 | 481 | 481 | {0F8797B0-5F8C-49C4-B0EB-EB72D9819F58}
6126 | 4381 | {B413E6A7-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | TAMARACK | Bank 1 | CB 1102 | PGE\JSKe | 2017-01-23 14:16:03.8970467 -08:00 | 1522901102 | 082831108 | 8 | 3 | 3 | 1 | 154 | 3.36 | 3.33 | 146 | 3.19 | 3.16 | 173 | 3.78 | 3.74 | 164 | 3.58 | 3.54 | 210 | 4.58 | 4.53 | 205 | 4.47 | 4.43 | 210 | 4.58 | 4.53 | 210 | 4.58 | 4.53 |  |  | FALSE | FALSE | 481 | 481 | 481 | 481 | {817155A2-570B-40C6-AD76-0590E7011A1C}
6127 | 1174 | {C51140F5-671D-11E5-80CA-005056A729E5} | FRESNO | KEARNEY | Bank 1 | CB 1104 | PGE\BXYD | 2017-01-24 08:04:06.6877736 -08:00 | 2527001104 | 082831109 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 489 | 10.67 | 10.56 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {09220849-9CAA-4234-9370-D874E0BB1BB8}
6128 | 1174 | {C5114100-671D-11E5-80CA-005056A729E5} | FRESNO | KEARNEY | Bank 1 | CB 1106 | PGE\BXYD | 2017-01-24 08:06:32.5955089 -08:00 | 2527001106 | 013652109 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {13566F64-9A5B-4EC6-B11D-0C089DBA41E8}
6129 | 1174 | {C511410B-671D-11E5-80CA-005056A729E5} | FRESNO | KEARNEY | Bank 1 | CB 1110 | PGE\BXYD | 2017-01-24 08:09:38.6111013 -08:00 | 2527001110 | 013652111 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {9537848D-B5CB-44B1-AB1C-15C92D7BA289}
6131 | 1169 | {C51140AA-671D-11E5-80CA-005056A729E5} | FRESNO | HURON | Bank 1 | CB 1106 | PGE\BXYD | 2017-01-24 08:31:21.4846530 -08:00 | 2531601106 | 013652112 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 916 | 1125 | 1100 | 1200 | {B7A6C0BD-6A97-412E-9873-7C79635E8135}
6132 | 1169 | {C51140AF-671D-11E5-80CA-005056A729E5} | FRESNO | HURON | Bank 1 | CB 1107 | PGE\BXYD | 2017-01-24 08:34:54.5352187 -08:00 | 2531601107 | 013652113 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 916 | 1125 | 1100 | 1200 | {B0D0AFA5-4E5C-4BB6-9D61-0636AA8FF5B2}
6133 | 1169 | {C51140B4-671D-11E5-80CA-005056A729E5} | FRESNO | HURON | Bank 1 | CB 1108 | PGE\BXYD | 2017-01-24 08:38:34.6058294 -08:00 | 2531601108 | 082832110 | 8 | 3 | 3 | 1 | 317 | 6.92 | 6.85 | 317 | 6.92 | 6.85 | 317 | 6.92 | 6.85 | 317 | 6.92 | 6.85 | 317 | 6.92 | 6.85 | 317 | 6.92 | 6.85 | 317 | 6.92 | 6.85 | 317 | 6.92 | 6.85 |  |  | FALSE | FALSE | 916 | 1125 | 1100 | 1200 | {8812C4FD-78B0-4871-8914-96DDF34043BE}
6134 | 1169 | {C51140B9-671D-11E5-80CA-005056A729E5} | FRESNO | HURON | Bank 1 | CB 1109 | PGE\BXYD | 2017-01-24 08:40:45.1630663 -08:00 | 2531601109 | 102530401 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 916 | 1125 | 1100 | 1200 | {167C2723-2032-45FD-908E-EB01CFF6630A}
6135 | 1169 | {C51140BE-671D-11E5-80CA-005056A729E5} | FRESNO | HURON | Bank 1 | CB 1116 | PGE\BXYD | 2017-01-24 08:43:43.7998114 -08:00 | 2531601116 | 082832111 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 916 | 1125 | 1100 | 1200 | {6BB20B15-E016-4ECE-B369-C07B411D9282}
6136 | 4382 | {C5114084-671D-11E5-80CA-005056A729E5} | FRESNO | HENRIETTA | Bank 1 | CB 1104 | PGE\BXYD | 2017-01-24 08:55:53.8064909 -08:00 | 2526801104 | 082832112 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 |  |  | FALSE | FALSE | 512 | 666 | 615 | 769 | {7D968553-9B8E-49D9-993A-CB9885990563}
6137 | 4382 | {C511408C-671D-11E5-80CA-005056A729E5} | FRESNO | HENRIETTA | Bank 1 | CB 1108 | PGE\BXYD | 2017-01-24 09:08:47.3530495 -08:00 | 2526801108 | 082832113 | 8 | 3 | 3 | 1 | 512 | 11.17 | 11.06 | 512 | 11.17 | 11.06 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 512 | 666 | 615 | 769 | {C98A9F2E-D64A-442B-8698-388E676E1CA0}
6138 | 4383 | {8D2988B5-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | EAST QUINCY | Bank 1 | CB 1101 | PGE\SDK6 | 2017-01-24 12:36:00.1396737 -08:00 | 1025501101 | 082832114 | 8 | 3 | 3 | 1 | 295 | 6.44 | 6.38 | 280 | 6.11 | 6.05 | 383 | 8.36 | 8.28 | 363 | 7.92 | 7.84 | 354 | 7.73 | 7.65 | 336 | 7.33 | 7.26 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | TRUE | FALSE | 295 | 383 | 354 | 442 | {01BFE66A-FA89-43A6-AE3E-DBADBC13FFD2}
6139 | 4386 | {8D2988CB-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | ELK CREEK | Bank 1 | CB 1101 | PGE\SDK6 | 2017-01-26 08:49:53.1663914 -08:00 | 1027801101 | 082832115 | 8 | 3 | 3 | 1 | 140 | 3.06 | 3.03 | 133 | 2.9 | 2.87 | 150 | 3.27 | 3.24 | 149 | 3.25 | 3.22 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 |  |  | TRUE | FALSE | 312 | 312 | 312 | 312 | {82AE5EC2-8131-416D-836C-BFA32286A514}
6140 | 4385 | {E224A260-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MC KEE | Bank 1 | CB 1103 | PGE\INM2 | 2017-01-24 13:42:28.9856580 -08:00 | 0835301103 | 083892101 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {288E958B-B002-4143-B5E0-C566824AF84B}
6141 | 4385 | {E81C7C2A-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MC KEE | Bank 1 | CB 1104 | PGE\INM2 | 2017-01-24 13:42:05.9755105 -08:00 | 0835301104 | 083892102 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {5F336037-324C-4A28-801E-39D686305656}
6142 | 4385 | {E81C7C48-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MC KEE | Bank 1 | CB 1105 | PGE\INM2 | 2017-01-24 13:41:33.7301038 -08:00 | 0835301105 | 083892103 | 7 | 3 | 3 | 2 | 545 | 11.77 | 11.65 | 545 | 11.77 | 11.65 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 556 | 12.01 | 11.89 | 556 | 12.01 | 11.89 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {4A11C720-C1E8-4709-A1C3-098F7047897C}
6143 | 4387 | {E81C7C5B-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MC KEE | Bank 2 | CB 1106 | PGE\INM2 | 2017-01-24 13:41:07.5531360 -08:00 | 0835301106 | 083892104 | 7 | 3 | 3 | 2 | 564 | 12.18 | 12.06 | 564 | 12.18 | 12.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 598 | 12.92 | 12.79 | 598 | 12.92 | 12.79 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {070DB998-1E6F-47AC-B49B-7D34F473DA24}
6144 | 4387 | {E81C7C72-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MC KEE | Bank 2 | CB 1107 | PGE\INM2 | 2017-01-24 13:50:16.5986555 -08:00 | 0835301107 | 083892105 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {AD783F14-743D-4959-8347-C1DC50672D4E}
6145 | 4387 | {E81C7C90-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MC KEE | Bank 2 | CB 1108 | PGE\INM2 | 2017-01-24 14:07:02.2435019 -08:00 | 0835301108 | 083892106 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {FED22E63-4055-498F-9A7F-4FFB743F7629}
6147 | 4384 | {E81C7CAA-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MC KEE | Bank 3 | CB 1109 | PGE\INM2 | 2017-01-24 14:16:04.7213793 -08:00 | 0835301109 | 083892107 | 7 | 3 | 3 | 2 | 545 | 11.77 | 11.65 | 545 | 11.77 | 11.65 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 556 | 12.01 | 11.89 | 556 | 12.01 | 11.89 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {E29E5281-233F-46D5-B9F1-F26F89A3F069}
6148 | 4388 | {8D298952-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | GANSNER | Bank 1 | CB 1101 | PGE\SDK6 | 2017-02-01 16:23:51.0184091 -08:00 | 1030201101 | 083892108 | 8 | 3 | 3 | 1 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | 350 | 7.64 | 7.56 | Normal - Group 1 in service. Only use Group 2 when relieving load from East Quincy at peak. |  | FALSE | FALSE | 481 | 481 | 481 | 481 | {FC7D411E-6535-4215-8BDF-0B83235847E5}
6150 | 4384 | {E81C7CB3-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MC KEE | Bank 3 | CB 1110 | PGE\INM2 | 2017-01-24 14:19:07.1801489 -08:00 | 0835301110 | 083892109 | 7 | 3 | 3 | 2 | 545 | 11.77 | 11.65 | 545 | 11.77 | 11.65 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 556 | 12.01 | 11.89 | 556 | 12.01 | 11.89 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {21710AC9-0699-4FAC-83F6-7B0878AF67B1}
6151 | 4384 | {E81C7CCA-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MC KEE | Bank 3 | CB 1111 | PGE\INM2 | 2017-01-24 14:22:36.8142927 -08:00 | 0835301111 | 083242104 | 7 | 3 | 3 | 2 | 582 | 12.57 | 12.44 | 582 | 12.57 | 12.44 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {943B1513-6581-45F7-92C3-9DBF3807F4CF}
6152 | 4384 | {E81C7CD7-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MC KEE | Bank 3 | CB 1112 | PGE\INM2 | 2017-01-24 14:26:17.7273088 -08:00 | 0835301112 | 083242105 | 7 | 3 | 3 | 2 | 582 | 12.57 | 12.44 | 582 | 12.57 | 12.44 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {45349FD3-223E-4D16-B014-62F232D19B47}
6153 | 1122 | {E81C7CFB-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MILPITAS | Bank 1 | CB 1101 | PGE\INM2 | 2017-01-24 14:37:33.5704411 -08:00 | 0828301101 | 083242106 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {AA189C16-6C1F-4E5E-BF1D-2B308BEFAE23}
6154 | 4389 | {A0864EAB-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | OROVILLE | Bank 1 | CB 402 | PGE\SDK6 | 2017-02-01 15:10:33.8212355 -08:00 | 102520402 | 083242108 | 4 | 3 | 3 | 1 | 282 | 2.13 | 2.11 | 267 | 2.02 | 2 | 315 | 2.38 | 2.36 | 299 | 2.26 | 2.24 | 350 | 2.65 | 2.62 | 340 | 2.57 | 2.54 | 350 | 2.65 | 2.62 | 350 | 2.65 | 2.62 |  |  | TRUE | FALSE | 636 | 745 | 822 | 1028 | {1D8D00C0-087A-4B5C-B25E-2DF654686820}
6155 | 1122 | {E81C7D12-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MILPITAS | Bank 1 | CB 1103 | PGE\INM2 | 2017-01-24 14:42:23.9039022 -08:00 | 0828301103 | 083242109 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {1E108F0A-83CF-4660-97EF-FA2EEFB5660B}
6156 | 4389 | {A0864EB4-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | OROVILLE | Bank 1 | CB 403 | PGE\SDK6 | 2017-01-24 14:47:38.3843601 -08:00 | 102520403 | 083242110 | 3 | 3 | 3 | 1 | 282 | 2.03 | 2.01 | 267 | 1.92 | 1.9 | 315 | 2.27 | 2.25 | 299 | 2.15 | 2.13 | 350 | 2.52 | 2.49 | 340 | 2.45 | 2.43 | 350 | 2.52 | 2.49 | 350 | 2.52 | 2.49 | Feeder Reg is 3-phase 216 KVA 55C. |  | TRUE | FALSE | 636 | 745 | 864 | 1036 | {26B38FB7-408A-4B48-8936-91277E2D71E6}
6157 | 1122 | {E81C7D22-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MILPITAS | Bank 1 | CB 1105 | PGE\INM2 | 2017-01-24 15:10:20.4934495 -08:00 | 0828301105 | 083242111 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {6D8A7E5E-1791-495D-9B3D-E2CCABE00B99}
6158 | 1159 | {E81C7DA4-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MILPITAS | Bank 2 | CB 1108 | PGE\INM2 | 2017-01-24 15:16:05.4584608 -08:00 | 0828301108 | 083912109 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {BC31EC1F-1076-4A9A-BB95-A8D4EB9CCAC4}
6159 | 1159 | {E81C7DE5-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MILPITAS | Bank 2 | CB 1109 | PGE\INM2 | 2017-01-24 15:22:00.0331337 -08:00 | 0828301109 | 083912110 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {24E11AA6-E8BC-4732-B5E3-C6191A74A0D1}
6160 | 4390 | {E0730FD7-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CONTRA COSTA | Bank 9 | CB 2109 | PGE\WCL5 | 2017-01-24 15:58:09.2894391 -08:00 | 0136502109 | 083912111 | 22 | 3 | 3 | 1 | 661 | 23.79 | 23.55 | 661 | 23.79 | 23.55 | 792 | 28.51 | 28.22 | 792 | 28.51 | 28.22 | 717 | 25.81 | 25.55 | 717 | 25.81 | 25.55 | 800 | 28.79 | 28.5 | 800 | 28.79 | 28.5 | 45 amps of wayload on 1100Al EPR UG cable at circuit outlet to be factored in: Summer Normal = 616A, Summer EMG = 747A, Winter Normal = 672A, Winter EMG = 797A. |  | FALSE | FALSE | 1667 | 2167 | 2000 | 2500 | {3E04B6EC-6276-4DF6-A785-C3111B4FD6A6}
6162 | 4390 | {E0730FEF-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CONTRA COSTA | Bank 9 | CB 2111 | PGE\WCL5 | 2017-01-24 16:03:54.7068533 -08:00 | 0136502111 | 082342101 | 22 | 3 | 3 | 1 | 503 | 18.1 | 17.92 | 503 | 18.1 | 17.92 | 639 | 23 | 22.77 | 639 | 23 | 22.77 | 557 | 20.05 | 19.85 | 557 | 20.05 | 19.85 | 674 | 24.26 | 24.02 | 674 | 24.26 | 24.02 | Contra Costa 2111 Feeder OCB is normally open. Emergency use only, or for clearances. |  | FALSE | FALSE | 1667 | 2167 | 2000 | 2500 | {8C89FD26-AC92-4475-A9B4-24F18A640B10}
6165 | 4390 | {E0730FF2-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CONTRA COSTA | Bank 9 | CB 2112 | PGE\WCL5 | 2017-01-24 16:06:42.7667306 -08:00 | 0136502112 | 082342102 | 22 | 3 | 3 | 1 | 578 | 20.8 | 20.59 | 578 | 20.8 | 20.59 | 689 | 24.8 | 24.55 | 689 | 24.8 | 24.55 | 627 | 22.57 | 22.34 | 627 | 22.57 | 22.34 | 732 | 26.35 | 26.09 | 732 | 26.35 | 26.09 |  |  | FALSE | FALSE | 1667 | 2167 | 2000 | 2500 | {7A8A2095-8ED5-47C1-B1C4-3E1CC33EA553}
6167 | 4390 | {E0730FF5-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CONTRA COSTA | Bank 9 | CB 2113 | PGE\WCL5 | 2017-01-24 16:09:35.1010353 -08:00 | 0136502113 | 082342106 | 22 | 3 | 3 | 1 | 661 | 23.79 | 23.55 | 661 | 23.79 | 23.55 | 792 | 28.51 | 28.22 | 760 | 27.35 | 27.08 | 717 | 25.81 | 25.55 | 717 | 25.81 | 25.55 | 800 | 28.79 | 28.5 | 760 | 27.35 | 27.08 |  |  | FALSE | FALSE | 1667 | 2167 | 2000 | 2500 | {CC6C3FE7-DE54-4AAD-B0DF-937D011D7E17}
6169 | 4392 | {E81C7E45-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MILPITAS | Bank 3 | CB 2110 | PGE\INM2 | 2017-01-25 08:31:33.4534301 -08:00 | 0828302110 | 082342107 | 11 | 3 | 3 | 2 | 342 | 12.8 | 12.67 | 342 | 12.8 | 12.67 | 342 | 12.8 | 12.67 | 342 | 12.8 | 12.67 | 342 | 12.8 | 12.67 | 342 | 12.8 | 12.67 | 342 | 12.8 | 12.67 | 342 | 12.8 | 12.67 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {F35573EF-599C-4958-BCD9-6CD4E6DB0BDD}
6170 | 4393 | {8D298A17-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | GRAYS FLAT | Bank 1 | CB 401 | PGE\SDK6 | 2017-01-25 08:43:28.6244145 -08:00 | 102530401 | 082342108 | 4 | 3 | 3 | 1 | 183 | 1.39 | 1.38 | 173 | 1.31 | 1.3 | 211 | 1.6 | 1.58 | 200 | 1.51 | 1.49 | 237 | 1.79 | 1.77 | 225 | 1.7 | 1.68 | 284 | 2.15 | 2.13 | 269 | 2.04 | 2.02 |  |  | TRUE | FALSE | 198 | 257 | 237 | 297 | {3F1FE3F3-B4F9-4BB8-9897-208DAE55A4E2}
6172 | 4392 | {E81C7E56-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MILPITAS | Bank 3 | CB 2111 | PGE\INM2 | 2017-01-25 09:07:59.1210407 -08:00 | 0828302111 | 082250403 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {48D410C0-A7CB-45E5-8D88-9A38DA318820}
6173 | 4392 | {E81C7EA5-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MILPITAS | Bank 3 | CB 2112 | PGE\INM2 | 2017-01-25 09:13:17.4410812 -08:00 | 0828302112 | 082250404 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {83D58C50-C286-4A34-AD27-80CE963F7F16}
6175 | 4394 | {E81C7EDB-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MILPITAS | Bank 6 | CB 2113 | PGE\INM2 | 2017-01-25 09:22:33.5690461 -08:00 | 0828302113 | 082250405 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {0CDEA3E9-E2AF-4C91-B75D-E33F72B2D4A9}
6176 | 4394 | {E81C7EEB-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MILPITAS | Bank 6 | CB 2114 | PGE\INM2 | 2017-01-25 09:27:42.1234240 -08:00 | 0828302114 | 082250407 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {6C3626E9-E5D0-4EA0-B59E-697C1433BC5D}
6177 | 4394 | {E81C7F09-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MILPITAS | Bank 6 | CB 2115 | PGE\JLDe | 2017-03-13 15:08:43.5661844 -07:00 | 0828302115 | 082250408 | 11 | 3 | 3 | 2 | 564 | 21.1 | 20.89 | 564 | 21.1 | 20.89 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {1BA38643-85A9-4F6D-8D63-A4CF709C2EB8}
6178 | 4395 | {EED7A930-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MONTAGUE | Bank 1 | CB 2101 | PGE\INM2 | 2017-01-25 10:08:45.6444157 -08:00 | 0838902101 | 024052101 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {D9A2C40F-DAD7-4FDB-B710-6B54BA997AF2}
6179 | 4395 | {EED7A969-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MONTAGUE | Bank 1 | CB 2102 | PGE\INM2 | 2017-01-25 10:18:36.5606036 -08:00 | 0838902102 | 024050401 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {A355FA8A-BE4B-49FA-A94F-B5F87F940558}
6180 | 4395 | {EED7A99C-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MONTAGUE | Bank 1 | CB 2103 | PGE\INM2 | 2017-01-25 10:21:51.9362560 -08:00 | 0838902103 | 082250410 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {62AE1C9B-4F3D-409F-83FB-11469B78ED60}
6181 | 4396 | {EED7A9BD-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MONTAGUE | Bank 2 | CB 2104 | PGE\INM2 | 2017-01-25 10:26:57.8698171 -08:00 | 0838902104 | 082251109 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {C17D2E5B-564B-4BEB-8D11-168192E3C97A}
6182 | 4396 | {EED7A9E2-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MONTAGUE | Bank 2 | CB 2105 | PGE\INM2 | 2017-01-25 10:29:47.3649036 -08:00 | 0838902105 | 082251110 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {E64A31DC-B98D-4256-AFB5-0EFC76C02016}
6183 | 4396 | {EED7AA0E-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MONTAGUE | Bank 2 | CB 2106 | PGE\INM2 | 2017-01-25 10:34:17.7458368 -08:00 | 0838902106 | 024050402 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {031BA1D4-9462-4C66-B980-55B04B32FB67}
6185 | 4397 | {EED7AA3D-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MONTAGUE | Bank 3 | CB 2107 | PGE\INM2 | 2017-01-25 11:42:45.2746395 -08:00 | 0838902107 | 082251111 | 11 | 3 | 3 | 2 | 513 | 19.19 | 19 | 513 | 19.19 | 19 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 528 | 19.75 | 19.55 | 528 | 19.75 | 19.55 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {107DE1B0-29B7-4B67-8107-17D2DE245D0E}
6186 | 4397 | {EED7AA69-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MONTAGUE | Bank 3 | CB 2108 | PGE\INM2 | 2017-01-25 11:52:00.3918540 -08:00 | 0838902108 | 024050403 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {B42A65BB-6D2F-4EF7-B022-F64283369A9C}
6187 | 4397 | {EED7AAA4-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MONTAGUE | Bank 3 | CB 2109 | PGE\INM2 | 2017-01-25 11:57:15.4877312 -08:00 | 0838902109 | 024050404 | 11 | 3 | 3 | 2 | 468 | 17.51 | 17.33 | 468 | 17.51 | 17.33 | 591 | 22.11 | 21.89 | 591 | 22.11 | 21.89 | 528 | 19.75 | 19.55 | 528 | 19.75 | 19.55 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {14B63BAD-C4A8-49EE-902F-2D51D58387C9}
6188 | 4398 | {EED7AACF-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MORGAN HILL | Bank 1 | CB 2104 | PGE\INM2 | 2017-01-25 12:14:27.2531117 -08:00 | 0832402104 | 024050405 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {B8CD9ABC-91B5-4680-BDD3-C78B39CAACE2}
6189 | 4398 | {EED7AB10-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MORGAN HILL | Bank 1 | CB 2105 | PGE\INM2 | 2017-01-25 12:18:56.3270861 -08:00 | 0832402105 | 082251112 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {2B69F2E0-1966-44D2-9300-F0F3FC1AD8D8}
6190 | 4399 | {EED7AB78-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MORGAN HILL | Bank 2 | CB 2106 | PGE\INM2 | 2017-01-25 12:25:34.6027451 -08:00 | 0832402106 | 024060401 | 11 | 3 | 3 | 2 | 426 | 15.94 | 15.78 | 426 | 15.94 | 15.78 | 479 | 17.92 | 17.74 | 479 | 17.92 | 17.74 | 482 | 18.03 | 17.85 | 482 | 18.03 | 17.85 | 515 | 19.27 | 19.08 | 515 | 19.27 | 19.08 |  |  | FALSE | FALSE | 801 | 1042 | 962 | 1202 | {44E92740-61A0-4E81-A93B-BF784B392940}
6191 | 4399 | {EED7ABA4-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MORGAN HILL | Bank 2 | CB 2108 | PGE\INM2 | 2017-01-25 12:30:02.2414919 -08:00 | 0832402108 | 024060402 | 11 | 3 | 3 | 2 | 564 | 21.1 | 20.89 | 564 | 21.1 | 20.89 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 801 | 1042 | 962 | 1202 | {A209D840-9F82-4197-9DF0-E892A6185E73}
6193 | 4400 | {EED7ABFD-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MORGAN HILL | Bank 3 | CB 2109 | PGE\INM2 | 2017-01-25 13:15:41.0301599 -08:00 | 0832402109 | 082251113 | 11 | 3 | 3 | 2 | 564 | 21.1 | 20.89 | 564 | 21.1 | 20.89 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {BB184B9F-138F-4899-B972-A44718A57D67}
6194 | 4400 | {EED7AC38-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MORGAN HILL | Bank 3 | CB 2110 | PGE\INM2 | 2017-01-25 13:21:25.3443812 -08:00 | 0832402110 | 082261101 | 11 | 2 | 2 | 2 | 564 | 21.1 | 20.89 | 564 | 21.1 | 20.89 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {B012BDC4-6450-4568-A8D2-9F1EF339959F}
6195 | 4400 | {F4D10CAE-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | MORGAN HILL | Bank 3 | CB 2111 | PGE\INM2 | 2017-01-25 13:41:18.3617234 -08:00 | 0832402111 | 082261102 | 11 | 3 | 3 | 2 | 582 | 21.77 | 21.55 | 582 | 21.77 | 21.55 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {8EADF134-5B51-487F-A841-F0A16E1F7CAA}
6196 | 4401 | {F4D10E05-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | PIERCY | Bank 3 | CB 2109 | PGE\INM2 | 2017-01-25 13:49:16.3861160 -08:00 | 0839102109 | 082261103 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {8FE8D6DB-9C7E-4226-BEE3-422CED00B960}
6197 | 4401 | {F4D10E62-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | PIERCY | Bank 3 | CB 2110 | PGE\INM2 | 2017-01-25 14:07:38.5941119 -08:00 | 0839102110 | 082261104 | 11 | 4 | 4 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {4A5131E3-7D0A-4F69-A03C-8252047ED84E}
6198 | 2672 | {3380DCD6-6E51-11E6-BBF8-D4BED91EFF1A} | NORTH VALLEY | PIT NO 5 | Bank 5 | CB 1101 (Non-SCADA) | PGE\SDK6 | 2017-01-26 08:44:10.2917935 -08:00 |  | 082261105 | 8 | 3 | 3 | 1 | 137 | 2.99 | 2.96 | 130 | 2.84 | 2.81 | 157 | 3.43 | 3.4 | 149 | 3.25 | 3.22 | 164 | 3.58 | 3.54 | 155 | 3.38 | 3.35 | 185 | 4.04 | 4 | 175 | 3.82 | 3.78 |  |  | TRUE | FALSE | 137 | 178 | 164 | 206 | {00000000-0000-0000-0000-000000000000}
6199 | 4401 | {F4D10E80-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | PIERCY | Bank 3 | CB 2111 | PGE\INM2 | 2017-01-25 14:10:21.0868367 -08:00 | 0839102111 | 082261106 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {CC6E5EC4-5605-4C30-8F0C-F3A71BBFDA65}
6201 | 4402 | {F4D10EA5-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | RIVER OAKS | Bank 1 | CB 2101 | PGE\INM2 | 2017-01-26 08:23:20.9474827 -08:00 | 0823402101 | 024060403 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {86A8CD1A-5C0C-4FA1-AF16-B51CE9B3CB10}
6202 | 4402 | {F4D10ED1-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | RIVER OAKS | Bank 1 | CB 2102 | PGE\INM2 | 2017-01-26 08:35:34.8791965 -08:00 | 0823402102 | 082261107 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {DEDCBC4B-D9D9-4B3D-860C-B3692647F5DD}
6203 | 4403 | {F4D10F55-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | RIVER OAKS | Bank 2 | CB 2106 | PGE\INM2 | 2017-01-26 08:32:43.7751061 -08:00 | 0823402106 | 024060404 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {2610E86C-F930-4966-9E4F-E4BB625EFB50}
6204 | 4403 | {F4D10FC0-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | RIVER OAKS | Bank 2 | CB 2107 | PGE\INM2 | 2017-01-26 08:32:23.2919122 -08:00 | 0823402107 | 082261108 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {0711502D-8B96-4AB1-8F0D-38235D363F8A}
6205 | 4403 | {FAC8C23A-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | RIVER OAKS | Bank 2 | CB 2108 | PGE\INM2 | 2017-01-26 08:37:34.4866966 -08:00 | 0823402108 | 022641104 | 11 | 3 | 3 | 2 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {40B218F7-1C16-4D4B-8E96-EEE257E8BC02}
6207 | 4404 | {FAC8C265-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE A | Bank 1 | CB 403 (Non-SCADA) | PGE\INM2 | 2017-03-15 10:05:54.0639692 -07:00 | 082250403 | 022641105 | 3 | 3 | 2 | 2 | 387 | 2.79 | 2.76 | 387 | 2.79 | 2.76 | 480 | 3.46 | 3.43 | 480 | 3.46 | 3.43 | 464 | 3.34 | 3.31 | 464 | 3.34 | 3.31 | 480 | 3.46 | 3.43 | 480 | 3.46 | 3.43 | Phase Tap = 6 Lever = 2 IT = 3600 GE IAC53B Ground Tap = 2 Lever =2 IT = NA GE IAC53B |  | FALSE | FALSE | 2775 | 3608 | 3330 | 4163 | {3160180B-E04C-404D-A443-2C510C0F6C56}
6208 | 4404 | {FAC8C268-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE A | Bank 1 | CB 404 (Non-SCADA) | PGE\INM2 | 2017-03-15 10:07:01.9252742 -07:00 | 082250404 | 022641107 | 3 | 3 | 3 | 2 | 320 | 2.31 | 2.29 | 320 | 2.31 | 2.29 | 355 | 2.56 | 2.53 | 355 | 2.56 | 2.53 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 366 | 2.64 | 2.61 | 366 | 2.64 | 2.61 | Phase MTT = 500 IT = 3600 GE/SEL F60/351 Ground MTT = 160 IT = 3600 GE/SEL F60/351 |  | FALSE | FALSE | 2775 | 3608 | 3330 | 4163 | {3BFF07D0-C9EC-4DD5-A23A-D499BBDA695D}
6209 | 4404 | {FAC8C26B-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE A | Bank 1 | CB 405 (Non-SCADA) | PGE\INM2 | 2017-01-26 10:37:31.9659070 -08:00 | 082250405 | 022641112 | 3 | 3 | 3 | 2 | 377 | 2.72 | 2.69 | 336 | 2.42 | 2.4 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 388 | 2.8 | 2.77 | 388 | 2.8 | 2.77 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | Phase Tap = 6 Lever = 1.5 IT = 3600 GE IAC53B Ground Tap = 2 Lever = 2 ? GE IAC53B |  | FALSE | FALSE | 2775 | 3608 | 3330 | 4163 | {5D528405-CD26-4E0D-BA6E-6959CD012E0C}
6210 | 4405 | {FAC8C278-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE A | Bank 2 | CB 407 (Non-SCADA) | PGE\INM2 | 2017-01-26 10:35:29.2227466 -08:00 | 082250407 | 022641102 | 3 | 3 | 3 | 2 | 400 | 2.88 | 2.85 | 336 | 2.42 | 2.4 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | Phase Tap = 6 Lever = 2 IT = 3600 GE IAC53B Ground Tap = 2 Lever = 1.5 IT = 3600 GE IAC53B |  | FALSE | FALSE | 2775 | 3608 | 3330 | 4163 | {C3ADD57C-38CA-4AB9-9989-B1A84A8EF899}
6211 | 4405 | {FAC8C27B-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE A | Bank 2 | CB 408 (Non-SCADA) | PGE\INM2 | 2017-01-26 11:01:00.5793952 -08:00 | 082250408 | 082261109 | 3 | 3 | 3 | 2 | 377 | 2.72 | 2.69 | 336 | 2.42 | 2.4 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 388 | 2.8 | 2.77 | 388 | 2.8 | 2.77 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | Phase Tap = 6 Lever = 1.5 IT = 3600 GE IAC53B Ground Tap = 2 Lever = 2 IT = 3200 GE IAC53B |  | FALSE | FALSE | 2775 | 3608 | 3330 | 4163 | {FB3441C8-4DFD-4668-A053-824E1A9F3B9E}
6212 | 4406 | {13EDC01D-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BURLINGAME | Bank 1 | CB 2101 | PGE\C7CF | 2017-01-26 12:06:37.4555029 -08:00 | 024052101 | 082261110 | 12 | 3 | 3 | 2 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 | 533 | 20.14 | 19.94 |  |  | FALSE | FALSE | 793 | 1031 | 952 | 1190 | {00000000-0000-0000-0000-000000000000}
6213 | 4407 | {13EDC061-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BURLINGAME | Bank 3 (Non Scada) | CB 401 | PGE\C7CF | 2017-01-26 12:34:45.2675602 -08:00 | 024050401 | 022641108 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 1200 | 1440 | 1200 | 1440 | {9276F423-58B1-4727-AA51-3ADC404F0B9B}
6214 | 4405 | {FAC8C27E-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE A | Bank 2 | CB 410 (Non-SCADA) | PGE\INM2 | 2017-01-26 12:19:28.5471313 -08:00 | 082250410 | 022641109 | 3 | 3 | 3 | 2 | 377 | 2.72 | 2.69 | 336 | 2.42 | 2.4 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 388 | 2.8 | 2.77 | 388 | 2.8 | 2.77 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | Phase Tap = 6 Lever = 1.5 IT = 2400 GE IAC53B Ground Tap = 2 Lever = 2 IT = 1200 GE IAC53B |  | FALSE | FALSE | 2775 | 3608 | 3330 | 4163 | {76094172-F042-4FBB-BA7E-0112283511EA}
6215 | 4409 | {FAC8C28B-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE A | Bank 3 | CB 1109 | PGE\INM2 | 2017-01-26 12:26:06.8695912 -08:00 | 0822501109 | 022641110 | 7 | 3 | 3 | 2 | 390 | 8.42 | 8.34 | 390 | 8.42 | 8.34 | 480 | 10.37 | 10.27 | 480 | 10.37 | 10.27 | 402 | 8.68 | 8.59 | 402 | 8.68 | 8.59 | 486 | 10.5 | 10.4 | 486 | 10.5 | 10.4 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {012B30CA-3F0E-4330-A609-2CEB760E4571}
6216 | 4409 | {FAC8C2A9-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE A | Bank 3 | CB 1110 | PGE\INM2 | 2017-01-26 12:30:19.1420425 -08:00 | 0822501110 | 082261111 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {F7A9E1FC-C150-4430-BBAD-034386B7E096}
6217 | 4407 | {13EDC072-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BURLINGAME | Bank 3 (Non Scada) | CB 402 | PGE\C7CF | 2017-01-26 12:34:00.0578908 -08:00 | 024050402 | 022641101 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 285 | 2.16 | 2.14 | 390 | 2.95 | 2.92 | 370 | 2.8 | 2.77 | 360 | 2.72 | 2.69 | 342 | 2.59 | 2.56 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 1200 | 1440 | 1200 | 1440 | {B01A6F21-A09F-4DDB-A746-E38C6D71A40A}
6218 | 4409 | {FAC8C2D5-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE A | Bank 3 | CB 1111 | PGE\INM2 | 2017-01-26 12:43:00.6238861 -08:00 | 0822501111 | 082261112 | 7 | 3 | 3 | 2 | 450 | 9.72 | 9.62 | 450 | 9.72 | 9.62 | 504 | 10.89 | 10.78 | 504 | 10.89 | 10.78 | 464 | 10.02 | 9.92 | 464 | 10.02 | 9.92 | 519 | 11.21 | 11.1 | 519 | 11.21 | 11.1 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {7096AD69-1E54-42F3-9308-46EE6977F830}
6219 | 4407 | {13EDC082-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BURLINGAME | Bank 3 (Non Scada) | CB 403 | PGE\C7CF | 2017-01-26 12:45:04.2718639 -08:00 | 024050403 | 022641103 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 285 | 2.16 | 2.14 | 390 | 2.95 | 2.92 | 370 | 2.8 | 2.77 | 360 | 2.72 | 2.69 | 342 | 2.59 | 2.56 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 1200 | 1440 | 1200 | 1440 | {0DA6A7A2-0B1B-4F3C-B281-3A5570937439}
6220 | 4407 | {13EDC092-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BURLINGAME | Bank 3 (Non Scada) | CB 404 | PGE\C7CF | 2017-01-26 12:48:47.2313515 -08:00 | 024050404 | 022641106 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 285 | 2.16 | 2.14 | 390 | 2.95 | 2.92 | 370 | 2.8 | 2.77 | 360 | 2.72 | 2.69 | 342 | 2.59 | 2.56 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 1200 | 1440 | 1200 | 1440 | {FD2A3728-58E5-481A-9160-3735498DC396}
6221 | 4407 | {13EDC0A2-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | BURLINGAME | Bank 3 (Non Scada) | CB 405 | PGE\C7CF | 2017-01-26 12:52:37.9753888 -08:00 | 024050405 | 082261113 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 285 | 2.16 | 2.14 | 390 | 2.95 | 2.92 | 370 | 2.8 | 2.77 | 360 | 2.72 | 2.69 | 342 | 2.59 | 2.56 | 417 | 3.16 | 3.13 | 417 | 3.16 | 3.13 |  |  | FALSE | FALSE | 1200 | 1440 | 1200 | 1440 | {676F10E9-2DDB-484B-8B0E-DA20E2273FC6}
6222 | 4409 | {FAC8C2E1-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE A | Bank 3 | CB 1112 | PGE\INM2 | 2017-01-26 12:59:34.5658000 -08:00 | 0822501112 | 022641111 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {7282D950-32BB-4537-8B3A-4779BEEF1784}
6223 | 4410 | {19AB6B22-FDD4-11E5-9D37-D4BED91EFF1A} | PENINSULA | CAROLANDS | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2017-01-26 13:01:37.6365667 -08:00 | 024060401 | 082261114 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 |  |  | FALSE | FALSE | 475 | 600 | 570 | 600 | {E4B63EAD-44F6-4699-ABBF-2FC634DDDB0C}
6224 | 4410 | {19AB6B27-FDD4-11E5-9D37-D4BED91EFF1A} | PENINSULA | CAROLANDS | Bank 1 (Non SCADA) | CB 402 (Non-SCADA) | PGE\C7CF | 2017-01-26 13:07:50.9829463 -08:00 | 024060402 | 022641115 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 |  |  | FALSE | FALSE | 475 | 600 | 570 | 600 | {E1BBDF57-AF5B-4595-AC1B-A992C9D72A30}
6225 | 4411 | {FAC8C305-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE A | Bank 4 | CB 1113 | PGE\INM2 | 2017-01-26 13:11:15.1596727 -08:00 | 0822501113 | 082261115 | 7 | 3 | 3 | 2 | 390 | 8.42 | 8.34 | 390 | 8.42 | 8.34 | 480 | 10.37 | 10.27 | 480 | 10.37 | 10.27 | 402 | 8.68 | 8.59 | 402 | 8.68 | 8.59 | 486 | 10.5 | 10.4 | 486 | 10.5 | 10.4 |  |  | FALSE | FALSE | 486 | 631 | 583 | 729 | {C0C29B05-D2CB-4929-91C2-D1A867C994AB}
6226 | 4413 | {FAC8C322-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE B | Bank 1 | CB 1101 | PGE\INM2 | 2017-01-26 13:20:03.7758382 -08:00 | 0822601101 | 022571102 | 7 | 3 | 3 | 2 | 481 | 10.39 | 10.29 | 481 | 10.39 | 10.29 | 592 | 12.79 | 12.66 | 592 | 12.79 | 12.66 | 495 | 10.69 | 10.58 | 495 | 10.69 | 10.58 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {A8FD44B0-5C38-45D5-855C-13558CD33769}
6227 | 4413 | {FAC8C32B-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE B | Bank 1 | CB 1102 | PGE\INM2 | 2017-01-26 13:24:56.4686668 -08:00 | 0822601102 | 022571104 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {DD0EC422-40FD-49F7-AF1A-79216E6B656A}
6228 | 4413 | {FAC8C33B-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE B | Bank 1 | CB 1103 | PGE\INM2 | 2017-01-26 13:32:24.3844804 -08:00 | 0822601103 | 022571109 | 7 | 3 | 3 | 2 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {623C0383-2F6B-46DB-AD36-38F283E22546}
6229 | 4413 | {FAC8C352-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE B | Bank 1 | CB 1104 | PGE\INM2 | 2017-01-26 13:35:40.8078577 -08:00 | 0822601104 | 022571112 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {94418D96-10C1-428D-83F0-8BCA0456744F}
6230 | 4414 | {FAC8C381-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE B | Bank 2 | CB 1105 | PGE\INM2 | 2017-01-26 13:44:09.0968323 -08:00 | 0822601105 | 022570401 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {26861575-7F96-4C76-9B85-E9A7C9CAFFC2}
6231 | 4414 | {FAC8C3AD-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE B | Bank 2 | CB 1106 | PGE\INM2 | 2017-01-26 13:47:22.1661451 -08:00 | 0822601106 | 022570404 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {738FB9E3-C351-4B2E-8B7D-5482151D1793}
6232 | 4412 | {13EDC0E9-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | CAROLANDS | Bank 2 | CB 403 | PGE\C7CF | 2017-01-26 13:48:03.2573353 -08:00 | 02406403 | 022571105 | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 |  |  | FALSE | FALSE | 1387 | 1803 | 1664 | 2000 | {886101CC-F330-4EFE-A424-5DE602EB963E}
6233 | 4414 | {FAC8C3D2-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE B | Bank 2 | CB 1107 | PGE\INM2 | 2017-01-26 13:51:04.0804126 -08:00 | 0822601107 | 022571106 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {B96B7738-F9CC-4F64-8CC8-70EAD47C17D1}
6234 | 4412 | {13EDC10E-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | CAROLANDS | Bank 2 | CB 404 | PGE\C7CF | 2017-01-26 13:53:52.5636526 -08:00 | 02406404 | 022571107 | 4 | 3 | 3 | 2 | 515 | 3.9 | 3.86 | 515 | 3.9 | 3.86 | 556 | 4.21 | 4.17 | 556 | 4.21 | 4.17 | 530 | 4.01 | 3.97 | 530 | 4.01 | 3.97 | 573 | 4.34 | 4.3 | 573 | 4.34 | 4.3 |  |  | FALSE | FALSE | 1387 | 1803 | 1664 | 2000 | {13706818-DC03-4DD9-AE83-F744E18DA238}
6235 | 4414 | {FAC8C3F0-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE B | Bank 2 | CB 1108 | PGE\INM2 | 2017-01-26 13:53:52.8912589 -08:00 | 0822601108 | 022571108 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {A50DCA7F-18BE-437F-A4C7-E716AA5E1799}
6237 | 4416 | {08FE9DC7-BBE9-11E6-93A9-D4BED91EFF1A} | PENINSULA | DALY CITY | 12kv Buses | CB 1150/12 (Under Construction) | PGE\LMSQ | 2017-04-19 22:15:45.4306529 -07:00 |  | 022571101 | 7 | 4 | 4 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  | Extraneous value - doesn't reflect actual value of bus | FALSE | FALSE | 3120 | 3650 | 4115 | 4460 | {BFA7F936-0452-42DC-A454-A4793149AE52}
6238 | 4416 | {19A5D568-BBE9-11E6-93A9-D4BED91EFF1A} | PENINSULA | DALY CITY | 12kv Buses | CB 1150/22 (Under Construction) | PGE\LMSQ | 2017-04-19 22:15:54.4008254 -07:00 |  | 022571110 | 7 | 4 | 4 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3120 | 3650 | 4115 | 4460 | {110FD1ED-A624-47D5-A42C-DDB0A6B009C5}
6239 | 4416 | {288D8B45-BBE9-11E6-93A9-D4BED91EFF1A} | PENINSULA | DALY CITY | 12kv Buses | CB 1350/12 (Under Construction) | PGE\LMSQ | 2017-04-19 22:16:05.7734441 -07:00 |  | 022571113 | 7 | 4 | 4 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3120 | 3650 | 4115 | 4460 | {D8E8D0FC-9BC3-4272-9BBD-29888A0D2277}
6240 | 4416 | {36933E10-BBE9-11E6-93A9-D4BED91EFF1A} | PENINSULA | DALY CITY | 12kv Buses | CB 1350/22 (Under Construction) | PGE\LMSQ | 2017-04-19 22:16:16.3504475 -07:00 |  | 022571114 | 7 | 4 | 4 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3120 | 3650 | 4115 | 4460 | {5813F152-303F-4549-8611-9A69F8190F15}
6241 | 4417 | {13EDC139-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | DALY CITY | Bank 1 | CB 1104 | PGE\C7CF | 2017-01-26 14:11:29.4371767 -08:00 | 0226401104 | 022571103 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B1158E54-8B71-4841-B141-EAB19FE2BB4F}
6242 | 4417 | {13EDC165-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | DALY CITY | Bank 1 | CB 1105 | PGE\DMAL | 2017-05-17 13:17:21.9488689 -07:00 | 0226401105 | 022571111 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Standby Source to BART Colma (11780/11778) |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {1B002417-4970-4C77-BE6D-9A40B09E2BCA}
6243 | 4417 | {13EDC17C-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | DALY CITY | Bank 1 | CB 1107 | PGE\DMAL | 2017-05-17 13:19:03.1271904 -07:00 | 0226401107 | 022571115 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Standby Source to BART Daly City (5842/5840). |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {7ED4CFD3-FEAB-481C-8260-4403CB0455D8}
6244 | 4417 | {13EDC185-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | DALY CITY | Bank 1 | CB 1112 | PGE\C7CF | 2017-01-26 14:23:40.7792407 -08:00 | 0226401112 | 022600401 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {E4785E0B-E9E3-41C5-AE37-B66176F273A6}
6245 | 4418 | {13EDC1AD-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | DALY CITY | Bank 2 | CB 1102 | PGE\C7CF | 2017-01-26 14:31:22.9381282 -08:00 | 0226401102 | 022600403 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 592 | 12.92 | 12.79 | 570 | 12.44 | 12.32 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {0CDA65BA-86E2-4A84-8335-17BD368879EE}
6246 | 4415 | {FAC8C418-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE B | Bank 3 | CB 1109 | PGE\INM2 | 2017-01-26 14:34:09.4245298 -08:00 | 0822601109 | 024130401 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {B9AA5712-30D7-4F7C-AF99-AEEC0CF33965}
6247 | 4415 | {FAC8C421-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE B | Bank 3 | CB 1110 | PGE\INM2 | 2017-01-26 14:39:51.5547091 -08:00 | 0822601110 | 252811102 | 7 | 3 | 3 | 2 | 564 | 12.18 | 12.06 | 564 | 12.18 | 12.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 598 | 12.92 | 12.79 | 598 | 12.92 | 12.79 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {74B6F77F-318B-4A28-BBBD-0AC7AC1D717E}
6248 | 4418 | {13EDC1BE-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | DALY CITY | Bank 2 | CB 1108 (Non-SCADA) | PGE\C7CF | 2017-01-26 14:41:46.0141102 -08:00 | 0226401108 | 022550401 | 8 | 3 | 3 | 2 | 475 | 10.37 | 10.27 | 475 | 10.37 | 10.27 | 584 | 12.75 | 12.62 | 570 | 12.44 | 12.32 | 489 | 10.67 | 10.56 | 489 | 10.67 | 10.56 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {A8FEE0F4-1DA8-4A9B-A9C4-F3DA6E379AC5}
6249 | 4418 | {13EDC1C8-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | DALY CITY | Bank 2 | CB 1109 | PGE\DMAL | 2017-05-17 13:20:20.1187389 -07:00 | 0226401109 | 022101101 | 8 | 3 | 3 | 2 | 475 | 10.37 | 10.27 | 475 | 10.37 | 10.27 | 584 | 12.75 | 12.62 | 570 | 12.44 | 12.32 | 489 | 10.67 | 10.56 | 489 | 10.67 | 10.56 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Standby Source to BART Balboa (3680/3682). |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {224244EB-04BE-46F8-914E-8062FFCDD053}
6250 | 4418 | {13EDC1E7-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | DALY CITY | Bank 2 | CB 1110 | PGE\C7CF | 2017-01-26 14:47:01.9045849 -08:00 | 0226401110 | 022101102 | 8 | 3 | 3 | 2 | 475 | 10.37 | 10.27 | 475 | 10.37 | 10.27 | 584 | 12.75 | 12.62 | 570 | 12.44 | 12.32 | 489 | 10.67 | 10.56 | 489 | 10.67 | 10.56 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {11207480-9B62-408A-BBF8-F65FF74CCE91}
6252 | 4415 | {FAC8C438-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE B | Bank 3 | CB 1111 | PGE\INM2 | 2017-01-26 14:48:16.4740189 -08:00 | 0822601111 | 022101103 | 7 | 3 | 3 | 2 | 517 | 11.17 | 11.06 | 517 | 11.17 | 11.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 533 | 11.51 | 11.39 | 533 | 11.51 | 11.39 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {DD402273-98AB-484E-8A3D-B5551379725D}
6253 | 4419 | {13EDC1F4-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | DALY CITY | Bank 3 | CB 1101 | PGE\C7CF | 2017-01-26 14:52:53.2389412 -08:00 | 0226401101 | 022101104 | 8 | 3 | 3 | 2 | 492 | 10.74 | 10.63 | 467 | 10.19 | 10.09 | 554 | 12.09 | 11.97 | 526 | 11.48 | 11.37 | 557 | 12.16 | 12.04 | 532 | 11.61 | 11.49 | 598 | 13.05 | 12.92 | 568 | 12.4 | 12.28 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9599919A-3E8D-45A0-993B-92605F9E7D58}
6254 | 4415 | {FAC8C441-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE B | Bank 3 | CB 1112 | PGE\INM2 | 2017-01-26 14:54:18.5101810 -08:00 | 0822601112 | 022101106 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {56E952D0-2FD8-45FF-A2BB-85B4F43C65ED}
6255 | 4419 | {13EDC20C-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | DALY CITY | Bank 3 | CB 1103 | PGE\C7CF | 2017-01-26 14:58:15.3071347 -08:00 | 0226401103 | 083701101 | 8 | 3 | 3 | 2 | 360 | 7.86 | 7.78 | 360 | 7.86 | 7.78 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 371 | 8.1 | 8.02 | 371 | 8.1 | 8.02 | 412 | 8.99 | 8.9 | 412 | 8.99 | 8.9 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F3B46105-C74F-4A88-93C1-F80AA46B6485}
6256 | 4419 | {13EDC20F-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | DALY CITY | Bank 3 | CB 1106 | PGE\C7CF | 2017-01-26 15:08:50.6120777 -08:00 | 0226401106 | 083701104 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {CC739A63-C371-4807-B47B-C00A23B3167E}
6257 | 4415 | {FAC8C466-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE B | Bank 3 | CB 1113 | PGE\INM2 | 2017-01-26 15:04:40.1602992 -08:00 | 0822601113 | 083701105 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {3F0BEE70-5B97-400D-B577-899C83EA1787}
6258 | 4419 | {1A5E72EC-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | DALY CITY | Bank 3 | CB 1111 | PGE\C7CF | 2017-01-26 15:07:43.4858207 -08:00 | 0226401111 | 083701106 | 8 | 3 | 3 | 2 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 533 | 11.63 | 11.51 | 533 | 11.63 | 11.51 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {958B6A20-9240-4841-8C8A-274E61875B48}
6259 | 4420 | {FAC8C48E-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE B | Bank 4 | CB 1114 | PGE\INM2 | 2017-01-26 15:10:20.1799545 -08:00 | 0822601114 | 083701107 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {2135C7BC-9783-4613-BFAB-738B0068861A}
6260 | 4419 | {1A5E7319-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | DALY CITY | Bank 3 | CB 1115 | PGE\C7CF | 2017-01-26 15:11:43.6474445 -08:00 | 0226401115 | 083701108 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {1FB7FB47-A76A-4DF5-9806-619BCE65380F}
6261 | 4421 | {8A7A42E1-BBE9-11E6-93A9-D4BED91EFF1A} | PENINSULA | DALY CITY | UNIT SUB 401 | CB 401/2 (Non-SCADA) (Under Construction) | PGE\C7CF | 2017-01-26 15:19:20.8781733 -08:00 |  | 083701109 | 4 | 3 | 3 | 2 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 348 | 2.63 | 2.6 | 348 | 2.63 | 2.6 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 330 | 429 | 396 | 495 | {96E3A06C-764A-46BC-A8D9-A5F2340B3367}
6262 | 4420 | {FAC8C497-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SAN JOSE B | Bank 4 | CB 1115 | PGE\INM2 | 2017-01-27 08:05:11.3278543 -08:00 | 0822601115 | 083701110 | 7 | 3 | 3 | 2 | 180 | 3.89 | 3.85 | 180 | 3.89 | 3.85 | 180 | 3.89 | 3.85 | 180 | 3.89 | 3.85 | 180 | 3.89 | 3.85 | 180 | 3.89 | 3.85 | 180 | 3.89 | 3.85 | 180 | 3.89 | 3.85 | De-rated capability due to cable in metal conduits only good for 178 amps. |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {CB18218F-C9D0-4369-AC0E-8368AFA27A89}
6263 | 4170 | {1A5E7322-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | EAST GRAND | Bank 1 | CB 1102 | PGE\C7CF | 2017-01-27 09:03:47.1847917 -08:00 | 0225701102 | 083392102 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {E38A6189-91D7-4646-B39E-2743367C04C1}
6264 | 4170 | {1A5E732B-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | EAST GRAND | Bank 1 | CB 1104 | PGE\C7CF | 2017-01-27 09:06:58.3016168 -08:00 | 0225701104 | 083392106 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 592 | 12.92 | 12.79 | 592 | 12.92 | 12.79 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 599 | 13.07 | 12.94 | 599 | 13.07 | 12.94 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {77E0E0CE-AA97-455F-B5C1-8B98E3C0B61A}
6265 | 4170 | {1A5E733B-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | EAST GRAND | Bank 1 | CB 1109 | PGE\C7CF | 2017-01-27 09:10:55.1735352 -08:00 | 0225701109 | 022101107 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {1799378C-E3B4-4C83-A635-612462F492B2}
6266 | 4170 | {1A5E734B-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | EAST GRAND | Bank 1 | CB 1112 | PGE\C7CF | 2017-01-27 09:25:50.5412747 -08:00 | 0225701112 | 022101110 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9D60CD2D-5DA2-4BB8-91D0-CBEB42082D62}
6267 | 4422 | {105F7662-3F02-11E6-A936-80000BC6CD8D} | PENINSULA | EAST GRAND | BANK 2-3 (4kv) | CB 401 | PGE\C7CF | 2017-06-08 17:11:34.2425145 -07:00 | 022570401 | 083392107 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 433 | 3.28 | 3.25 | 433 | 3.28 | 3.25 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {BEE26325-8786-4B6D-9FCB-1ECBCD0A36A8}
6268 | 4422 | {1C8F0DA8-ADE1-11E6-A430-9CB70DEE0A5E} | PENINSULA | EAST GRAND | BANK 2-3 (4kv) | CB 402 (Non-SCADA) | PGE\C7CF | 2017-06-08 17:12:33.4464120 -07:00 |  | 022101105 | 4 | 3 | 3 | 2 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 433 | 3.28 | 3.25 | 433 | 3.28 | 3.25 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {3696E8D1-2E30-4B6B-A0C2-DF7744B04B72}
6269 | 4422 | {105F766C-3F02-11E6-A936-80000BC6CD8D} | PENINSULA | EAST GRAND | BANK 2-3 (4kv) | CB 404 | PGE\C7CF | 2017-01-27 15:10:32.6701786 -08:00 | 022570404 | 022101108 | 4 | 3 | 3 | 2 | 336 | 2.54 | 2.51 | 319 | 2.41 | 2.39 | 433 | 3.28 | 3.25 | 415 | 3.14 | 3.11 | 403 | 3.05 | 3.02 | 382 | 2.89 | 2.86 | 433 | 3.28 | 3.25 | 433 | 3.28 | 3.25 |  |  | FALSE | FALSE | 825 | 1073 | 990 | 1238 | {B027A4C4-DC56-4503-BDF7-6B87E14CC84F}
6270 | 4173 | {1A5E737A-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | EAST GRAND | Bank 4 | CB 1105 | PGE\C7CF | 2017-01-27 15:15:48.3538022 -08:00 | 0225701105 | 012130401 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 592 | 12.92 | 12.79 | 592 | 12.92 | 12.79 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 599 | 13.07 | 12.94 | 599 | 13.07 | 12.94 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B674EC4D-7348-44B4-B75C-A5739F7B1835}
6271 | 4173 | {1A5E738A-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | EAST GRAND | Bank 4 | CB 1106 | PGE\C7CF | 2017-01-27 15:19:43.0105064 -08:00 | 0225701106 | 012130402 | 8 | 3 | 3 | 2 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {4EF111EC-8431-4A67-80F4-08BCA2612804}
6272 | 4173 | {1A5E7393-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | EAST GRAND | Bank 4 | CB 1107 | PGE\C7CF | 2017-01-27 15:22:44.1588676 -08:00 | 0225701107 | 012130403 | 8 | 3 | 3 | 2 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 | 800 | 17.46 | 17.29 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B998BFAF-5595-404E-94A1-42AA76DAD2C3}
6274 | 4173 | {25CD63CC-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | EAST GRAND | Bank 4 | CB 1108 | PGE\C7CF | 2017-01-27 15:31:18.8685670 -08:00 | 0225701108 | 012130404 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {EB28749C-66AA-4C6C-8537-4ED895074385}
6275 | 4174 | {25CD63D8-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | EAST GRAND | Bank 5 | CB 1101 | PGE\C7CF | 2017-01-27 15:33:45.3535060 -08:00 | 0225701101 | 022101109 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 592 | 12.92 | 12.79 | 570 | 12.44 | 12.32 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 599 | 13.07 | 12.94 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {588360B8-4465-4E41-A3FF-15101F5AFDF5}
6276 | 4174 | {25CD63FD-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | EAST GRAND | Bank 5 | CB 1110 | PGE\C7CF | 2017-01-27 15:39:07.8231731 -08:00 | 0225701110 | 022101111 | 8 | 3 | 3 | 2 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 592 | 12.92 | 12.79 | 570 | 12.44 | 12.32 | 495 | 10.8 | 10.69 | 495 | 10.8 | 10.69 | 599 | 13.07 | 12.94 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {19B311CA-0390-43D4-A01D-93E9F57934FA}
6277 | 4174 | {25CD6414-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | EAST GRAND | Bank 5 | CB 1113 | PGE\C7CF | 2017-01-27 15:45:46.0625259 -08:00 | 0225701113 | 163801701 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {32A9CDA1-FC88-4AFD-9DC4-CF041A3BA0FA}
6278 | 4174 | {25CD641D-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | EAST GRAND | Bank 5 | CB 1114 | PGE\C7CF | 2017-01-27 15:53:57.3252750 -08:00 | 0225701114 | 163801703 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {478D68A8-4090-4227-8463-053E7149ADAE}
6280 | 4175 | {25CD6430-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | EAST GRAND | Bank 6 | CB 1103 | PGE\C7CF | 2017-01-27 15:58:04.7740612 -08:00 | 0225701103 | 022031102 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {A2EB67AC-8E97-4B0D-B8C5-B43DF46E7D94}
6281 | 4175 | {25CD6439-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | EAST GRAND | Bank 6 | CB 1111 | PGE\C7CF | 2017-01-27 16:02:05.7176057 -08:00 | 0225701111 | 022031105 | 8 | 3 | 3 | 2 | 615 | 13.42 | 13.29 | 615 | 13.42 | 13.29 | 718 | 15.67 | 15.51 | 718 | 15.67 | 15.51 | 627 | 13.68 | 13.54 | 627 | 13.68 | 13.54 | 732 | 15.98 | 15.82 | 732 | 15.98 | 15.82 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {D4F9E528-ED28-4AD1-A5D5-0C7C9023A427}
6282 | 4175 | {25CD6445-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | EAST GRAND | Bank 6 | CB 1115 | PGE\C7CF | 2017-01-27 16:04:56.1330981 -08:00 | 0225701115 | 022031106 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {4278FEC4-BA5E-4716-B770-2F0EEB82085C}
6283 | 4175 | {7DB16038-ADE1-11E6-A430-9CB70DEE0A5E} | PENINSULA | EAST GRAND | Bank 6 | CB BK2-3 (Under Construction) | PGE\C7CF | 2017-01-27 16:06:14.4768003 -08:00 |  | 022031107 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {AA30BE9C-7138-483F-960C-69EB8D6B43F9}
6284 | 4423 | {2C77CD10-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | WESTLAKE | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\C7CF | 2017-01-30 10:57:48.3102390 -08:00 | 022600401 | 022031109 | 4 | 3 | 3 | 2 | 175 | 1.32 | 1.31 | 175 | 1.32 | 1.31 | 204 | 1.54 | 1.52 | 204 | 1.54 | 1.52 | 179 | 1.35 | 1.34 | 179 | 1.35 | 1.34 | 208 | 1.57 | 1.55 | 208 | 1.57 | 1.55 |  |  | FALSE | FALSE | 230 | 230 | 230 | 230 | {CB46F2FA-A056-464F-93F4-D1A8BEE556F5}
6285 | 4424 | {2C77CD16-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | WESTLAKE | Bank 3 (Non SCADA) | CB 403 (Non-SCADA) | PGE\C7CF | 2017-01-30 10:59:54.2186461 -08:00 | 022600403 | 022031110 | 4 | 3 | 3 | 2 | 187 | 1.42 | 1.41 | 187 | 1.42 | 1.41 | 187 | 1.42 | 1.41 | 187 | 1.42 | 1.41 | 187 | 1.42 | 1.41 | 187 | 1.42 | 1.41 | 187 | 1.42 | 1.41 | 187 | 1.42 | 1.41 |  |  | FALSE | FALSE | 187 | 187 | 187 | 187 | {C68B1431-7165-4A71-9FD8-EC1C86222254}
6286 | 4426 | {25CD663F-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MENLO | Bank 1 | CB 401 | PGE\C7CF | 2017-01-30 11:37:34.6731361 -08:00 | 024130401 | 022031112 | 4 | 3 | 3 | 2 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 396 | 3 | 2.97 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 330 | 429 | 396 | 495 | {69EA12AF-76D9-46E9-A168-B61ECBEFF65F}
6287 | 4427 | {07171970-DE73-11E6-8DDC-9CB70D532D7F} | YOSEMITE | MERCED FALLS | Bank 2 | CB 1101 (Under Construction) | PGE\BXYD | 2017-01-30 13:13:07.2730833 -08:00 |  | 022031121 | 8 | 3 | 3 | 1 | 416 | 9.08 | 8.99 | 395 | 8.62 | 8.53 | 484 | 10.56 | 10.45 | 459 | 10.02 | 9.92 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 429 | 558 | 515 | 644 | {A3E4E3F9-118D-403E-980D-6BB814BE2BB3}
6289 | 4427 | {5E3AA908-671D-11E5-80CA-005056A729E5} | YOSEMITE | MERCED FALLS | Bank 2 | CB 1102 | PGE\BXYD | 2017-01-30 13:16:49.7773096 -08:00 | 2528101102 | 252931104 | 8 | 3 | 3 | 1 | 429 | 9.36 | 9.27 | 429 | 9.36 | 9.27 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 429 | 558 | 515 | 644 | {BC2FBACC-1D6D-4EE1-8BDA-0502341A00C8}
6290 | 4429 | {E0EEEA4F-3C97-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | 21ST AVENUE | BANK 1 | CB 401 (Non-SCADA) | PGE\DMAL | 2017-05-12 20:30:24.3036052 -07:00 | 022550401 | 102111101 | 3 | 3 | 3 | 2 | 319 | 2.3 | 2.28 | 319 | 2.3 | 2.28 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 383 | 2.76 | 2.73 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 319 | 414 | 383 | 478 | {B14D8377-B507-448A-86AF-95651166B5F0}
6291 | 4432 | {B7BBC24E-FDD4-11E5-9D37-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 1 | CB 1101 | PGE\DMAL | 2017-04-21 15:01:48.9957990 -07:00 | 0221001101 | 102111102 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 665 | 14.51 | 14.36 | 665 | 14.51 | 14.36 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 674 | 14.71 | 14.56 | 674 | 14.71 | 14.56 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {539679F4-5AB0-4D10-912F-FE80EF184263}
6294 | 4432 | {B7BBC251-FDD4-11E5-9D37-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 1 | CB 1102 | PGE\DMAL | 2017-05-17 13:08:25.2643262 -07:00 | 0221001102 | 253642104 | 7 | 3 | 3 | 2 | 360 | 7.78 | 7.7 | 360 | 7.78 | 7.7 | 400 | 8.64 | 8.55 | 400 | 8.64 | 8.55 | 371 | 8.01 | 7.93 | 371 | 8.01 | 7.93 | 412 | 8.9 | 8.81 | 412 | 8.9 | 8.81 | Standby Source to MUNI West Portal Building (1882/1880). |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3000 | {C1C69933-BC9C-49CF-B543-DFC4A442B4AD}
6296 | 4432 | {BE6D0FDB-FDD4-11E5-9D37-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 1 | CB 1103 | PGE\GxFf | 2017-01-30 15:57:57.2714276 -08:00 | 0221001103 | 012160401 | 8 | 3 | 3 | 1 | 434 | 9.47 | 9.38 | 434 | 9.47 | 9.38 | 486 | 10.61 | 10.5 | 486 | 10.61 | 10.5 | 492 | 10.74 | 10.63 | 492 | 10.74 | 10.63 | 546 | 11.92 | 11.8 | 546 | 11.92 | 11.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {1D6B9F51-EC5B-4167-A960-E6D0E63CF767}
6297 | 4432 | {BE6D0FDE-FDD4-11E5-9D37-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 1 | CB 1104 | PGE\DMAL | 2017-05-17 13:10:53.5295774 -07:00 | 0221001104 | 012160402 | 7 | 3 | 3 | 2 | 425 | 9.18 | 9.09 | 425 | 9.18 | 9.09 | 476 | 10.28 | 10.18 | 476 | 10.28 | 10.18 | 438 | 9.46 | 9.37 | 438 | 9.46 | 9.37 | 490 | 10.58 | 10.47 | 490 | 10.58 | 10.47 | Standby Source to MUNI Balboa Traction & MUNI Balboa Building (189/289_152F/252F). |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3000 | {66BA5AAD-BCD9-480B-A451-FD99F36266A8}
6298 | 4432 | {C148AA5D-334D-11E6-B38D-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 1 | CB 1106 (Under Construction) | PGE\DMAL | 2017-05-17 13:13:09.3301889 -07:00 | 0221001106 | 253671101 | 7 | 3 | 3 | 2 | 590 | 12.74 | 12.61 | 590 | 12.74 | 12.61 | 590 | 12.74 | 12.61 | 590 | 12.74 | 12.61 | 590 | 12.74 | 12.61 | 590 | 12.74 | 12.61 | 590 | 12.74 | 12.61 | 590 | 12.74 | 12.61 | Standby Source to Cow Palace (93313/48149) |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3000 | {F4D08EB6-B6B8-4103-8359-22813962FE03}
6299 | 4433 | {FAC8C51B-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | STONE | Bank 1 | CB 1101 | PGE\INM2 | 2017-02-01 08:13:50.5783010 -08:00 | 0837001101 | 253671102 | 7 | 3 | 3 | 2 | 582 | 12.57 | 12.44 | 582 | 12.57 | 12.44 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {1CFAB6CB-649D-4546-B13C-C5C0313DABAC}
6300 | 4433 | {FAC8C55D-D1CA-11E5-8ECE-9CB70D532D7F} | SAN JOSE | STONE | Bank 1 | CB 1104 | PGE\INM2 | 2017-02-01 08:15:53.4298760 -08:00 | 0837001104 | 253671103 | 7 | 3 | 3 | 2 | 582 | 12.57 | 12.44 | 582 | 12.57 | 12.44 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {3F6FA22E-EA8C-4C6B-8E3F-08D12DD399ED}
6301 | 4433 | {00C225CA-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | STONE | Bank 1 | CB 1105 | PGE\INM2 | 2017-02-01 08:19:02.8319042 -08:00 | 0837001105 | 083611104 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {A3C4F20B-AE03-4238-88E3-675C57DDA79C}
6303 | 4435 | {00C225D7-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | STONE | Bank 2 | CB 1106 (Non-SCADA) | PGE\INM2 | 2017-02-01 08:23:34.9149924 -08:00 | 0837001106 | 022871121 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {0C7C118E-49E8-4365-BC28-132B2EF6BB83}
6305 | 4435 | {00C225DA-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | STONE | Bank 2 | CB 1107 | PGE\INM2 | 2017-02-01 08:26:51.8519172 -08:00 | 0837001107 | 022871123 | 7 | 3 | 3 | 2 | 582 | 12.57 | 12.44 | 582 | 12.57 | 12.44 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {ADF3F063-42D5-452E-8B60-4D6AC1A1F0A5}
6306 | 4435 | {00C22631-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | STONE | Bank 2 | CB 1108 | PGE\INM2 | 2017-02-01 08:29:48.0093756 -08:00 | 0837001108 | 022871112 | 7 | 3 | 3 | 2 | 582 | 12.57 | 12.44 | 582 | 12.57 | 12.44 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {3C8C867A-99DD-4C7D-8758-2F49832F0E41}
6307 | 4435 | {00C22642-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | STONE | Bank 2 | CB 1109 | PGE\INM2 | 2017-02-01 08:32:05.6811406 -08:00 | 0837001109 | 022871116 | 7 | 3 | 3 | 2 | 582 | 12.57 | 12.44 | 582 | 12.57 | 12.44 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {243FD6C9-5CF0-4557-944E-1D15D4471F5D}
6308 | 4435 | {00C2266F-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | STONE | Bank 2 | CB 1110 | PGE\INM2 | 2017-02-01 08:34:04.0242578 -08:00 | 0837001110 | 022871119 | 7 | 3 | 3 | 2 | 582 | 12.57 | 12.44 | 582 | 12.57 | 12.44 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {8F8424D2-1FAD-4775-B712-D084E21AEA26}
6309 | 4436 | {00C2269B-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SWIFT | Bank 1 | CB 2102 | PGE\INM2 | 2017-02-01 09:01:41.1087022 -08:00 | 0833902102 | 022871120 | 11 | 3 | 3 | 2 | 468 | 17.51 | 17.33 | 468 | 17.51 | 17.33 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 552 | 20.65 | 20.44 | 552 | 20.65 | 20.44 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {11D877C0-9F67-4EA8-A45F-C3BC9BAA0F8E}
6310 | 4436 | {00C2270D-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SWIFT | Bank 1 | CB 2106 | PGE\INM2 | 2017-02-01 10:10:13.6490264 -08:00 | 0833902106 | 022871122 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1804 | {A432FD2E-6080-4D37-BD8F-ECF9CCCAF069}
6311 | 4432 | {BE6D0FE1-FDD4-11E5-9D37-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 1 | CB 1107 (Under Construction) | PGE\GxFf | 2017-02-01 10:13:47.5490247 -08:00 | 0221001107 | 022873411 | 8 | 3 | 3 | 1 | 503 | 10.98 | 10.87 | 503 | 10.98 | 10.87 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {346CAA0D-7A7F-4E22-85AB-1C634307404B}
6312 | 4432 | {C148AA60-334D-11E6-B38D-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 1 | CB 1110 | PGE\GxFf | 2017-02-01 10:21:17.2010983 -08:00 | 0221001110 | 013471128 | 8 | 3 | 3 | 1 | 566 | 12.35 | 12.23 | 515 | 11.24 | 11.13 | 600 | 13.09 | 12.96 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 397 conductor is after the first tie SW14091 |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {ECF7175B-7170-4BC9-A58E-DDA5FCD79204}
6313 | 4438 | {00C22760-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SWIFT | Bank 2 | CB 2107 | PGE\INM2 | 2017-02-01 10:40:26.7409992 -08:00 | 0833902107 | 013471130 | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 600 | 22.45 | 22.23 | 600 | 22.45 | 22.23 |  |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1600 | {BB1FA4A7-11B9-49D5-A9BF-EF7899B6DC71}
6314 | 4437 | {C6E877A7-FDD4-11E5-9D37-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 2 | CB 1105 | PGE\GxFf | 2017-02-01 10:49:06.8373229 -08:00 | 0221001105 | 013471125 | 8 | 3 | 3 | 1 | 434 | 9.47 | 9.38 | 434 | 9.47 | 9.38 | 486 | 10.61 | 10.5 | 486 | 10.61 | 10.5 | 560 | 12.22 | 12.1 | 560 | 12.22 | 12.1 | 598 | 13.05 | 12.92 | 598 | 13.05 | 12.92 |  | 45 MVA BK#2 | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {4792390A-F847-4036-95BD-D8552C63857F}
6315 | 4437 | {C6E877AD-FDD4-11E5-9D37-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 2 | CB 1108 | PGE\DMAL | 2017-05-17 13:15:13.0147673 -07:00 | 0221001108 | 013471119 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 594 | 12.83 | 12.7 | 594 | 12.83 | 12.7 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | Standby Source to BART Glen Park Station (606/616). |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3000 | {B0AA02C9-3D53-4138-BB23-93C9EFE769C8}
6316 | 4439 | {9059BE3C-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | ANTIOCH | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\WCL5 | 2017-02-02 11:22:25.8902693 -08:00 | 012130401 | 022031101 | 4 | 3 | 3 | 1 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 450 | 3.41 | 3.38 | 450 | 3.41 | 3.38 | Distribution Equipment for Antioch Sub will be removed in 2017 due to cutover of all station 4kV to 21kV. Actual Individual 3-phase induction 4kV feeder regs are 225kVA, 4330V, +-10%, 300 Amp (not selectable from EDPI component list). Closest regs with similar capabilities were selected above. |  | FALSE | FALSE | 990 | 1288 | 1189 | 1486 | {63DA67B0-7533-4DB1-AA7A-29B20C8775B5}
6318 | 4439 | {9059BE3F-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | ANTIOCH | Bank 1 (Non SCADA) | CB 402 (Non-SCADA) | PGE\WCL5 | 2017-02-02 11:35:33.0245150 -08:00 | 012130402 | 022031103 | 4 | 3 | 3 | 1 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 450 | 3.41 | 3.38 | 450 | 3.41 | 3.38 | Distribution Equipment for Antioch Sub will be removed in 2017 due to cutover of all station 4kV to 21kV. Actual Individual 3-phase induction 4kV feeder regs are 225kVA, 4330V, +-10%, 300 Amp (not selectable from EDPI component list). Closest regs with similar capabilities were selected above. |  | FALSE | FALSE | 990 | 1288 | 1189 | 1486 | {F6BB3074-EC3B-45B4-8CD8-83A1B072CE43}
6319 | 4439 | {9059BE42-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | ANTIOCH | Bank 1 (Non SCADA) | CB 403 (Non-SCADA) | PGE\WCL5 | 2017-02-02 11:36:01.5726980 -08:00 | 012130403 | 102701101 | 4 | 3 | 3 | 1 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 450 | 3.41 | 3.38 | 450 | 3.41 | 3.38 | Distribution Equipment for Antioch Sub will be removed in 2017 due to cutover of all station 4kV to 21kV. Actual Individual 3-phase induction 4kV feeder regs are 225kVA, 4330V, +-10%, 300 Amp (not selectable from EDPI component list). Closest regs with similar capabilities were selected above. |  | FALSE | FALSE | 990 | 1288 | 1189 | 1486 | {12AA96AD-DA0D-4B8D-945B-EADE23DBA619}
6320 | 4439 | {9059BE45-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | ANTIOCH | Bank 1 (Non SCADA) | CB 404 (Non-SCADA) | PGE\WCL5 | 2017-02-02 11:36:21.5096258 -08:00 | 012130404 | 102701102 | 4 | 3 | 3 | 1 | 300 | 2.27 | 2.25 | 300 | 2.27 | 2.25 | 390 | 2.95 | 2.92 | 390 | 2.95 | 2.92 | 360 | 2.72 | 2.69 | 360 | 2.72 | 2.69 | 450 | 3.41 | 3.38 | 450 | 3.41 | 3.38 | Distribution Equipment for Antioch Sub will be removed in 2017 due to cutover of all station 4kV to 21kV. Actual Individual 3-phase induction 4kV feeder regs are 225kVA, 4330V, +-10%, 300 Amp (not selectable from EDPI component list). Closest regs with similar capabilities were selected above. |  | FALSE | FALSE | 990 | 1288 | 1189 | 1486 | {3165392F-0DC7-4FFD-815E-0C5410860612}
6322 | 4440 | {C63DFD7D-BB3E-11E6-93A9-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 3 | CB 401 (Non-SCADA) | PGE\GxFf | 2017-02-03 13:55:21.6477964 -08:00 |  | 102701103 | 4 | 4 | 4 | 2 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 |  |  | FALSE | FALSE | 658 | 658 | 658 | 658 | {1C458F9F-9634-4276-9886-F792B868ACB3}
6324 | 4440 | {EF3735AD-BB3E-11E6-93A9-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 3 | CB 404 (Non-SCADA) | PGE\GxFf | 2017-02-03 14:35:57.5927478 -08:00 |  | 022031116 | 4 | 4 | 4 | 2 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 |  |  | FALSE | FALSE | 658 | 658 | 658 | 658 | {2745FFF7-1209-4D15-985D-C0DD948358CA}
6325 | 4454 | {D5ED0401-FDD4-11E5-9D37-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 4 | CB 1109 | PGE\GxFf | 2017-02-06 12:10:42.5905226 -08:00 | 0221001109 | 022031104 | 8 | 4 | 4 | 2 | 439 | 9.58 | 9.48 | 439 | 9.58 | 9.48 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 448 | 9.78 | 9.68 | 448 | 9.78 | 9.68 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {576CD265-DFB0-482E-AA71-3541F31CE4DB}
6326 | 4454 | {D5ED0404-FDD4-11E5-9D37-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 4 | CB 1111 | PGE\GxFf | 2017-02-06 13:00:59.7355794 -08:00 | 0221001111 | 022031108 | 8 | 4 | 4 | 2 | 566 | 12.35 | 12.23 | 550 | 12 | 11.88 | 600 | 13.09 | 12.96 | 550 | 12 | 11.88 | 600 | 13.09 | 12.96 | 550 | 12 | 11.88 | 600 | 13.09 | 12.96 | 550 | 12 | 11.88 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {96A86178-C96E-4ECE-BE74-40B44CF1FAD4}
6327 | 4454 | {3C51A2E4-BB3A-11E6-93A9-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 4 | CB HM-1 (Non-SCADA) | PGE\DMAL | 2017-02-23 15:00:49.3409873 -08:00 |  | 022031111 | 8 | 3 | 3 | 2 | 455 | 9.93 | 9.83 | 455 | 9.93 | 9.83 | 529 | 11.54 | 11.42 | 529 | 11.54 | 11.42 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 540 | 11.78 | 11.66 | 540 | 11.78 | 11.66 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {98A20E6D-7A41-4296-8187-2F53E4D0D369}
6328 | 4454 | {556A7B0E-BB3A-11E6-93A9-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 4 | CB HM-2 (Non-SCADA) | PGE\DMAL | 2017-02-23 15:00:30.1214177 -08:00 |  | 022031113 | 8 | 3 | 3 | 2 | 455 | 9.93 | 9.83 | 455 | 9.93 | 9.83 | 529 | 11.54 | 11.42 | 529 | 11.54 | 11.42 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 540 | 11.78 | 11.66 | 540 | 11.78 | 11.66 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {0BBB58A8-C43D-46AF-8F49-DCB10220C172}
6330 | 4454 | {665DD770-BB3A-11E6-93A9-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 4 | CB HM-3 (Non-SCADA) | PGE\DMAL | 2017-02-23 15:00:14.5991192 -08:00 |  | 022031114 | 8 | 3 | 3 | 2 | 455 | 9.93 | 9.83 | 455 | 9.93 | 9.83 | 529 | 11.54 | 11.42 | 529 | 11.54 | 11.42 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 540 | 11.78 | 11.66 | 540 | 11.78 | 11.66 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {4FBB6344-ED14-4449-A15E-FE3E5D3F5BF5}
6331 | 4455 | {86BD03C6-8B36-11E6-841B-D4BED91EFF1A} | STOCKTON | RIPON | Bank 1 | CB 1701 | PGE\T1SI | 2017-02-06 14:47:26.2213870 -08:00 | 163801701 | 022031115 | 23 | 3 | 3 | 1 | 515 | 15.34 | 15.19 | 489 | 14.57 | 14.42 | 578 | 17.22 | 17.05 | 549 | 16.36 | 16.2 | 600 | 17.87 | 17.69 | 570 | 16.98 | 16.81 | 600 | 17.87 | 17.69 | 600 | 17.87 | 17.69 |  |  | FALSE | FALSE | 1510 | 1963 | 1812 | 2265 | {ED037BF7-5D2D-4194-80E7-3B135230F7E0}
6332 | 4455 | {F6F3AEFD-3CBE-11E6-B38D-D4BED91EFF1A} | STOCKTON | RIPON | Bank 1 | CB 1703 | PGE\T1SI | 2017-02-06 14:54:17.7261004 -08:00 | 163801703 | 022031117 | 23 | 3 | 3 | 1 | 515 | 15.34 | 15.19 | 489 | 14.57 | 14.42 | 578 | 17.22 | 17.05 | 549 | 16.36 | 16.2 | 600 | 17.87 | 17.69 | 570 | 16.98 | 16.81 | 600 | 17.87 | 17.69 | 600 | 17.87 | 17.69 |  |  | FALSE | FALSE | 1510 | 1963 | 1812 | 2265 | {10DC6928-E00C-4079-858A-E077B40F872C}
6333 | 4456 | {C12F15F2-BB3A-11E6-93A9-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 9 | CB HL-1 | PGE\DMAL | 2017-02-23 15:02:38.3714840 -08:00 |  | 022031118 | 8 | 3 | 3 | 2 | 455 | 9.93 | 9.83 | 455 | 9.93 | 9.83 | 529 | 11.54 | 11.42 | 529 | 11.54 | 11.42 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 540 | 11.78 | 11.66 | 540 | 11.78 | 11.66 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {D9ACC719-FDA7-4CD7-874A-35EB3FBBD4F5}
6334 | 4456 | {D1EBD9F2-BB3A-11E6-93A9-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 9 | CB HL-2 (Under Construction) | PGE\DMAL | 2017-02-23 15:03:12.1461335 -08:00 |  | 102812101 | 8 | 3 | 3 | 2 | 455 | 9.93 | 9.83 | 455 | 9.93 | 9.83 | 529 | 11.54 | 11.42 | 529 | 11.54 | 11.42 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 540 | 11.78 | 11.66 | 540 | 11.78 | 11.66 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {F9B8928D-12E2-4987-99CE-175C33D413F5}
6335 | 4456 | {DB6A2DD8-BB3A-11E6-93A9-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 9 | CB HL-3 (Under Construction) | PGE\DMAL | 2017-02-23 15:03:50.6632742 -08:00 |  | 102601101 | 8 | 3 | 3 | 2 | 455 | 9.93 | 9.83 | 455 | 9.93 | 9.83 | 529 | 11.54 | 11.42 | 529 | 11.54 | 11.42 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 540 | 11.78 | 11.66 | 540 | 11.78 | 11.66 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {62AD42A8-0377-446E-B869-560FDAE6A6D5}
6336 | 4456 | {1C7073CB-BB3F-11E6-93A9-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 9 | CB HL-4 (Under Construction) | PGE\DMAL | 2017-02-23 15:04:19.3054250 -08:00 |  | 103330401 | 8 | 3 | 3 | 2 | 455 | 9.93 | 9.83 | 455 | 9.93 | 9.83 | 529 | 11.54 | 11.42 | 529 | 11.54 | 11.42 | 464 | 10.13 | 10.03 | 464 | 10.13 | 10.03 | 540 | 11.78 | 11.66 | 540 | 11.78 | 11.66 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {C76E0342-8D7E-49BB-BB17-DFAFDE30E9B4}
6337 | 4442 | {D74FE73D-BB3E-11E6-93A9-D4BED91EFF1A} | PENINSULA | SF H MARTIN | BANK 5 | CB 402 (Non-SCADA) | PGE\GxFf | 2017-02-07 15:45:11.8869855 -08:00 |  | 103330402 | 4 | 3 | 3 | 1 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 3 single phase regulators. Isummer emerg 380 Amps;I winter norm 356 Amps; I winter emergency-428 Amps |  | FALSE | FALSE | 658 | 658 | 658 | 658 | {E4CBE560-D12E-4FA1-B7C4-F0D40CBD58B3}
6338 | 4459 | {5A01185D-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 1 | CB 1102 | PGE\DMAL | 2017-02-08 11:44:19.9022141 -08:00 | 0220301102 | 103331103 | 7 | 3 | 3 | 2 | 427 | 9.22 | 9.13 | 405 | 8.75 | 8.66 | 474 | 10.24 | 10.14 | 450 | 9.72 | 9.62 | 440 | 9.5 | 9.41 | 418 | 9.03 | 8.94 | 488 | 10.54 | 10.43 | 463 | 10 | 9.9 |  |  | FALSE | FALSE | 3472 | 3750 | 3750 | 3750 | {514790E1-2916-4638-87BB-25D5796009DD}
6339 | 4459 | {5A011860-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 1 | CB 1105 | PGE\DMAL | 2017-02-08 12:33:17.1858711 -08:00 | 0220301105 | 103331104 | 7 | 3 | 3 | 2 | 490 | 10.58 | 10.47 | 467 | 10.09 | 9.99 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 |  |  | FALSE | FALSE | 3472 | 3750 | 3750 | 3750 | {D1523CB5-2EE4-4B95-9073-EB5767E1E86A}
6340 | 4459 | {5A011863-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 1 | CB 1106 (Under Construction) | PGE\DMAL | 2017-02-08 12:37:16.1185343 -08:00 | 0220301106 | 022071101 | 7 | 3 | 3 | 2 | 383 | 8.27 | 8.19 | 383 | 8.27 | 8.19 | 425 | 9.18 | 9.09 | 425 | 9.18 | 9.09 | 394 | 8.51 | 8.42 | 394 | 8.51 | 8.42 | 438 | 9.46 | 9.37 | 438 | 9.46 | 9.37 |  |  | FALSE | FALSE | 3472 | 3750 | 3750 | 3750 | {5A8C3770-97D0-4BDA-AC80-2D2A2D592856}
6341 | 4459 | {5A011869-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 1 | CB 1107 | PGE\DMAL | 2017-05-16 11:09:25.9616962 -07:00 | 0220301107 | 022071103 | 7 | 3 | 3 | 2 | 490 | 10.58 | 10.47 | 467 | 10.09 | 9.99 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | Feeder will become standby to SF General Hospital (A1116) after reconfiguration project. |  | FALSE | FALSE | 3472 | 3750 | 3750 | 3750 | {F44E7E22-B974-4AAA-AEA2-29C40970BEF6}
6342 | 4459 | {5A01186C-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 1 | CB 1109 | PGE\DMAL | 2017-05-17 09:58:54.7984676 -07:00 | 0220301109 | 022071105 | 7 | 3 | 3 | 2 | 492 | 10.63 | 10.52 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | Standby Source to Sutro Tower T895_T897. Normal Source to T896_T898. Internal Customer ATS. |  | FALSE | FALSE | 3472 | 3750 | 3750 | 3750 | {FE238299-4F62-40C5-947F-F4E9767526B6}
6343 | 4459 | {5A01187B-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 1 | CB 1110 | PGE\DMAL | 2017-03-08 15:48:09.1632620 -08:00 | 0220301110 | 022071107 | 7 | 3 | 3 | 2 | 467 | 10.09 | 9.99 | 467 | 10.09 | 9.99 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 481 | 10.39 | 10.29 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 |  |  | FALSE | FALSE | 3472 | 3750 | 3750 | 3750 | {657ADD97-13A5-40A1-AF48-DBB5166DDBF6}
6344 | 4459 | {5A011887-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 1 | CB 1112 | PGE\DMAL | 2017-02-08 14:28:58.0112549 -08:00 | 0220301112 | 103481101 | 7 | 3 | 3 | 2 | 490 | 10.58 | 10.47 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 |  |  | FALSE | FALSE | 3472 | 3750 | 3750 | 3750 | {C151CEF9-4262-4354-9369-D5D5F83D6DF7}
6345 | 4459 | {605EFD52-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 1 | CB 1121 | PGE\DMAL | 2017-03-08 15:49:41.7658800 -08:00 | 022031121 | 103481102 | 7 | 3 | 3 | 2 | 517 | 11.17 | 11.06 | 491 | 10.6 | 10.49 | 604 | 13.05 | 12.92 | 573 | 12.38 | 12.26 | 527 | 11.38 | 11.27 | 500 | 10.8 | 10.69 | 616 | 13.3 | 13.17 | 585 | 12.64 | 12.51 |  |  | FALSE | FALSE | 3472 | 3750 | 3750 | 3750 | {AB77FE2D-4B1E-4126-9A58-9D878F1CBBAA}
6346 | 2713 | {5447F99D-EE4E-11E6-B1DB-20689D5FE5C8} | KERN | TEJON | Bank 1 (Non SCADA) | CB 1104 (Non-SCADA) | PGE\J2T4 | 2017-02-08 15:23:08.7785024 -08:00 | 2529301104 | 103581101 | 8 | 4 | 4 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 859 | 1116 | 1030 | 1288 | {02BBFE9D-4A56-4D8D-81DC-D731FEA84C93}
6348 | 4470 | {80989061-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CAPAY | Bank 1 | CB 1101 | PGE\SDK6 | 2017-02-09 12:18:58.1955724 -08:00 | 1021101101 | 102491101 | 8 | 3 | 3 | 1 | 425 | 9.28 | 9.19 | 173 | 3.78 | 3.74 | 425 | 9.28 | 9.19 | 200 | 4.36 | 4.32 | 425 | 9.28 | 9.19 | 252 | 5.5 | 5.45 | 425 | 9.28 | 9.19 | 269 | 5.87 | 5.81 | Operational Circuit Capability is for when relieving 1102 through SW 8355 . |  | TRUE | FALSE | 458 | 595 | 549 | 687 | {3FEBB21A-2EC9-4E26-88DD-1E11A493BD4B}
6349 | 4470 | {8098906A-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CAPAY | Bank 1 | CB 1102 | PGE\SDK6 | 2017-02-09 12:18:43.6872934 -08:00 | 1021101102 | 102491102 | 8 | 3 | 3 | 1 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 | 425 | 9.28 | 9.19 |  |  | TRUE | FALSE | 458 | 595 | 549 | 687 | {2B71F0EC-9A50-458F-844B-71EEBBA50DEA}
6350 | 2767 | {013CC213-5FFF-11E6-9BE4-80000BC6CD8D} | KERN | POSO MOUNTAIN | Bank 2 | CB 2104 | PGE\JCS9 | 2017-05-22 09:47:46.8958009 -07:00 | 253642104 | 102491103 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {98286233-4F72-4F11-8D69-A71F9A505DAE}
6351 | 4471 | {569672FA-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | PITTSBURG | Bank 1 | CB 401 (Non-SCADA) | PGE\WCL5 | 2017-02-09 15:00:03.2113864 -08:00 | 012160401 | 103331101 | 4 | 3 | 3 | 1 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 661 | 860 | 794 | 992 | {55F7EAFC-BB8C-49EC-B73E-E4345543D72D}
6352 | 4471 | {569672FD-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | PITTSBURG | Bank 1 | CB 402 (Non-SCADA) | PGE\WCL5 | 2017-02-09 15:02:11.8202596 -08:00 | 012160402 | 102491105 | 4 | 3 | 3 | 1 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 661 | 860 | 794 | 992 | {143A48CE-0955-42F7-A862-7500505A59BD}
6354 | 4473 | {2717D600-A5BE-11E5-A1F0-D4BED91EFF1A} | YOSEMITE | PANOCHE | Bank 3 | CB 1101 (Under Construction) | PGE\BXYD | 2017-02-09 15:16:57.2620870 -08:00 | 2536701101 | 103331102 | 8 | 3 | 3 | 1 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 | 450 | 9.82 | 9.72 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {5F276B2E-690E-49F1-9900-7D7C9777FB81}
6355 | 4473 | {2717D603-A5BE-11E5-A1F0-D4BED91EFF1A} | YOSEMITE | PANOCHE | Bank 3 | CB 1102 (Under Construction) | PGE\BXYD | 2017-02-09 15:20:25.4168899 -08:00 | 2536701102 | 102491106 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {0827B72A-D303-404E-971D-D2B79911BFC0}
6356 | 4473 | {2717D606-A5BE-11E5-A1F0-D4BED91EFF1A} | YOSEMITE | PANOCHE | Bank 3 | CB 1103 (Under Construction) | PGE\BXYD | 2017-02-09 15:43:14.5616191 -08:00 | 2536701103 | 103261101 | 8 | 3 | 3 | 1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 | 375 | 8.18 | 8.1 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {2CA862CF-374D-4508-AE88-EA86132CB028}
6357 | 4460 | {9ED2E39D-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | BRITTON | Bank 1 | CB 1104 | PGE\MSJ9 | 2017-04-20 17:55:59.8086872 -07:00 | 0836101104 | 103261102 | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | SW 10933 - 8 hour emergency rating of 800 Amps Relay Minimum Phase: 720A T 6 L 2.5 CT Ratio: 600:5 To Operate Ground: 185A T 1.5 L 2 Ammeter Range 0 to 100 |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {7FAB143A-9369-4CAF-BBED-0C3BEE07A604}
6374 | 4474 | {6658559D-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 1 (Banks 11, 15, 16) | CB 1121 | PGE\DMAL | 2017-05-17 09:50:21.2989928 -07:00 | 0228701121 | 103261103 | 7 | 3 | 3 | 2 | 454 | 9.81 | 9.71 | 454 | 9.81 | 9.71 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 468 | 10.11 | 10.01 | 468 | 10.11 | 10.01 | 566 | 12.22 | 12.1 | 566 | 12.22 | 12.1 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. Standby to New Transbay Terminal Center Primary Service1 (Device 573918) on Minna/2nd Street. Normal Source to Building Primary Service2 (Device 285650) on Natoma/1st Street. Internal customer ATS. |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {39C20AF2-CA6B-4CBA-8AD5-B74BB8D01AE3}
6375 | 4474 | {665855A0-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 1 (Banks 11, 15, 16) | CB 1123 | PGE\DMAL | 2017-03-09 12:55:15.3044224 -08:00 | 022871123 | 103311101 | 7 | 3 | 3 | 2 | 462 | 9.98 | 9.88 | 462 | 9.98 | 9.88 | 538 | 11.62 | 11.5 | 538 | 11.62 | 11.5 | 471 | 10.17 | 10.07 | 471 | 10.17 | 10.07 | 549 | 11.86 | 11.74 | 549 | 11.86 | 11.74 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {E6159D92-B37C-459A-A19D-B9907C32ACE4}
6376 | 4474 | {83A0C16C-BD97-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 1 (Banks 11, 15, 16) | CB CAP BK 1-2 STA BK-1 (Non-SCADA) | PGE\DMAL | 2017-02-22 13:52:21.7919892 -08:00 |  | 103311102 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {F18C0588-3FCA-48D7-B287-436BF0BE8820}
6377 | 4474 | {94428939-BD97-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 1 (Banks 11, 15, 16) | CB CAP BK 6-7 (Non-SCADA) | PGE\DMAL | 2017-02-22 13:52:54.3498153 -08:00 |  | 102361101 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {BDB22B2B-00D9-4CCA-9721-1BB26355E281}
6378 | 4474 | {D135E721-BD97-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 1 (Banks 11, 15, 16) | CB D-E TIE /12 (Non-SCADA) | PGE\DMAL | 2017-02-22 13:40:33.6787719 -08:00 |  | 102931101 | 7 | 3 | 3 | 2 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {9BB2F1C0-D3B1-4C5B-B3FB-A255735F077D}
6379 | 4474 | {E15471D2-BD97-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 1 (Banks 11, 15, 16) | CB E-F TIE/12 (Non-SCADA) | PGE\DMAL | 2017-02-22 13:41:23.0693217 -08:00 |  | 102931102 | 7 | 3 | 3 | 2 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {887676BA-2C6B-457B-8355-F4756332087D}
6380 | 4474 | {F2C48B67-BD97-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 1 (Banks 11, 15, 16) | CB F-G TIE/12 (Non-SCADA) | PGE\DMAL | 2017-03-09 13:59:17.5959112 -08:00 |  | 102931103 | 7 | 3 | 3 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {760EF40A-588A-4E0F-83CF-1D82B85DB353}
6381 | 4475 | {ADBF638E-BD97-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 2 (Banks 12, 13, 14) | CB CAP BK 3-5 (Non-SCADA) | PGE\DMAL | 2017-02-22 14:31:39.2625243 -08:00 |  | 210102127 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {267CDCC7-223A-4E48-BB4E-BCA3555657F4}
6382 | 4475 | {2B9EEAD5-BD98-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 2 (Banks 12, 13, 14) | CB D-E TIE/22 (Non-SCADA) | PGE\DMAL | 2017-02-22 13:53:55.1909853 -08:00 |  | 103491101 | 7 | 3 | 3 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {4419F80D-3258-416E-BBBF-3743EC093358}
6383 | 4475 | {143F801C-BD98-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 2 (Banks 12, 13, 14) | CB E-F TIE/22 (Non-SCADA) | PGE\DMAL | 2017-02-22 13:55:08.8712022 -08:00 |  | 103491102 | 7 | 3 | 3 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {04A059A0-685D-44FD-9682-ABDC766E51EB}
6384 | 4475 | {06CC9EEB-BD98-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 2 (Banks 12, 13, 14) | CB F-G TIE/22 (Non-SCADA) | PGE\DMAL | 2017-02-22 13:56:10.2583827 -08:00 |  | 103721101 | 7 | 3 | 3 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {55E2DFBB-9FFA-49BC-85EC-FA57F3C1E0F1}
6385 | 4475 | {15319B5B-3D5B-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 2 (Banks 12, 13, 14) | CB 1112 | PGE\DMAL | 2017-03-15 12:05:33.2957009 -07:00 | 0228701112 | 152331108 | 7 | 3 | 3 | 2 | 446 | 9.63 | 9.53 | 446 | 9.63 | 9.53 | 538 | 11.62 | 11.5 | 538 | 11.62 | 11.5 | 459 | 9.91 | 9.81 | 459 | 9.91 | 9.81 | 549 | 11.86 | 11.74 | 549 | 11.86 | 11.74 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {80FE50AA-1DF3-4070-B97E-BBE53D04820D}
6386 | 4475 | {3E8C273D-687B-11E6-9BE4-80000BC6CD8D} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 2 (Banks 12, 13, 14) | CB 1116 | PGE\DMAL | 2017-03-15 12:05:56.9807513 -07:00 | 022871116 | 152331107 | 7 | 3 | 3 | 2 | 483 | 10.43 | 10.33 | 483 | 10.43 | 10.33 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 493 | 10.65 | 10.54 | 493 | 10.65 | 10.54 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {104A4CAD-9F66-4267-BFFB-20AF6424DB1C}
6387 | 4475 | {2262FF25-3D5B-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 2 (Banks 12, 13, 14) | CB 1119 | PGE\DMAL | 2017-05-16 12:08:45.1833977 -07:00 | 0228701119 | 152331105 | 7 | 3 | 3 | 2 | 480 | 10.37 | 10.27 | 480 | 10.37 | 10.27 | 559 | 12.07 | 11.95 | 559 | 12.07 | 11.95 | 490 | 10.58 | 10.47 | 490 | 10.58 | 10.47 | 570 | 12.31 | 12.19 | 570 | 12.31 | 12.19 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. Standby Source to Muni Downtown Station (ATS 252B_152B). |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {7025B749-80B4-4662-8D49-EC70C5BFD627}
6388 | 4475 | {66585579-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 2 (Banks 12, 13, 14) | CB 1120 | PGE\DMAL | 2017-03-09 12:30:14.2747570 -08:00 | 0228701120 | 022070406 | 7 | 3 | 3 | 2 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | Branch A_SW-14906_600EPR-AL_1ELC: SN=516_SE=605_WN=526_WE=617amp. Branch B_SW-16016_500EPR-Cu_1ELC: SN=513_SE=601_WN=523_WE=613amp. Parallel: 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {2E9F5C9D-6FE4-4A69-B2FD-389C669AC401}
6389 | 4475 | {6658557C-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 2 (Banks 12, 13, 14) | CB 1122 | PGE\DMAL | 2017-03-09 12:59:32.0853604 -08:00 | 0228701122 | 022070407 | 7 | 3 | 3 | 2 | 462 | 9.98 | 9.88 | 462 | 9.98 | 9.88 | 538 | 11.62 | 11.5 | 538 | 11.62 | 11.5 | 471 | 10.17 | 10.07 | 471 | 10.17 | 10.07 | 549 | 11.86 | 11.74 | 549 | 11.86 | 11.74 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {F5705062-04DA-4509-A672-E668E41D5215}
6390 | 4483 | {4F789F92-BD98-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 1 (Banks 1, 5) | CB D-E TIE/32 (Non-SCADA) | PGE\DMAL | 2017-02-22 14:58:29.4942897 -08:00 |  | 022070408 | 13 | 3 | 3 | 2 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {62BCE222-15BF-43E7-A376-0795675A8AD0}
6391 | 4483 | {614A63A7-BD98-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 1 (Banks 1, 5) | CB E-F TIE/32 (Non-SCADA) | PGE\DMAL | 2017-02-22 14:59:06.9506100 -08:00 |  | 022871103 | 13 | 3 | 3 | 2 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {19D6AA09-E1DB-4577-8DB3-6EB74EDD2D7C}
6392 | 4484 | {75191633-BD98-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 2 (Banks 2, 3) | CB D-E TIE /42 (Non-SCADA) | PGE\DMAL | 2017-02-22 15:00:37.7599563 -08:00 |  | 022871106 | 13 | 3 | 3 | 2 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {5BEB031A-FA8F-4716-B9C7-261FC89F8F70}
6393 | 4484 | {85ECEBC8-BD98-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 2 (Banks 2, 3) | CB E-F TIE /42 (Non-SCADA) | PGE\DMAL | 2017-02-22 15:01:08.1025398 -08:00 |  | 022871110 | 13 | 3 | 3 | 2 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 | 3000 | 179.27 | 177.48 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {25581585-BDD2-4DA0-A770-3C48EC39486B}
6394 | 4484 | {20B37FF9-BD97-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 2 (Banks 2, 3) | CB CAP 33 (Non-SCADA) | PGE\DMAL | 2017-02-22 15:02:08.7097053 -08:00 |  | 022221101 | 13 | 3 | 3 | 2 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {385DF8A9-4E68-4F2A-A09D-5668D9069003}
6395 | 4484 | {2ABB0C42-BD97-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 2 (Banks 2, 3) | CB CAP 34 (Non-SCADA) | PGE\DMAL | 2017-02-22 15:02:56.3998224 -08:00 |  | 022221102 | 13 | 3 | 3 | 2 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {640A6B02-C37F-4944-A356-FA10A96FC2D4}
6396 | 4483 | {F0E30C76-BD96-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 1 (Banks 1, 5) | CB CAP 21 (Non-SCADA) | PGE\DMAL | 2017-02-22 15:04:09.5340288 -08:00 |  | 022221103 | 13 | 3 | 3 | 2 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {9B921606-2CAC-47CB-8C9F-435DC265DDAF}
6397 | 4483 | {03BEA639-BD97-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 1 (Banks 1, 5) | CB CAP 32 (Non-SCADA) | PGE\DMAL | 2017-02-22 15:04:53.1524676 -08:00 |  | 022221104 | 13 | 3 | 3 | 2 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 | 800 | 47.8 | 47.32 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {D9756AB6-782C-416C-A8E5-D3CD4FCF20BF}
6398 | 4484 | {665855A6-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 2 (Banks 2, 3) | CB 3411 | PGE\DMAL | 2017-03-15 13:13:10.6294802 -07:00 | 022873411 | 022221105 | 13 | 3 | 3 | 2 | 446 | 26.65 | 26.38 | 446 | 26.65 | 26.38 | 549 | 32.81 | 32.48 | 549 | 32.81 | 32.48 | 459 | 27.43 | 27.16 | 459 | 27.43 | 27.16 | 556 | 33.22 | 32.89 | 556 | 33.22 | 32.89 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {20EA8DAE-A617-42F2-971E-DDBC1EB3A251}
6399 | 4483 | {6CFE07C7-917E-11E6-841B-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 1 (Banks 1, 5) | CB 3412 | PGE\DMAL | 2017-03-15 13:07:20.2343496 -07:00 |  | 022221106 | 13 | 3 | 3 | 2 | 446 | 26.65 | 26.38 | 446 | 26.65 | 26.38 | 549 | 32.81 | 32.48 | 549 | 32.81 | 32.48 | 459 | 27.43 | 27.16 | 459 | 27.43 | 27.16 | 556 | 33.22 | 32.89 | 556 | 33.22 | 32.89 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {2AEC85ED-C228-4D0B-BBD5-137E902727A1}
6401 | 3851 | {0D3AE14B-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | RICHMOND R | Bank 3 | CB 1128 | PGE\C7CF | 2017-05-24 10:09:20.5660252 -07:00 | 0134701128 | 022221107 | 7 | 3 | 3 | 2 | 467 | 10.09 | 9.99 | 467 | 10.09 | 9.99 | 523 | 11.3 | 11.19 | 523 | 11.3 | 11.19 | 481 | 10.39 | 10.29 | 481 | 10.39 | 10.29 | 539 | 11.64 | 11.52 | 539 | 11.64 | 11.52 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {7B294480-E4E1-4D40-B8E3-7347ED32D320}
6402 | 3851 | {0D3AE160-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | RICHMOND R | Bank 3 | CB 1130 | PGE\C7CF | 2017-05-24 10:28:07.0123269 -07:00 | 0134701130 | 102021101 | 7 | 3 | 3 | 2 | 445 | 9.61 | 9.51 | 445 | 9.61 | 9.51 | 494 | 10.67 | 10.56 | 494 | 10.67 | 10.56 | 458 | 9.89 | 9.79 | 458 | 9.89 | 9.79 | 509 | 10.99 | 10.88 | 509 | 10.99 | 10.88 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {CCC291E7-701B-45BC-9221-1DA0D7C4B19D}
6406 | 3850 | {00DE4D59-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | RICHMOND R | Bank 2 | CB 1125 | PGE\C7CF | 2017-07-31 09:09:11.0435825 -07:00 | 0134701125 | 022801101 | 7 | 3 | 3 | 2 | 360 | 7.78 | 7.7 | 360 | 7.78 | 7.7 | 400 | 8.64 | 8.55 | 400 | 8.64 | 8.55 | 371 | 8.01 | 7.93 | 371 | 8.01 | 7.93 | 412 | 8.9 | 8.81 | 412 | 8.9 | 8.81 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {7932A96C-DBD9-44FC-A822-B39DBE3BFBFD}
6407 | 3851 | {06D72FDE-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | RICHMOND R | Bank 3 | CB 1119 | PGE\C7CF | 2017-05-24 09:56:21.2430477 -07:00 | 0134701119 | 022801102 | 7 | 3 | 3 | 2 | 446 | 9.63 | 9.53 | 446 | 9.63 | 9.53 | 549 | 11.86 | 11.74 | 549 | 11.86 | 11.74 | 459 | 9.91 | 9.81 | 459 | 9.91 | 9.81 | 556 | 12.01 | 11.89 | 556 | 12.01 | 11.89 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {371AA8A3-BD25-4ED4-BA2D-422D9D2F46D4}
6409 | 1076 | {0BB790C7-D9B6-11E6-8DDC-9CB70D532D7F} | EAST BAY | EL CERRITO G | Bank 4 | CB BANK 4/2E (Non-SCADA) | PGE\MUSF | 2017-03-02 15:46:44.8765606 -08:00 |  | 022801103 | 8 | 3 | 3 | 2 | 2749 | 59.99 | 59.39 | 2749 | 59.99 | 59.39 | 3000 | 65.47 | 64.82 | 2850 | 62.2 | 61.58 | 3000 | 65.47 | 64.82 | 2850 | 62.2 | 61.58 | 3000 | 65.47 | 64.82 | 2850 | 62.2 | 61.58 |  |  | FALSE | FALSE | 2749 | 3574 | 3299 | 4123 | {1D9E03B0-1832-439B-B3F8-FC32D15B061F}
6410 | 4486 | {07991CDA-B71A-11E6-B077-D4BED91EFF1A} | SAN FRANCISCO | POTRERO (SF A) | 12kV Bus 1 | CB IJ/12 | PGE\DMAL | 2017-03-28 15:32:14.5119929 -07:00 |  | 022801104 | 7 | 3 | 3 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {E11B1671-0A59-4A76-8B60-EBCC62D01993}
6412 | 4488 | {15F96092-B71A-11E6-B077-D4BED91EFF1A} | SAN FRANCISCO | POTRERO (SF A) | 12kV Bus 2 | CB IJ/22 | PGE\DMAL | 2017-03-28 15:32:36.8241399 -07:00 |  | 022801105 | 7 | 3 | 3 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {AA4BBFB7-7291-487A-A109-9C689FA0C0F3}
6413 | 4458 | {605EFD58-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 10 | CB 1101 | PGE\DMAL | 2017-03-08 14:06:34.2258952 -08:00 | 0220301101 | 022801106 | 7 | 3 | 3 | 2 | 445 | 9.61 | 9.51 | 445 | 9.61 | 9.51 | 494 | 10.67 | 10.56 | 475 | 10.26 | 10.16 | 458 | 9.89 | 9.79 | 458 | 9.89 | 9.79 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 |  |  | FALSE | FALSE | 3472 | 3750 | 3750 | 3750 | {7683E262-F95C-4D0F-9F30-F1F85E05B1CD}
6414 | 4458 | {605EFD64-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 10 | CB 1103 | PGE\DMAL | 2017-03-08 14:07:57.2639968 -08:00 | 0220301103 | 022801112 | 7 | 3 | 3 | 2 | 492 | 10.63 | 10.52 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 |  |  | FALSE | FALSE | 3472 | 3750 | 3750 | 3750 | {C6EF9638-95B5-481D-A321-D1F0634CF8D9}
6415 | 4485 | {9A705E36-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | ORLAND B | Bank 1 | CB 1101 | PGE\GSD5 | 2017-03-08 09:48:30.2061655 -08:00 | 1027001101 | 022801113 | 8 | 4 | 4 | 1 | 267 | 5.83 | 5.77 | 267 | 5.83 | 5.77 | 267 | 5.83 | 5.77 | 267 | 5.83 | 5.77 | 267 | 5.83 | 5.77 | 267 | 5.83 | 5.77 | 267 | 5.83 | 5.77 | 267 | 5.83 | 5.77 |  | Refer to Bank 1 notes | FALSE | FALSE | 458 | 595 | 549 | 687 | {F765DD6A-BFAE-43F0-8DAE-3BB0D83A2C48}
6416 | 4485 | {9A705E3F-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | ORLAND B | Bank 1 | CB 1102 | PGE\GSD5 | 2017-03-08 10:04:40.6540276 -08:00 | 1027001102 | 022801121 | 8 | 4 | 4 | 1 | 458 | 10 | 9.9 | 458 | 10 | 9.9 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  | Refer to Orland B Bank 1 notes | FALSE | FALSE | 458 | 595 | 549 | 687 | {3F20E9B1-B2E0-4C00-B097-070355AFA900}
6417 | 4457 | {25582F29-B71A-11E6-B077-D4BED91EFF1A} | SAN FRANCISCO | POTRERO (SF A) | Bank 2 | CB BUS TIE/2 | PGE\DMAL | 2017-03-08 12:20:06.9544676 -08:00 |  | 022801122 | 7 | 3 | 3 | 2 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {031B90D6-45EE-45B4-AB8F-201C2DD013A8}
6418 | 4457 | {F9E70AA8-AAAB-11E6-B077-D4BED91EFF1A} | SAN FRANCISCO | POTRERO (SF A) | Bank 2 | AE-1 | PGE\DMAL | 2017-03-14 14:55:26.8170934 -07:00 |  | 022801123 | 7 | 3 | 3 | 2 | 864 | 18.66 | 18.47 | 864 | 18.66 | 18.47 | 1004 | 21.69 | 21.47 | 1004 | 21.69 | 21.47 | 882 | 19.05 | 18.86 | 882 | 19.05 | 18.86 | 1024 | 22.12 | 21.9 | 1024 | 22.12 | 21.9 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {F2FF09D1-C0FD-461C-A422-5B8C7E4D125E}
6419 | 4457 | {0A5D2AAC-AAAC-11E6-B077-D4BED91EFF1A} | SAN FRANCISCO | POTRERO (SF A) | Bank 2 | AE-2 | PGE\DMAL | 2017-03-14 14:48:59.6155270 -07:00 |  | 022801124 | 7 | 3 | 3 | 2 | 864 | 18.66 | 18.47 | 864 | 18.66 | 18.47 | 1004 | 21.69 | 21.47 | 1004 | 21.69 | 21.47 | 882 | 19.05 | 18.86 | 882 | 19.05 | 18.86 | 1024 | 22.12 | 21.9 | 1024 | 22.12 | 21.9 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {7F93129A-88CD-4817-B164-F3F23B20FFED}
6420 | 4457 | {1F147F5C-AAAC-11E6-B077-D4BED91EFF1A} | SAN FRANCISCO | POTRERO (SF A) | Bank 2 | AE-3 | PGE\DMAL | 2017-03-14 14:50:10.8583684 -07:00 |  | 022801125 | 7 | 3 | 3 | 2 | 864 | 18.66 | 18.47 | 864 | 18.66 | 18.47 | 1004 | 21.69 | 21.47 | 1004 | 21.69 | 21.47 | 882 | 19.05 | 18.86 | 882 | 19.05 | 18.86 | 1024 | 22.12 | 21.9 | 1024 | 22.12 | 21.9 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {2ECCBF5A-9213-4E5A-AE8E-17D2007B45DF}
6421 | 4457 | {2C264461-AAAC-11E6-B077-D4BED91EFF1A} | SAN FRANCISCO | POTRERO (SF A) | Bank 2 | AE-4 | PGE\DMAL | 2017-03-14 14:51:02.3011297 -07:00 |  | 022801126 | 7 | 3 | 3 | 2 | 864 | 18.66 | 18.47 | 864 | 18.66 | 18.47 | 1004 | 21.69 | 21.47 | 1004 | 21.69 | 21.47 | 882 | 19.05 | 18.86 | 882 | 19.05 | 18.86 | 1024 | 22.12 | 21.9 | 1024 | 22.12 | 21.9 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {9491C00E-D2B5-4A15-A38D-B1148A5C2D3E}
6422 | 4490 | {9A705E59-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | ORLAND B | Bank 2 | CB 1103 | PGE\GSD5 | 2017-03-08 13:37:30.0368018 -08:00 | 1027001103 | 022801129 | 8 | 4 | 4 | 1 | 514 | 11.22 | 11.11 | 514 | 11.22 | 11.11 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 570 | 12.44 | 12.32 | 570 | 12.44 | 12.32 | 583 | 12.72 | 12.59 | 583 | 12.72 | 12.59 |  |  | FALSE | FALSE | 572 | 744 | 687 | 859 | {2DF215A3-D8A1-42DB-ACEF-8E7190727F81}
6423 | 4457 | {605EFD9D-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 2 | CB 1116 | PGE\DMAL | 2017-03-08 13:42:11.6350260 -08:00 | 0220301116 | 103031101 | 7 | 3 | 3 | 2 | 492 | 10.63 | 10.52 | 467 | 10.09 | 9.99 | 554 | 11.97 | 11.85 | 526 | 11.36 | 11.25 | 527 | 11.38 | 11.27 | 527 | 11.38 | 11.27 | 598 | 12.92 | 12.79 | 568 | 12.27 | 12.15 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {96DA1207-552D-4449-A7B8-F44789E03703}
6425 | 4457 | {2F3BE32E-AAA9-11E6-B077-D4BED91EFF1A} | SAN FRANCISCO | POTRERO (SF A) | Bank 2 | CB 1120 | PGE\DMAL | 2017-03-13 05:11:33.1246133 -07:00 |  | 103031102 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | Former AE-4 tie cable. Outdoor OCB to be used as Future Feeder. |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {00000000-0000-0000-0000-000000000000}
6427 | 4458 | {605EFD70-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 10 | CB 1104 | PGE\DMAL | 2017-03-08 14:10:39.3614860 -08:00 | 0220301104 | 102831101 | 7 | 3 | 3 | 2 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 |  |  | FALSE | FALSE | 3472 | 3750 | 3750 | 3750 | {2FFA22FF-EA5D-48D6-948E-A06A823FAC2D}
6428 | 4458 | {605EFD76-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 10 | CB 1108 | PGE\DMAL | 2017-03-08 14:14:38.9424800 -08:00 | 0220301108 | 022801130 | 7 | 3 | 3 | 2 | 481 | 10.39 | 10.29 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 495 | 10.69 | 10.58 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 |  |  | FALSE | FALSE | 3472 | 3750 | 3750 | 3750 | {423F3050-4AD6-4202-A7D6-A303CD32DAAD}
6429 | 4458 | {605EFD79-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 10 | CB 1111 | PGE\DMAL | 2017-03-08 14:17:29.4186728 -08:00 | 0220301111 | 022801131 | 7 | 3 | 3 | 2 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 475 | 10.26 | 10.16 |  |  | FALSE | FALSE | 3472 | 3750 | 3750 | 3750 | {D8A46B55-5E10-444E-A3C5-E7C5A5090CA4}
6430 | 4458 | {605EFD7C-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 10 | CB 1113 | PGE\DMAL | 2017-03-08 14:23:11.5412684 -08:00 | 0220301113 | 022801132 | 7 | 3 | 3 | 2 | 360 | 7.78 | 7.7 | 360 | 7.78 | 7.7 | 400 | 8.64 | 8.55 | 400 | 8.64 | 8.55 | 371 | 8.01 | 7.93 | 371 | 8.01 | 7.93 | 412 | 8.9 | 8.81 | 412 | 8.9 | 8.81 |  |  | FALSE | FALSE | 3472 | 3750 | 3750 | 3750 | {5EA1FDAD-693B-46BC-9FB8-932DD1AEF950}
6432 | 4458 | {605EFD4F-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 10 | CB 1114 | PGE\DMAL | 2017-05-23 16:00:26.2680069 -07:00 | 0220301114 | 022801133 | 7 | 3 | 3 | 2 | 320 | 6.91 | 6.84 | 320 | 6.91 | 6.84 | 320 | 6.91 | 6.84 | 320 | 6.91 | 6.84 | 320 | 6.91 | 6.84 | 320 | 6.91 | 6.84 | 320 | 6.91 | 6.84 | 320 | 6.91 | 6.84 | ATS - Alternate Source for AT&T Ballpark_Peak 250amp. Available Feeder Capability = SN = SE = WN = WE = 570amp - 250amp (ATT) = 320amp. |  | FALSE | FALSE | 3472 | 3750 | 3750 | 3750 | {7941C20B-DD6D-4D62-A69E-8DC7B9C8CF8E}
6433 | 4458 | {605EFD7F-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 10 | CB 1115 | PGE\DMAL | 2017-03-08 15:26:05.8897940 -08:00 | 0220301115 | 022801134 | 7 | 3 | 3 | 2 | 360 | 7.78 | 7.7 | 360 | 7.78 | 7.7 | 400 | 8.64 | 8.55 | 400 | 8.64 | 8.55 | 371 | 8.01 | 7.93 | 371 | 8.01 | 7.93 | 412 | 8.9 | 8.81 | 412 | 8.9 | 8.81 |  |  | FALSE | FALSE | 3472 | 3750 | 3750 | 3750 | {F83E01CD-39A5-49F0-A646-8BBD08D88C6C}
6434 | 4458 | {605EFD82-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 10 | CB 1117 | PGE\DMAL | 2017-03-08 15:29:11.0014132 -08:00 | 0220301117 | 102831102 | 7 | 3 | 3 | 2 | 555 | 11.99 | 11.87 | 555 | 11.99 | 11.87 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 566 | 12.22 | 12.1 | 566 | 12.22 | 12.1 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 3472 | 3750 | 3750 | 3750 | {97C86E2D-D4F8-4BF4-9D61-B22966CEE1A7}
6435 | 4458 | {605EFD94-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | POTRERO (SF A) | Bank 10 | CB 1118 | PGE\DMAL | 2017-03-08 15:32:46.6477120 -08:00 | 0220301118 | 102831106 | 7 | 3 | 3 | 2 | 467 | 10.09 | 9.99 | 467 | 10.09 | 9.99 | 523 | 11.3 | 11.19 | 523 | 11.3 | 11.19 | 481 | 10.39 | 10.29 | 481 | 10.39 | 10.29 | 539 | 11.64 | 11.52 | 539 | 11.64 | 11.52 | ATS - Alternate Source to BART Station Mission/16th Street. |  | FALSE | FALSE | 3472 | 3750 | 3750 | 3750 | {1E4C72CE-3940-403A-B6E5-F633C628C524}
6436 | 4489 | {80988F37-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | BIG MEADOWS | Bank 1 | CB 2101 | PGE\JBJ8 | 2017-03-09 15:34:33.1720377 -08:00 | 1028102101 | 102831103 | 11 | 4 | 4 | 1 | 224 | 8.38 | 8.3 | 224 | 8.38 | 8.3 | 291 | 10.89 | 10.78 | 285 | 10.66 | 10.55 | 269 | 10.06 | 9.96 | 269 | 10.06 | 9.96 | 300 | 11.22 | 11.11 | 285 | 10.66 | 10.55 | transferred from sharepoint | Big Meadows Bank 1 Net Capability | FALSE | FALSE | 400 | 484 | 481 | 601 | {919381D8-330A-4503-A232-CDF93F0F8767}
6437 | 4494 | {8D2989C2-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | GLENN | Bank 3 | CB 1101 | PGE\GSD5 | 2017-03-08 16:02:08.6708954 -08:00 | 1026001101 | 102831104 | 8 | 4 | 4 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | Settings Group 1 is the normal setting and allows for the bypass of LR 2416 or LR 2552 provided that the circuit is in normal configuration (with the 65E fuses at 93211 in service and 14165 bypassed). Group 1 should also be used for field transfers to relieve Orland “B” since the total load transferred under these conditions is limited to less than the Group 1 capability by the 4/0 AWG Al on Wyo Road. Settings Group 2 is intended for relief of Capay provided that the Capay 1101 circuit is still in service or can be picked up through SW 8355 outside Capay Sub. All reclosers must be in service (LR 2416 or LR 66596 can be bypassed provided that all load side reclosers are in service). Settings Group 3 is intended for relief of Capay if the Capay 1101 circuit must be picked up through SW 8351 (Group 2 cannot see end of line in this configuration). All reclosers except 2416 or 66596 must be in service as above. Settings Group 4 is a special setting allowing both LR 2552 and CO’s 93211 to be bypassed sumultaneously. However, this setting can only see up to normally open SW 7427 (the fault duties at CO’s 4971 are too low for a usable breaker setting) and 93211 should not be bypassed unless we are relieving Corning through 7427. | Information extracted from Capability Sheet on Sharepoint. | FALSE | FALSE | 1374 | 1787 | 1649 | 2006 | {5D86E4B4-D5DF-4E0C-B9B2-CF8377051BD1}
6438 | 4495 | {86A61B6C-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CORNING | Bank 1 | CB 401 | PGE\GSD5 | 2017-03-14 13:13:29.1540469 -07:00 | 103330401 | 102831105 | 3 | 4 | 4 | 1 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 416 | 541 | 499 | 624 | {92FB1998-C621-4A39-8FDE-FA4651FD1654}
6439 | 4495 | {86A61B75-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CORNING | Bank 1 | CB 402 | PGE\GSD5 | 2017-03-14 13:13:50.2491677 -07:00 | 103330402 | 022530401 | 3 | 4 | 4 | 1 | 282 | 2.03 | 2.01 | 267 | 1.92 | 1.9 | 300 | 2.16 | 2.14 | 299 | 2.15 | 2.13 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 |  | Information extracted from Capability Sheet on Sharepoint. | FALSE | FALSE | 416 | 541 | 499 | 624 | {5F46DD3E-C9EB-4D07-AAB8-451F9CEDA631}
6440 | 4496 | {86A61C0E-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CORNING | Bank 3 | CB 1103 | PGE\GSD5 | 2017-03-09 09:36:03.0538829 -08:00 | 1033301103 | 022530402 | 8 | 4 | 4 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {180A260F-73D6-46D2-87EA-4D668120EF89}
6441 | 4496 | {86A61C33-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CORNING | Bank 3 | CB 1104 | PGE\GSD5 | 2017-03-08 16:35:24.5264765 -08:00 | 1033301104 | 103461102 | 8 | 4 | 4 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {860FB468-CEE2-4504-89BF-2382390997C0}
6443 | 4497 | {6EF98159-3D59-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | SF E | 12kv Bus 1 (AE-1, AE-2, AE-3, AE-4) | CB 1101 | PGE\DMAL | 2017-03-08 17:42:40.1212826 -08:00 | 0220701101 | 103561101 | 7 | 3 | 3 | 2 | 391 | 8.45 | 8.37 | 371 | 8.01 | 7.93 | 440 | 9.5 | 9.41 | 418 | 9.03 | 8.94 | 443 | 9.57 | 9.47 | 420 | 9.07 | 8.98 | 473 | 10.22 | 10.12 | 449 | 9.7 | 9.6 |  |  | FALSE | FALSE | 3750 | 3750 | 3750 | 3750 | {404E73F8-4BCF-42B7-85E3-4C77DF3252F8}
6444 | 4497 | {66CD4440-3D59-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | SF E | 12kv Bus 1 (AE-1, AE-2, AE-3, AE-4) | CB 1103 | PGE\DMAL | 2017-05-17 10:00:41.5045196 -07:00 | 0220701103 | 103561102 | 7 | 3 | 3 | 2 | 405 | 8.75 | 8.66 | 405 | 8.75 | 8.66 | 498 | 10.76 | 10.65 | 498 | 10.76 | 10.65 | 417 | 9.01 | 8.92 | 417 | 9.01 | 8.92 | 505 | 10.91 | 10.8 | 505 | 10.91 | 10.8 | 1) Standby Source to Sutro Tower T896_T898. Normal Source to T895_T897. Internal Customer ATS. 2) Standby Source to 18th Street Sub. |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {B381758B-366D-42EE-8155-A9CD165E66A5}
6446 | 4497 | {6EF9815C-3D59-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | SF E | 12kv Bus 1 (AE-1, AE-2, AE-3, AE-4) | CB 1105 | PGE\DMAL | 2017-03-08 17:59:15.4516232 -08:00 | 0220701105 | 103521102 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | ATS1 - MUNI Church Traction. ATS2 - MUNI Castro Building. Branch SW-19942 - 4/0XLA cable rating (243/299/250/303). Branch SW-19944 - 4/0T cable rating (233/259/240/266). |  | FALSE | FALSE | 3750 | 3750 | 3750 | 3750 | {B3764D66-9F8C-4508-9E54-F9084A648EF9}
6447 | 4497 | {76D73229-3D59-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | SF E | 12kv Bus 1 (AE-1, AE-2, AE-3, AE-4) | CB 1107 | PGE\DMAL | 2017-03-28 15:28:19.1578493 -07:00 | 0220701107 | 103521103 | 7 | 3 | 3 | 2 | 445 | 9.61 | 9.51 | 422 | 9.11 | 9.02 | 494 | 10.67 | 10.56 | 469 | 10.13 | 10.03 | 458 | 9.89 | 9.79 | 435 | 9.4 | 9.31 | 509 | 10.99 | 10.88 | 483 | 10.43 | 10.33 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {EB313DA8-04FE-43CB-95DA-5F2BE4A4E40B}
6448 | 4497 | {B8A75640-B738-11E6-B077-D4BED91EFF1A} | SAN FRANCISCO | SF E | 12kv Bus 1 (AE-1, AE-2, AE-3, AE-4) | E MUNI TIE | PGE\DMAL | 2017-04-11 10:25:17.0802490 -07:00 |  | 103521104 | 7 | 3 | 3 | 2 | 573 | 12.38 | 12.26 | 573 | 12.38 | 12.26 | 676 | 14.6 | 14.45 | 676 | 14.6 | 14.45 | 584 | 12.61 | 12.48 | 584 | 12.61 | 12.48 | 690 | 14.9 | 14.75 | 690 | 14.9 | 14.75 | MUNI primary switchgear is inside of Station E. Space is leased by MUNI. |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {00000000-0000-0000-0000-000000000000}
6449 | 4497 | {260BFE26-B73A-11E6-B077-D4BED91EFF1A} | SAN FRANCISCO | SF E | 12kv Bus 1 (AE-1, AE-2, AE-3, AE-4) | CB D-E/12 (12KV BUS) | PGE\DMAL | 2017-03-28 15:28:38.2401960 -07:00 |  | 022801108 | 7 | 3 | 3 | 2 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {00000000-0000-0000-0000-000000000000}
6450 | 4498 | {3F3C5D16-B73A-11E6-B077-D4BED91EFF1A} | SAN FRANCISCO | SF E | 12KV Bus 2 | CB D-E/22 (12KV BUS) | PGE\DMAL | 2017-03-28 12:28:15.5538603 -07:00 |  | 012022216 | 7 | 3 | 3 | 2 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {00000000-0000-0000-0000-000000000000}
6452 | 4499 | {10CF1228-B73D-11E6-B077-D4BED91EFF1A} | SAN FRANCISCO | SF E | Bank 1 | CB BK-1 AUX/2 (Non-SCADA) | PGE\DMAL | 2017-03-28 12:27:49.3409883 -07:00 |  | 012022218 | 3 | 3 | 3 | 2 | 1457 | 10.5 | 10.4 | 1457 | 10.5 | 10.4 | 1894 | 13.65 | 13.51 | 1894 | 13.65 | 13.51 | 1748 | 12.59 | 12.46 | 1748 | 12.59 | 12.46 | 2000 | 14.41 | 14.27 | 2000 | 14.41 | 14.27 |  |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2185 | {F11E2BBC-05BD-45FD-96DD-EB21B1B92A68}
6453 | 4499 | {80A9A3DD-B747-11E6-B077-D4BED91EFF1A} | SAN FRANCISCO | SF E | Bank 1 | CB BK-1 MAIN-D/2 (Non-SCADA) | PGE\DMAL | 2017-03-28 12:27:35.3919957 -07:00 |  | 012022215 | 3 | 3 | 3 | 2 | 1457 | 10.5 | 10.4 | 1457 | 10.5 | 10.4 | 1894 | 13.65 | 13.51 | 1894 | 13.65 | 13.51 | 1748 | 12.59 | 12.46 | 1748 | 12.59 | 12.46 | 2000 | 14.41 | 14.27 | 2000 | 14.41 | 14.27 |  |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2185 | {925FEC93-CDE7-4BAC-A00A-8F79291CEDBB}
6454 | 4500 | {590353F3-B73A-11E6-B077-D4BED91EFF1A} | SAN FRANCISCO | SF E | Bank 2 | CB D-E/2 (4KV MAIN BUS) | PGE\DMAL | 2017-03-28 12:28:59.1015542 -07:00 |  | 012022217 | 3 | 3 | 3 | 2 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 |  |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2185 | {00000000-0000-0000-0000-000000000000}
6455 | 4500 | {260D4DA8-B73D-11E6-B077-D4BED91EFF1A} | SAN FRANCISCO | SF E | Bank 2 | CB BK-2 AUX/2 (Non-SCADA) | PGE\DMAL | 2017-03-08 18:36:31.1618168 -08:00 |  | 012022211 | 3 | 3 | 3 | 2 | 1457 | 10.5 | 10.4 | 1457 | 10.5 | 10.4 | 1894 | 13.65 | 13.51 | 1894 | 13.65 | 13.51 | 1748 | 12.59 | 12.46 | 1748 | 12.59 | 12.46 | 2000 | 14.41 | 14.27 | 2000 | 14.41 | 14.27 |  |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2185 | {83389EE8-19BC-4F2D-8E4D-2731FCA2D06E}
6456 | 4500 | {9707061B-B747-11E6-B077-D4BED91EFF1A} | SAN FRANCISCO | SF E | Bank 2 | CB BK-2 MAIN E/2 (Non-SCADA) | PGE\DMAL | 2017-03-08 18:37:08.2125293 -08:00 |  | 152461101 | 3 | 3 | 3 | 2 | 1457 | 10.5 | 10.4 | 1457 | 10.5 | 10.4 | 1894 | 13.65 | 13.51 | 1894 | 13.65 | 13.51 | 1748 | 12.59 | 12.46 | 1748 | 12.59 | 12.46 | 2000 | 14.41 | 14.27 | 2000 | 14.41 | 14.27 |  |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2185 | {3D597DED-05B3-4268-A9D9-E3EEE3CAD2B9}
6459 | 4502 | {9A705CA0-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | LOS MOLINOS | Bank 1 | CB 1101 | PGE\GSD5 | 2017-03-09 10:21:58.2743209 -08:00 | 1034801101 | 012022212 | 8 | 4 | 4 | 2 | 345 | 7.53 | 7.45 | 345 | 7.53 | 7.45 | 386 | 8.42 | 8.34 | 386 | 8.42 | 8.34 | 443 | 9.67 | 9.57 | 443 | 9.67 | 9.57 | 473 | 10.32 | 10.22 | 473 | 10.32 | 10.22 | Refer to Capability Sheet on Sharepoint: CIRCUIT CAPABILITY 282 300 300 300 |  | FALSE | FALSE | 548 | 712 | 658 | 822 | {C09CC3EA-4312-4CE3-B92D-F1DC512F064C}
6460 | 4502 | {9A705CC5-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | LOS MOLINOS | Bank 1 | CB 1102 | PGE\GSD5 | 2017-03-09 10:28:48.7683861 -08:00 | 1034801102 | 012022214 | 8 | 4 | 4 | 2 | 223 | 4.87 | 4.82 | 223 | 4.87 | 4.82 | 248 | 5.41 | 5.36 | 248 | 5.41 | 5.36 | 283 | 6.18 | 6.12 | 283 | 6.18 | 6.12 | 300 | 6.55 | 6.48 | 300 | 6.55 | 6.48 | Please refer to Capability Sheet on Sharepoint CIRCUIT CAPABILITY 183 212 269 287 |  | FALSE | FALSE | 548 | 712 | 658 | 822 | {390705D5-F79E-4E9F-9BCE-7D79B3CE39E5}
6461 | 4503 | {ACCC4EB2-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | VINA | Bank 1 | CB 1101 | PGE\GSD5 | 2017-03-09 10:42:24.2331253 -08:00 | 1035801101 | 083611107 | 8 | 4 | 4 | 2 | 118 | 2.58 | 2.55 | 118 | 2.58 | 2.55 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 142 | 3.1 | 3.07 | 142 | 3.1 | 3.07 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | Please refer to Capability Sheet on Sharepoint. CIRCUIT CAPABILITY 98 127 118 147 |  | FALSE | FALSE | 118 | 154 | 142 | 177 | {125200A9-656E-437D-854D-0BB69ADB1624}
6462 | 4492 | {86A61AAD-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CHICO B | Bank 1 | CB 1101 | PGE\DWS8 | 2017-05-26 16:19:39.9033896 -07:00 | 1024901101 | 083611108 | 7 | 3 | 3 | 1 | 515 | 11.12 | 11.01 | 515 | 11.12 | 11.01 | 578 | 12.48 | 12.36 | 578 | 12.48 | 12.36 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 740 | 963 | 888 | 1111 | {703973CB-3ADA-4032-A66E-3B85E22AC01B}
6463 | 4492 | {86A61AC4-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CHICO B | Bank 1 | CB 1102 | PGE\DWS8 | 2017-05-26 16:27:02.7677541 -07:00 | 1024901102 | 152461102 | 7 | 3 | 3 | 2 | 454 | 9.81 | 9.71 | 454 | 9.81 | 9.71 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 468 | 10.11 | 10.01 | 468 | 10.11 | 10.01 | 566 | 12.22 | 12.1 | 566 | 12.22 | 12.1 |  |  | FALSE | FALSE | 740 | 963 | 888 | 1111 | {C2A5A305-8747-4506-B2E7-63CB91BDC850}
6465 | 4492 | {86A61ACD-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CHICO B | Bank 1 | CB 1103 | PGE\DRN3 | 2017-03-09 15:16:47.2971405 -08:00 | 1024901103 | 012021103 | 7 | 3 | 3 | 1 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 |  |  | FALSE | FALSE | 740 | 963 | 888 | 1111 | {15DF1019-F677-41DE-A522-5474DE499C96}
6467 | 4504 | {86A61B88-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CORNING | Bank 2 | CB 1101 | PGE\GSD5 | 2017-03-09 15:30:34.8542822 -08:00 | 1033301101 | 012021104 | 8 | 4 | 4 | 1 | 438 | 9.56 | 9.46 | 438 | 9.56 | 9.46 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 485 | 10.58 | 10.47 | 485 | 10.58 | 10.47 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | Refer to capability sheet on sharepoint: CIRCUIT CAPABILITY 500 500 500 500 |  | FALSE | FALSE | 577 | 750 | 692 | 866 | {B2E43750-4CFF-48F6-BA86-BE5E99AD66F9}
6468 | 4493 | {86A61AE0-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CHICO B | Bank 2 | CB 1105 | PGE\DRN3 | 2017-03-09 15:33:11.3484642 -08:00 | 1024901105 | 083611109 | 7 | 3 | 3 | 1 | 566 | 12.22 | 12.1 | 566 | 12.22 | 12.1 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 740 | 963 | 888 | 1111 | {2B187C29-A10C-4580-AC89-4743A35C8CD5}
6469 | 4504 | {86A61BD8-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CORNING | Bank 2 | CB 1102 | PGE\GSD5 | 2017-03-09 15:35:09.3855482 -08:00 | 1033301102 | 022340402 | 8 | 4 | 4 | 1 | 502 | 10.96 | 10.85 | 502 | 10.96 | 10.85 | 595 | 12.99 | 12.86 | 595 | 12.99 | 12.86 | 545 | 11.89 | 11.77 | 545 | 11.89 | 11.77 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Refer to capability sheet on Sharepoint: CIRCUIT CAPABILITY 570 570 570 570 |  | FALSE | FALSE | 577 | 750 | 692 | 866 | {013C5A2C-C024-4639-B70E-335C16F8E0FB}
6470 | 4493 | {86A61AF0-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CHICO B | Bank 2 | CB 1106 | PGE\DRN3 | 2017-03-09 15:38:32.9954496 -08:00 | 1024901106 | 022490401 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  | all data from Sharepoint | FALSE | FALSE | 740 | 963 | 888 | 1111 | {7F2C1BE5-D4FA-4ABD-8B1C-D50B340C4C20}
6472 | 4505 | {7A8F245E-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | ANDERSON | Bank 1 | CB 1101 | PGE\JLDe | 2017-03-12 19:57:21.8227670 -07:00 | 1032601101 | 022490402 | 8 | 3 | 2 | 1 | 477 | 10.41 | 10.31 | 477 | 10.41 | 10.31 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | AXDJ:I'm the sole NV Reliability Engineer assigned to do Reliability Planning for the area not Capacity Planning since the re-organization on 4/1/16. I'm not responsible for accuracy of this sheet. These numbers including load factors and other unfilled data have to be validated and updated by one of the 5 Capacity DEs assigned to do capacity Planning for the North Valley area. Current Capability sheet in use is indicating feeder amps capability as : Sum Nor Sum Em Win Nor Win Em 440 500 500 500 |  | TRUE | FALSE | 859 | 1116 | 1030 | 1288 | {FF447FA2-5E7B-481B-A4D9-AA8E0889E607}
6473 | 4505 | {7A8F2467-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | ANDERSON | Bank 1 | CB 1102 | PGE\JLDe | 2017-03-12 19:48:20.1023495 -07:00 | 1032601102 | 022490403 | 8 | 3 | 2 | 1 | 503 | 10.98 | 10.87 | 489 | 10.67 | 10.56 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | AXDJ:I'm the sole NV Reliability Engineer no longer assigned to do Capacity planning for any part of NV area since 4/1/16. I'm not responsible for accuracy of this sheet. These numbers including load factors and other unfilled data have to be validated and updated by one of the 5 Capacity DEs assigned to do capacity Planning for the area. Current Capability sheet in use is indicating feeder amps capability as : Sum Nor Sum Em Win Nor Win Em 503 570 557 570 |  | TRUE | FALSE | 859 | 1116 | 1030 | 1288 | {EE20782F-B932-4FE4-B485-79073DCFB122}
6475 | 4505 | {7A8F247E-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | ANDERSON | Bank 1 | CB 1103 | PGE\JLDe | 2017-03-12 19:57:39.7631120 -07:00 | 1032601103 | 012541102 | 8 | 3 | 2 | 1 | 464 | 10.13 | 10.03 | 440 | 9.6 | 9.5 | 500 | 10.91 | 10.8 | 494 | 10.78 | 10.67 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | AXDJ:I'm the sole NV Reliability Engineer no longer assigned to do Capacity planning for any part of NV area since 4/1/16. I'm not responsible for accuracy of this sheet. These numbers including load factors and other unfilled data have to be validated and updated by one of the 5 Capacity DEs assigned to do capacity Planning for the area. Current Capability sheet in use is indicating feeder amps capability as : Sum Nor Sum Em Win Nor Win Em 464 500 500 500 |  | TRUE | FALSE | 859 | 1116 | 1030 | 1288 | {76221728-3F44-49C1-A7B4-292E32FB4034}
6476 | 4506 | {80988F92-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | BURNEY | Bank 1 | CB 1101 | PGE\JLDe | 2017-03-12 20:07:38.2686215 -07:00 | 1033101101 | 022500401 | 8 | 3 | 2 | 1 | 219 | 4.78 | 4.73 | 208 | 4.54 | 4.49 | 285 | 6.22 | 6.16 | 270 | 5.89 | 5.83 | 263 | 5.74 | 5.68 | 249 | 5.43 | 5.38 | 329 | 7.18 | 7.11 | 312 | 6.81 | 6.74 | AXDJ: I'm the sole NV Reliability Engineer assigned to do Reliability Planning for the entire North Valley area not to do Capacity Planning ever since the DE re-org on 4/1/16. I'm not responsible for accuracy of this sheet. These numbers including load factors and other unfilled data have to be validated and updated by one of the 5 Capacity DEs assigned to do capacity Planning for the North Valley area. Current Capability sheet in use is indicating feeder amps capability as : Sum Nor Sum Em Win Nor Win Em 218 283 261 327 |  | TRUE | FALSE | 219 | 285 | 263 | 329 | {15A47641-33D8-4885-93BF-41F9FD0B6BFC}
6477 | 4507 | {80988FA5-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | BURNEY | Bank 2 | CB 1102 | PGE\JLDe | 2017-03-12 20:26:25.8271049 -07:00 | 1033101102 | 022500402 | 8 | 3 | 2 | 1 | 103 | 2.25 | 2.23 | 97 | 2.12 | 2.1 | 134 | 2.92 | 2.89 | 127 | 2.77 | 2.74 | 123 | 2.68 | 2.65 | 116 | 2.53 | 2.5 | 154 | 3.36 | 3.33 | 146 | 3.19 | 3.16 | AXDJ: I'm the sole NV Reliability Engineer assigned to do Reliability Planning for the entire North Valley area not to do Capacity Planning ever since the DE re-org on 4/1/16. I'm not responsible for accuracy of this sheet. These numbers including load factors and other unfilled data have to be validated and updated by one of the 5 Capacity DEs assigned to do capacity Planning for the North Valley area. Current Capability sheet in use is indicating feeder amps capability as : Sum Nor Sum Em Win Nor Win Em 98 127 118 147 | 3-1 ph 0.75 MVA | TRUE | FALSE | 103 | 134 | 123 | 154 | {38B6ACA3-634C-43FF-81A7-6FC8FE53C482}
6479 | 4508 | {941FA15C-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | HAMILTON BRANCH | Bank 2 | CB 1101 | PGE\JBJ8 | 2017-03-21 12:03:14.1766475 -07:00 | 1023601101 | 022500403 | 7 | 4 | 4 | 1 | 384 | 8.29 | 8.21 | 384 | 8.29 | 8.21 | 384 | 8.29 | 8.21 | 384 | 8.29 | 8.21 | 384 | 8.29 | 8.21 | 384 | 8.29 | 8.21 | 384 | 8.29 | 8.21 | 384 | 8.29 | 8.21 |  |  | FALSE | FALSE | 400 | 400 | 400 | 400 | {0D479004-4416-4453-AF8E-C93F2F2A023B}
6482 | 4511 | {8D2987CB-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | COTTONWOOD | Bank 6 | CB 1101 | PGE\AxDj | 2017-03-10 17:46:04.4209089 -08:00 | 1029301101 | 022480401 | 8 | 4 | 4 | 2 | 345 | 7.53 | 7.45 | 345 | 7.53 | 7.45 | 386 | 8.42 | 8.34 | 386 | 8.42 | 8.34 | 443 | 9.67 | 9.57 | 443 | 9.67 | 9.57 | 473 | 10.32 | 10.22 | 473 | 10.32 | 10.22 | AXDJ: I'm the sole NV Reliability Engineer assigned to do Reliability Planning for the entire North Valley area not to do Capacity Planning ever since the DE re-org on 4/1/16. I'm not responsible for accuracy of this sheet. These numbers including load factors and other unfilled data have to be validated and updated by one of the 5 Capacity DEs assigned to do capacity Planning for the North Valley area. Current Capability sheet in use is indicating feeder amps capability as : Sum Nor Sum Em Win Nor Win Em 345 386 443 473 | with LTC | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {4EB5F180-E9E5-4123-BD1A-EDA5C1FD990E}
6483 | 4511 | {8D2987D4-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | COTTONWOOD | Bank 6 | CB 1102 | PGE\AxDj | 2017-03-10 17:53:58.8396457 -08:00 | 1029301102 | 022480402 | 8 | 4 | 4 | 2 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | AXDJ: I'm the sole NV Reliability Engineer assigned to do Reliability Planning for the entire North Valley area which is three times the size of Sierra or Sacramento and wasnt assigned to do Capacity Planning ever since the DE re-org on 4/1/16. I'm not responsible for accuracy of this sheet. These numbers including load factors and other unfilled data have to be validated and updated by one of the 5 Capacity DEs assigned to do capacity Planning for the North Valley area. Current Capability sheet in use is indicating feeder amps capability as : Sum Nor Sum Em Win Nor Win Em 515 578 600 600 |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {D2887A93-8E6D-4C94-A327-0E9200F34B38}
6484 | 4513 | {8D2987EE-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | COTTONWOOD | Bank 8 | CB 1103 | PGE\AxDj | 2017-03-10 18:00:47.2741413 -08:00 | 1029301103 | 022781103 | 8 | 4 | 4 | 1 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | AXDJ: I'm the sole NV Reliability Engineer assigned to do Reliability Planning for the entire North Valley area not to do Capacity Planning ever since the DE re-org on 4/1/16. I'm not responsible for accuracy of this sheet. These numbers including load factors and other unfilled data have to be validated and updated by one of the 5 Capacity DEs assigned to do capacity Planning for the North Valley area. Current Capability sheet in use is indicating feeder amps capability as : Sum Nor Sum Em Win Nor Win Em 733 733 733 733 |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B46F8B63-B31D-40AD-9B3D-5938D5749613}
6487 | 4515 | {B67CF1DF-C45F-11E5-A522-005056A71442} | Bank 5 | CB 1105 | Bank T5581 (Former Boston Sub) | LR CR242 | PGE\MUSF | 2017-03-13 17:37:24.5679194 -07:00 | 2101092127 | 022550402 | 3 | 3 | 3 | 2 | 346 | 2.49 | 2.47 | 346 | 2.49 | 2.47 | 451 | 3.25 | 3.22 | 451 | 3.25 | 3.22 | 416 | 3 | 2.97 | 416 | 3 | 2.97 | 520 | 3.75 | 3.71 | 520 | 3.75 | 3.71 |  |  | FALSE | FALSE | 346 | 451 | 416 | 520 | {4B545AE9-A885-48BD-BBDD-C323FFCD6AA5}
6489 | 4516 | {9A705CE2-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | MC ARTHUR | Bank 1 | CB 1101 | PGE\WRA4 | 2017-08-14 11:05:43.9598048 -07:00 | 103491101 | 022550403 | 7 | 4 | 4 | 1 | 417 | 9.01 | 8.92 | 416 | 8.99 | 8.9 | 417 | 9.01 | 8.92 | 417 | 9.01 | 8.92 | 417 | 9.01 | 8.92 | 417 | 9.01 | 8.92 | 417 | 9.01 | 8.92 | 417 | 9.01 | 8.92 | transferred from sharepoint | 3–1Ph New 3 Single Phase 3.5 MVA 3.5 MVA | FALSE | FALSE | 430 | 430 | 430 | 430 | {70EE210E-AC81-450D-B531-F7FD4353D45E}
6493 | 4516 | {9A705CF9-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | MC ARTHUR | Bank 1 | CB 1102 | PGE\JBJ8 | 2017-03-21 23:24:42.9342091 -07:00 | 103491102 | 022400401 | 7 | 4 | 4 | 1 | 417 | 9.01 | 8.92 | 416 | 8.99 | 8.9 | 417 | 9.01 | 8.92 | 417 | 9.01 | 8.92 | 417 | 9.01 | 8.92 | 417 | 9.01 | 8.92 | 417 | 9.01 | 8.92 | 417 | 9.01 | 8.92 | transferred from sharepoint | 3–1Ph New 3 Single Phase 3.5 MVA 3.5 MVA | FALSE | FALSE | 430 | 430 | 430 | 430 | {91282D7D-6010-4CCA-8A55-7A20BCC7E4F4}
6496 | 4518 | {A6861C1F-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | PIT NO 1 | Bank 4 | CB 1101 | PGE\DCGa | 2017-08-15 08:37:46.8033046 -07:00 | 103721101 | 022400402 | 8 | 3 | 3 | 1 | 200 | 4.36 | 4.32 | 199 | 4.34 | 4.3 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | QA COMPLETED BY DCGA ON 08/15/2017 |  | FALSE | FALSE | 548 | 712 | 600 | 720 | {83D47FAF-E554-44B8-A624-72B2B7FB4822}
6500 | 4523 | {53849E4E-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | EAST MARYSVILLE | Bank 3 | CB 1108 | PGE\TEJ2 | 2017-03-14 10:21:58.0583757 -07:00 | 1523301108 | 022610401 | 7 | 4 | 4 | 1 | 514 | 11.1 | 10.99 | 514 | 11.1 | 10.99 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 578 | 752 | 694 | 868 | {B6818E19-6360-4375-B97F-3BE8B34889A6}
6501 | 4523 | {53849E45-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | EAST MARYSVILLE | Bank 3 | CB 1107 | PGE\TEJ2 | 2017-03-14 10:15:29.3433280 -07:00 | 1523301107 | 022610402 | 7 | 4 | 4 | 1 | 514 | 11.1 | 10.99 | 514 | 11.1 | 10.99 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 578 | 752 | 694 | 868 | {606DB666-2BEA-4FEA-8E7C-333479EC355D}
6503 | 4524 | {53849E32-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | EAST MARYSVILLE | Bank 2 | CB 1105 | PGE\TEJ2 | 2017-03-14 09:54:48.1482359 -07:00 | 1523301105 | 012061102 | 7 | 4 | 4 | 1 | 578 | 12.48 | 12.36 | 578 | 12.48 | 12.36 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 578 | 752 | 694 | 868 | {E081A161-03CE-453B-B390-A0DEBAF07EFE}
6504 | 4499 | {77267305-B739-11E6-B077-D4BED91EFF1A} | SAN FRANCISCO | SF E | Bank 1 | CB 401 (Non-SCADA) | PGE\DMAL | 2017-03-28 12:06:49.5004307 -07:00 |  | 083671104 | 3 | 3 | 3 | 2 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 500EPRcu SPLITS: Each branch limited by (a) 500T-2ELC; by (b) old style OH switch rated at 400amp and (c) 4/0cu OH conductor. |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2185 | {00000000-0000-0000-0000-000000000000}
6505 | 4499 | {9402A909-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF E | Bank 1 | CB 406 (Non-SCADA) | PGE\DMAL | 2017-03-28 12:07:33.5474174 -07:00 | 02207406 | 083671105 | 3 | 3 | 3 | 2 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 |  |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2185 | {DF330DA6-1119-4D61-8D93-9EC0267FBA2E}
6506 | 4499 | {9402A90E-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF E | Bank 1 | CB 407 (Non-SCADA) | PGE\DMAL | 2017-03-28 12:14:26.9462529 -07:00 | 02207407 | 083671106 | 3 | 3 | 3 | 2 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 |  |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2185 | {D4EE69DB-069D-471E-9B94-064837194821}
6507 | 4499 | {9402A913-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF E | Bank 1 | CB 408 (Non-SCADA) | PGE\DMAL | 2017-03-28 12:18:45.7359523 -07:00 | 02207408 | 083671107 | 3 | 3 | 3 | 2 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 |  |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2185 | {98B47E9F-A628-449A-915B-B827049D66AD}
6509 | 2398 | {DA6C31E7-D1D3-11E6-B89B-9CB70D532D7F} | EAST BAY | MIRA VISTA | Bank 1 (Non SCADA) | CB 402 (Non-SCADA) | PGE\MUSF | 2017-03-14 17:15:18.8286714 -07:00 |  | 012101102 | 3 | 3 | 3 | 2 | 555 | 4 | 3.96 | 555 | 4 | 3.96 | 721 | 5.2 | 5.15 | 721 | 5.2 | 5.15 | 666 | 4.8 | 4.75 | 666 | 4.8 | 4.75 | 832 | 5.99 | 5.93 | 832 | 5.99 | 5.93 |  |  | FALSE | FALSE | 555 | 721 | 666 | 832 | {EBFB78AC-95B1-4AB4-8000-84ADB6B668D7}
6510 | 4475 | {2A05E001-BD96-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 2 (Banks 12, 13, 14) | CB 1102 | PGE\DMAL | 2017-03-15 12:03:31.3598189 -07:00 |  | 012101104 | 7 | 3 | 3 | 2 | 426 | 9.2 | 9.11 | 426 | 9.2 | 9.11 | 524 | 11.32 | 11.21 | 524 | 11.32 | 11.21 | 439 | 9.48 | 9.39 | 439 | 9.48 | 9.39 | 531 | 11.47 | 11.36 | 531 | 11.47 | 11.36 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {89B7FCA6-CAEE-4527-9ED4-B33F0F0AAC69}
6511 | 4475 | {1BBCA367-3D5B-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 2 (Banks 12, 13, 14) | CB 1103 | PGE\DMAL | 2017-03-15 12:04:03.8604513 -07:00 | 0228701103 | 083671108 | 7 | 3 | 3 | 2 | 426 | 9.2 | 9.11 | 426 | 9.2 | 9.11 | 524 | 11.32 | 11.21 | 524 | 11.32 | 11.21 | 439 | 9.48 | 9.39 | 439 | 9.48 | 9.39 | 531 | 11.47 | 11.36 | 531 | 11.47 | 11.36 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {8116F3EF-16AB-4D51-880E-4B4F3DD370CA}
6512 | 4475 | {0D20F9FA-3D5B-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 2 (Banks 12, 13, 14) | CB 1106 | PGE\DMAL | 2017-03-15 12:04:20.2745969 -07:00 | 0228701106 | 083671109 | 7 | 3 | 3 | 2 | 426 | 9.2 | 9.11 | 426 | 9.2 | 9.11 | 524 | 11.32 | 11.21 | 524 | 11.32 | 11.21 | 439 | 9.48 | 9.39 | 439 | 9.48 | 9.39 | 531 | 11.47 | 11.36 | 531 | 11.47 | 11.36 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {AC4B270D-DB8B-49A0-874E-49D2959026E7}
6513 | 4475 | {3C160E3F-BD96-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 2 (Banks 12, 13, 14) | CB 1107 | PGE\DMAL | 2017-03-15 12:04:31.4930101 -07:00 |  | 083671110 | 7 | 3 | 3 | 2 | 426 | 9.2 | 9.11 | 426 | 9.2 | 9.11 | 524 | 11.32 | 11.21 | 524 | 11.32 | 11.21 | 439 | 9.48 | 9.39 | 439 | 9.48 | 9.39 | 531 | 11.47 | 11.36 | 531 | 11.47 | 11.36 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {BA5F729A-6B2D-4E09-B2C7-EDE966F0A4E4}
6514 | 4475 | {15319B5E-3D5B-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 2 (Banks 12, 13, 14) | CB 1110 | PGE\DMAL | 2017-03-15 12:04:44.5213481 -07:00 | 0228701110 | 253642103 | 7 | 3 | 3 | 2 | 426 | 9.2 | 9.11 | 426 | 9.2 | 9.11 | 524 | 11.32 | 11.21 | 524 | 11.32 | 11.21 | 439 | 9.48 | 9.39 | 439 | 9.48 | 9.39 | 531 | 11.47 | 11.36 | 531 | 11.47 | 11.36 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {304DC583-3F28-4543-A836-88F0F0A896E3}
6515 | 4475 | {4A307E5A-BD96-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 12kv Bus 2 (Banks 12, 13, 14) | CB 1111 | PGE\DMAL | 2017-03-15 12:04:56.8631629 -07:00 |  | 253651111 | 7 | 3 | 3 | 2 | 426 | 9.2 | 9.11 | 426 | 9.2 | 9.11 | 524 | 11.32 | 11.21 | 524 | 11.32 | 11.21 | 439 | 9.48 | 9.39 | 439 | 9.48 | 9.39 | 531 | 11.47 | 11.36 | 531 | 11.47 | 11.36 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {E1AB7B1E-12C6-4EBF-AE59-FDF02C17E712}
6516 | 4483 | {A62E7132-917D-11E6-841B-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 1 (Banks 1, 5) | CB 3401 | PGE\DMAL | 2017-03-15 13:07:40.7835006 -07:00 |  | 253651112 | 13 | 3 | 3 | 2 | 346 | 20.68 | 20.47 | 346 | 20.68 | 20.47 | 426 | 25.46 | 25.21 | 426 | 25.46 | 25.21 | 356 | 21.27 | 21.06 | 356 | 21.27 | 21.06 | 431 | 25.75 | 25.49 | 431 | 25.75 | 25.49 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {BE7AAC9C-F80C-4F00-8EAF-807D107618D1}
6517 | 4483 | {F1176314-917D-11E6-841B-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 1 (Banks 1, 5) | CB 3404 | PGE\DMAL | 2017-03-15 13:07:57.4631076 -07:00 |  | 012061103 | 13 | 3 | 3 | 2 | 346 | 20.68 | 20.47 | 346 | 20.68 | 20.47 | 426 | 25.46 | 25.21 | 426 | 25.46 | 25.21 | 356 | 21.27 | 21.06 | 356 | 21.27 | 21.06 | 431 | 25.75 | 25.49 | 431 | 25.75 | 25.49 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {9E14F947-F5BE-4C13-8067-43848C56F580}
6518 | 4483 | {06C5A114-917E-11E6-841B-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 1 (Banks 1, 5) | CB 3405 | PGE\DMAL | 2017-03-15 13:08:09.9923166 -07:00 |  | 012061101 | 13 | 3 | 3 | 2 | 346 | 20.68 | 20.47 | 346 | 20.68 | 20.47 | 426 | 25.46 | 25.21 | 426 | 25.46 | 25.21 | 356 | 21.27 | 21.06 | 356 | 21.27 | 21.06 | 431 | 25.75 | 25.49 | 431 | 25.75 | 25.49 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {C6205327-D17F-4194-994A-65267B07F538}
6519 | 4483 | {2B4F63B8-917E-11E6-841B-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 1 (Banks 1, 5) | CB 3408 | PGE\DMAL | 2017-03-15 13:08:27.5144856 -07:00 |  | 022801120 | 13 | 3 | 3 | 2 | 346 | 20.68 | 20.47 | 346 | 20.68 | 20.47 | 426 | 25.46 | 25.21 | 426 | 25.46 | 25.21 | 356 | 21.27 | 21.06 | 356 | 21.27 | 21.06 | 431 | 25.75 | 25.49 | 431 | 25.75 | 25.49 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {D8E504BC-DA3A-4AD9-BE8F-38E1EB8889CC}
6520 | 4483 | {4EF0B924-917E-11E6-841B-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 1 (Banks 1, 5) | CB 3409 | PGE\DMAL | 2017-03-15 13:08:51.1218246 -07:00 |  | 022801128 | 13 | 3 | 3 | 2 | 346 | 20.68 | 20.47 | 346 | 20.68 | 20.47 | 426 | 25.46 | 25.21 | 426 | 25.46 | 25.21 | 356 | 21.27 | 21.06 | 356 | 21.27 | 21.06 | 431 | 25.75 | 25.49 | 431 | 25.75 | 25.49 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {EE8CFBDD-9FEC-446F-9CBF-4679BF1421C9}
6521 | 4484 | {E0B54D3E-917D-11E6-841B-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 2 (Banks 2, 3) | CB 3403 | PGE\DMAL | 2017-03-15 13:13:58.2960342 -07:00 |  | 022801135 | 13 | 3 | 3 | 2 | 346 | 20.68 | 20.47 | 346 | 20.68 | 20.47 | 426 | 25.46 | 25.21 | 426 | 25.46 | 25.21 | 356 | 21.27 | 21.06 | 356 | 21.27 | 21.06 | 431 | 25.75 | 25.49 | 431 | 25.75 | 25.49 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {5E7C878C-0B72-46A3-A3F0-9BD7CF8E3AD7}
6522 | 4484 | {110FB26C-917E-11E6-841B-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 2 (Banks 2, 3) | CB 3406 | PGE\DMAL | 2017-03-15 13:14:11.1215358 -07:00 |  | 022801136 | 13 | 3 | 3 | 2 | 399 | 23.84 | 23.6 | 399 | 23.84 | 23.6 | 491 | 29.34 | 29.05 | 491 | 29.34 | 29.05 | 411 | 24.56 | 24.31 | 411 | 24.56 | 24.31 | 497 | 29.7 | 29.4 | 497 | 29.7 | 29.4 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {2314F7FD-F18A-473B-B72F-F70F8551839B}
6523 | 4484 | {1E1B10BB-917E-11E6-841B-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 2 (Banks 2, 3) | CB 3407 | PGE\DMAL | 2017-03-15 13:14:28.4094382 -07:00 |  | 022801107 | 13 | 3 | 3 | 2 | 346 | 20.68 | 20.47 | 346 | 20.68 | 20.47 | 426 | 25.46 | 25.21 | 426 | 25.46 | 25.21 | 356 | 21.27 | 21.06 | 356 | 21.27 | 21.06 | 431 | 25.75 | 25.49 | 431 | 25.75 | 25.49 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {85169734-59D7-4DC5-89C0-6A063DF14295}
6524 | 4484 | {58E8934A-917E-11E6-841B-D4BED91EFF1A} | SAN FRANCISCO | EMBARCADERO (SF Z) | 34kv Bus 2 (Banks 2, 3) | CB 3410 | PGE\DMAL | 2017-03-15 13:16:51.0346330 -07:00 |  | 022801127 | 13 | 3 | 3 | 2 | 346 | 20.68 | 20.47 | 346 | 20.68 | 20.47 | 426 | 25.46 | 25.21 | 426 | 25.46 | 25.21 | 356 | 21.27 | 21.06 | 356 | 21.27 | 21.06 | 431 | 25.75 | 25.49 | 431 | 25.75 | 25.49 | 1000AL KCM 3/C 34KV ARMOR CABLE: SN=493_SE=685_WN=493_WE=685 amp. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {AE1B8C82-F65D-465A-A68A-D7E7C5F2DEA9}
6526 | 4528 | {120E70F1-3D5A-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | SF J | 12kv Bus 1 (ZJ-1, ZJ-2, ZJ- 3, ZJ- 4, ZJ- 5) | CB 1101 | PGE\DMAL | 2017-03-15 15:27:39.6228031 -07:00 | 0222201101 | 022801137 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {B2319316-0099-49D7-B652-D678CA8DD99B}
6527 | 4528 | {09DB5446-3D5A-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | SF J | 12kv Bus 1 (ZJ-1, ZJ-2, ZJ- 3, ZJ- 4, ZJ- 5) | CB 1102 | PGE\DMAL | 2017-03-15 15:31:06.0974597 -07:00 | 0222201102 | 022801138 | 7 | 3 | 3 | 2 | 320 | 6.91 | 6.84 | 320 | 6.91 | 6.84 | 355 | 7.67 | 7.59 | 355 | 7.67 | 7.59 | 330 | 7.13 | 7.06 | 330 | 7.13 | 7.06 | 366 | 7.91 | 7.83 | 366 | 7.91 | 7.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {271D0A2F-8555-4000-923D-9C61506B20E2}
6528 | 4528 | {120E70EE-3D5A-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | SF J | 12kv Bus 1 (ZJ-1, ZJ-2, ZJ- 3, ZJ- 4, ZJ- 5) | CB 1103 | PGE\DMAL | 2017-03-15 15:33:54.1885787 -07:00 | 0222201103 | 022801140 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {2A444E5C-695D-438E-8295-7E20F1A834AA}
6529 | 4528 | {0111CA8D-3D5A-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | SF J | 12kv Bus 1 (ZJ-1, ZJ-2, ZJ- 3, ZJ- 4, ZJ- 5) | CB 1104 | PGE\DMAL | 2017-03-15 15:35:44.2053317 -07:00 | 0222201104 | 022801141 | 7 | 3 | 3 | 2 | 320 | 6.91 | 6.84 | 320 | 6.91 | 6.84 | 355 | 7.67 | 7.59 | 355 | 7.67 | 7.59 | 330 | 7.13 | 7.06 | 330 | 7.13 | 7.06 | 366 | 7.91 | 7.83 | 366 | 7.91 | 7.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {FB3553A1-4CA3-4498-BFDA-0A6739AF0B1F}
6530 | 4528 | {FB0345B5-3D59-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | SF J | 12kv Bus 1 (ZJ-1, ZJ-2, ZJ- 3, ZJ- 4, ZJ- 5) | CB 1105 | PGE\DMAL | 2017-03-15 15:39:05.8424277 -07:00 | 0222201105 | 103071104 | 7 | 3 | 3 | 2 | 320 | 6.91 | 6.84 | 320 | 6.91 | 6.84 | 355 | 7.67 | 7.59 | 355 | 7.67 | 7.59 | 330 | 7.13 | 7.06 | 330 | 7.13 | 7.06 | 366 | 7.91 | 7.83 | 366 | 7.91 | 7.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {ED410E7E-FF60-433A-8120-113D2DD26494}
6531 | 4528 | {09DB5449-3D5A-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | SF J | 12kv Bus 1 (ZJ-1, ZJ-2, ZJ- 3, ZJ- 4, ZJ- 5) | CB 1106 | PGE\DMAL | 2017-03-15 15:41:28.4997424 -07:00 | 0222201106 | 103071105 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {3F2B93CE-2FBF-4C39-AE25-326B966CD713}
6532 | 4528 | {A23BBA97-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF J | 12kv Bus 1 (ZJ-1, ZJ-2, ZJ- 3, ZJ- 4, ZJ- 5) | CB 1107 | PGE\DMAL | 2017-03-27 12:37:46.0476077 -07:00 | 0222201107 | 103071106 | 7 | 3 | 3 | 2 | 1026 | 22.16 | 21.94 | 1026 | 22.16 | 21.94 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1046 | 22.59 | 22.36 | 1046 | 22.59 | 22.36 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {912E8104-5B51-4F35-9808-E63A107FB6B4}
6534 | 4528 | {504FF0D6-B806-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | SF J | 12kv Bus 1 (ZJ-1, ZJ-2, ZJ- 3, ZJ- 4, ZJ- 5) | CB J MUNI | PGE\DMAL | 2017-04-11 10:24:39.2809644 -07:00 |  | 102971101 | 7 | 3 | 3 | 2 | 230 | 4.97 | 4.92 | 230 | 4.97 | 4.92 | 230 | 4.97 | 4.92 | 230 | 4.97 | 4.92 | 230 | 4.97 | 4.92 | 230 | 4.97 | 4.92 | 230 | 4.97 | 4.92 | 230 | 4.97 | 4.92 | MUNI primary switchgear is inside of Station J. Space is leased by MUNI. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {00000000-0000-0000-0000-000000000000}
6535 | 4528 | {0E1867AE-B806-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | SF J | 12kv Bus 1 (ZJ-1, ZJ-2, ZJ- 3, ZJ- 4, ZJ- 5) | CB 1108 | PGE\DMAL | 2017-03-28 16:01:27.4041905 -07:00 |  | 102971102 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | Capacity Distribution Engineer will be responsible to update final ratings upon project completion |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {00000000-0000-0000-0000-000000000000}
6536 | 4529 | {87A8FE45-B807-11E6-93A9-D4BED91EFF1A} | SF J | 12KV BUS 1 (ZJ-1, ZJ-2, ZJ- 3, ZJ- 4, ZJ- 5) | Bank 1 | CB 403 | PGE\DMAL | 2017-03-15 16:29:34.9093040 -07:00 |  | 102971103 | 3 | 3 | 3 | 2 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 1665 | 2165 | 1998 | 2498 | {18037729-E610-425C-8561-B31E78038BE9}
6537 | 4529 | {93F58EDA-B807-11E6-93A9-D4BED91EFF1A} | SF J | 12KV BUS 1 (ZJ-1, ZJ-2, ZJ- 3, ZJ- 4, ZJ- 5) | Bank 1 | CB 407 | PGE\DMAL | 2017-03-28 15:56:54.1193970 -07:00 |  | 102971104 | 3 | 3 | 3 | 2 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2000 | {ADF7158A-4126-4D77-B0CC-A222E13E1BA4}
6538 | 4529 | {A355DBE4-B807-11E6-93A9-D4BED91EFF1A} | SF J | 12KV BUS 1 (ZJ-1, ZJ-2, ZJ- 3, ZJ- 4, ZJ- 5) | Bank 1 | CB 409 | PGE\DMAL | 2017-03-28 15:57:22.2514257 -07:00 |  | 102971105 | 3 | 3 | 3 | 2 | 365 | 2.63 | 2.6 | 365 | 2.63 | 2.6 | 394 | 2.84 | 2.81 | 394 | 2.84 | 2.81 | 376 | 2.71 | 2.68 | 376 | 2.71 | 2.68 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2000 | {1606E996-8C35-4FCD-9B02-5573085ED2DF}
6539 | 4528 | {49E99B9B-B807-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | SF J | 12kv Bus 1 (ZJ-1, ZJ-2, ZJ- 3, ZJ- 4, ZJ- 5) | CB D-E/12 | PGE\DMAL | 2017-03-28 16:01:52.4468450 -07:00 |  | 102971107 | 7 | 3 | 3 | 2 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {00000000-0000-0000-0000-000000000000}
6540 | 4528 | {593BA12B-B807-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | SF J | 12kv Bus 1 (ZJ-1, ZJ-2, ZJ- 3, ZJ- 4, ZJ- 5) | CB D-E/22 | PGE\DMAL | 2017-03-28 16:02:36.9931245 -07:00 |  | 102971109 | 7 | 3 | 3 | 2 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {00000000-0000-0000-0000-000000000000}
6542 | 4528 | {3441CE61-B807-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | SF J | 12kv Bus 1 (ZJ-1, ZJ-2, ZJ- 3, ZJ- 4, ZJ- 5) | CAP BK 1-2 | PGE\DMAL | 2017-03-28 15:58:17.7353381 -07:00 |  | 102971110 | 7 | 3 | 3 | 2 | 300 | 6.48 | 6.42 | 300 | 6.48 | 6.42 | 300 | 6.48 | 6.42 | 300 | 6.48 | 6.42 | 300 | 6.48 | 6.42 | 300 | 6.48 | 6.42 | 300 | 6.48 | 6.42 | 300 | 6.48 | 6.42 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {00000000-0000-0000-0000-000000000000}
6543 | 4527 | {E689FDF0-0E49-11E6-95F2-D4BED91EFF1A} | NORTH VALLEY | CENTERVILLE | BANK 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\JBJ8 | 2017-03-22 16:47:05.2796384 -07:00 | 102021101 | 102971111 | 7 | 4 | 4 | 1 | 92 | 1.99 | 1.97 | 92 | 1.99 | 1.97 | 110 | 2.38 | 2.36 | 110 | 2.38 | 2.36 | 110 | 2.38 | 2.36 | 110 | 2.38 | 2.36 | 110 | 2.38 | 2.36 | 110 | 2.38 | 2.36 | transferred from sharepoint | Centerville Bank 2 Net Capability | FALSE | FALSE | 92 | 120 | 111 | 138 | {186D604F-FA51-4C49-8FD4-C29EDA9760E7}
6546 | 4532 | {6CD4D2A6-BCBD-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB FY-1 | PGE\DMAL | 2017-03-15 18:43:49.3152190 -07:00 |  | 102650401 | 7 | 3 | 3 | 2 | 480 | 10.37 | 10.27 | 480 | 10.37 | 10.27 | 559 | 12.07 | 11.95 | 559 | 12.07 | 11.95 | 490 | 10.58 | 10.47 | 490 | 10.58 | 10.47 | 570 | 12.31 | 12.19 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {A400AB05-08C4-4513-9ED0-1404F1603CDA}
6547 | 4532 | {DA1D6EFB-F543-11E6-BC23-9CB70D532D7F} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB FY-2 | PGE\DMAL | 2017-03-15 18:45:15.8454985 -07:00 |  | 022331101 | 7 | 3 | 3 | 2 | 480 | 10.37 | 10.27 | 480 | 10.37 | 10.27 | 559 | 12.07 | 11.95 | 559 | 12.07 | 11.95 | 490 | 10.58 | 10.47 | 490 | 10.58 | 10.47 | 570 | 12.31 | 12.19 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {6B331950-CBB9-4A1F-89D4-49D2A0012549}
6548 | 4532 | {FA4F4C59-BCBC-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB FY-3 | PGE\DMAL | 2017-03-15 18:47:04.5506251 -07:00 |  | 022331102 | 7 | 3 | 3 | 2 | 517 | 11.17 | 11.06 | 517 | 11.17 | 11.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 527 | 11.38 | 11.27 | 527 | 11.38 | 11.27 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {B18D5950-322D-47D1-8601-DF7580E8015E}
6549 | 4532 | {0A2ED182-BCBD-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB FY-4 | PGE\DMAL | 2017-03-15 18:48:43.8105124 -07:00 |  | 022331103 | 7 | 3 | 3 | 2 | 517 | 11.17 | 11.06 | 517 | 11.17 | 11.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 527 | 11.38 | 11.27 | 527 | 11.38 | 11.27 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {617D9F98-8316-48B1-B854-D91A9AB611E8}
6550 | 4532 | {C1354A67-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB 1101 | PGE\DMAL | 2017-03-15 19:13:59.3564959 -07:00 | 0228001101 | 022331104 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {DAE1CEB2-5877-43EB-A0EE-AA17CC6F587E}
6551 | 4532 | {9BBBE063-BCBE-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB DE TIE/12 (Non-SCADA) | PGE\DMAL | 2017-03-28 16:28:02.2702169 -07:00 |  | 022331105 | 7 | 3 | 3 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {83AF8E65-129C-48A2-AA82-0E7CE2FC410A}
6552 | 4532 | {B6CD68F3-BCBE-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB EF TIE/12 (Non-SCADA) | PGE\DMAL | 2017-03-28 16:28:22.1015028 -07:00 |  | 022331106 | 7 | 3 | 3 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {8B5E2F58-8132-47C6-93F1-BB3AECB4448C}
6553 | 4532 | {8560FD0A-BCC1-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB CAP 3-4/12 (Non-SCADA) | PGE\DMAL | 2017-03-28 16:27:41.2531106 -07:00 |  | 022331107 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {CBC891BA-92B4-48FC-AFB8-CE3A65EC9E06}
6554 | 4533 | {AC64754F-BCBE-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB DE TIE/22 (Non-SCADA) | PGE\DMAL | 2017-03-28 16:53:57.3800541 -07:00 |  | 022331108 | 7 | 3 | 3 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {978A5141-7C90-4751-827C-6E838B7F2E93}
6555 | 4533 | {BF7215DB-BCBE-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB EF TIE/22 (Non-SCADA) | PGE\DMAL | 2017-03-28 16:54:17.0709139 -07:00 |  | 022331109 | 7 | 3 | 3 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {74099374-949D-433F-A746-E6C2FB618D17}
6556 | 4533 | {662806C0-BCC1-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB CAP 5-6/22 (Non-SCADA) | PGE\DMAL | 2017-03-28 16:53:13.4110819 -07:00 |  | 022801109 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {49EE1EF1-3EA5-4F51-A1D9-18E471755E99}
6557 | 4532 | {C86366FC-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB 1102 | PGE\DMAL | 2017-03-15 19:13:23.4542230 -07:00 | 0228001102 | 022801114 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {0FDF5D77-EE2F-40A9-A87E-6123623892CF}
6558 | 4532 | {C1354A64-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB 1103 | PGE\DMAL | 2017-03-15 19:16:08.9853891 -07:00 | 0228001103 | 022801115 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {9641CAC1-2587-4840-BA21-AE265458F3CB}
6559 | 4532 | {C86366FF-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB 1104 | PGE\DMAL | 2017-03-15 19:17:57.1134861 -07:00 | 0228001104 | 022801116 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {C6D489D9-0751-4C77-B136-6C3FB74425D3}
6560 | 4532 | {C86366F9-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB 1105 | PGE\DMAL | 2017-03-15 19:20:40.6318781 -07:00 | 0228001105 | 022801117 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {505B5D55-1F1C-476A-A276-1D74C8E1A119}
6561 | 4532 | {BA73D286-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB 1106 | PGE\DMAL | 2017-03-15 19:22:50.7756670 -07:00 | 0228001106 | 012061105 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {8B2FA6B8-D194-42F8-924B-6131454D4533}
6562 | 4532 | {002435B7-3C99-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB 1112 | PGE\DMAL | 2017-03-15 19:31:52.2587086 -07:00 | 0228001112 | 022801110 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {B4DB47A7-B871-46CF-BF4D-AD2F81569130}
6563 | 4532 | {F0F64FAB-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB 1113 | PGE\DMAL | 2017-04-04 12:20:37.9557417 -07:00 | 0228001113 | 022801111 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {09509747-AEB9-4D2A-8734-55327EEAA795}
6564 | 4533 | {F0F64FA8-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1121 | PGE\DMAL | 2017-03-15 19:37:22.9309683 -07:00 | 0228001121 | 022801119 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {F958F498-70F7-4B0D-810D-1FEF2A434B8E}
6565 | 4533 | {002435B4-3C99-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1122 | PGE\DMAL | 2017-03-15 19:38:48.4504632 -07:00 | 0228001122 | 022011105 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {2A32F231-67F4-4A0E-93F2-EBE012ABFCA3}
6566 | 4533 | {F0F64FA5-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1123 | PGE\DMAL | 2017-03-15 19:40:59.0155304 -07:00 | 0228001123 | 022011106 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {8000F2D7-E42A-4542-A066-E10799AF785C}
6567 | 4533 | {E9F92FFE-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1124 | PGE\DMAL | 2017-03-15 19:42:31.5407274 -07:00 | 0228001124 | 022011112 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {2408DE37-4484-455F-BBEC-35237C27F72B}
6568 | 4533 | {FA1B07A9-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1125 | PGE\DMAL | 2017-03-15 19:43:53.3155263 -07:00 | 0228001125 | 022011114 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {B359B0E8-12A3-48FC-9488-6B563B0AF3BF}
6569 | 4533 | {E9F92FFB-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1126 | PGE\DMAL | 2017-03-15 19:45:14.6846498 -07:00 | 0228001126 | 022011115 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {B7FCC3E9-3548-4EAD-9319-00E623B292B7}
6570 | 4533 | {E13AC48B-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1129 | PGE\DMAL | 2017-03-15 19:47:26.1234794 -07:00 | 0228001129 | 022011121 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {BDF18AFE-52FC-49C1-9147-6941AC5201AD}
6571 | 4530 | {A0864E4D-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | ORO FINO | Bank 1 | CB 1101 | PGE\JBJ8 | 2017-03-15 20:01:49.3005416 -07:00 | 1030301101 | 022011117 | 7 | 4 | 4 | 1 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | trasnferred from sharepoint |  | FALSE | FALSE | 721 | 721 | 721 | 721 | {05269492-85CE-438F-8F72-BCCF4C79200D}
6573 | 4530 | {A0864E56-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | ORO FINO | Bank 1 | CB 1102 | PGE\JBJ8 | 2017-03-16 16:45:38.7568068 -07:00 | 1030301102 | 022011123 | 7 | 4 | 4 | 1 | 300 | 6.48 | 6.42 | 285 | 6.16 | 6.1 | 381 | 8.23 | 8.15 | 361 | 7.8 | 7.72 | 333 | 7.19 | 7.12 | 316 | 6.83 | 6.76 | 403 | 8.7 | 8.61 | 382 | 8.25 | 8.17 | transferred from sharepoint |  | FALSE | FALSE | 486 | 631 | 583 | 721 | {A759F4C0-DCAE-48BD-A14A-E60659A7298F}
6575 | 4538 | {A0864F4C-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | PARADISE | Bank 1 | CB 1101 | PGE\JBJ8 | 2017-03-16 19:16:24.2426380 -07:00 | 1028301101 | 022010401 | 7 | 4 | 4 | 1 | 591 | 12.76 | 12.63 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 |  | Paradise Bank 1 Net Capability | FALSE | FALSE | 2083 | 2640 | 2200 | 2640 | {BE9F713D-DD49-47CD-B3C0-A3F488AD3586}
6577 | 4533 | {E13AC48E-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1130 | PGE\DMAL | 2017-03-16 19:29:40.1051901 -07:00 | 0228001130 | 022010402 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {5876C542-68AB-4CB6-9CB5-EF12BDF02E84}
6578 | 4533 | {E13AC488-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1131 | PGE\DMAL | 2017-03-16 19:30:58.0809873 -07:00 | 0228001131 | 022011101 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {786CD57C-9B82-4293-BD3B-E2AF173978BA}
6579 | 4533 | {DAC92782-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1132 | PGE\DMAL | 2017-03-16 19:32:12.5902098 -07:00 | 0228001132 | 022011102 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {C9BDCCA9-707C-4869-8075-6D867BAE78FE}
6580 | 4533 | {DAC9277F-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1133 | PGE\DMAL | 2017-03-16 19:33:18.1599519 -07:00 | 0228001133 | 022011104 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {EC297C9C-89E2-4F49-B659-7738FAC1997E}
6581 | 4533 | {D2F26C63-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1134 | PGE\DMAL | 2017-03-16 19:34:43.6985900 -07:00 | 0228001134 | 022011107 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {94682AD8-063D-4523-A215-82C34D98DEA4}
6582 | 4538 | {A0864F6A-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | PARADISE | Bank 1 | CB 1102 | PGE\JBJ8 | 2017-03-16 20:18:24.5044966 -07:00 | 1028301102 | 022011108 | 7 | 4 | 4 | 1 | 434 | 9.37 | 9.28 | 412 | 8.9 | 8.81 | 514 | 11.1 | 10.99 | 488 | 10.54 | 10.43 | 471 | 10.17 | 10.07 | 447 | 9.65 | 9.55 | 546 | 11.79 | 11.67 | 518 | 11.19 | 11.08 |  |  | FALSE | FALSE | 2083 | 2640 | 2200 | 2640 | {DFA92B6F-9F39-4CC2-9C08-A2685D2BC8C8}
6584 | 4538 | {A0864F88-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | PARADISE | Bank 1 | CB 1106 | PGE\JBJ8 | 2017-03-16 20:25:43.8977635 -07:00 | 1028301106 | 022011109 | 7 | 4 | 4 | 1 | 434 | 9.37 | 9.28 | 434 | 9.37 | 9.28 | 514 | 11.1 | 10.99 | 514 | 11.1 | 10.99 | 471 | 10.17 | 10.07 | 471 | 10.17 | 10.07 | 546 | 11.79 | 11.67 | 546 | 11.79 | 11.67 |  |  | FALSE | FALSE | 2083 | 2640 | 2200 | 2640 | {22658B5B-B6A0-4322-AEF2-1C4ADD08F0C5}
6586 | 4540 | {A0864FA2-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | PARADISE | Bank 2 | CB 1103 | PGE\JBJ8 | 2017-03-22 17:34:35.8885842 -07:00 | 1028301103 | 022011110 | 7 | 4 | 4 | 1 | 591 | 12.76 | 12.63 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | transferred from sharepoint |  | FALSE | FALSE | 2083 | 2640 | 2200 | 2640 | {F09D7AE9-096A-4278-A242-9BDC4D50088B}
6589 | 4540 | {A0864FCF-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | PARADISE | Bank 2 | CB 1104 | PGE\JBJ8 | 2017-03-22 17:33:52.6760302 -07:00 | 1028301104 | 022011111 | 7 | 4 | 4 | 1 | 591 | 12.76 | 12.63 | 591 | 12.76 | 12.63 | 667 | 14.41 | 14.27 | 667 | 14.41 | 14.27 | 642 | 13.87 | 13.73 | 642 | 13.87 | 13.73 | 667 | 14.41 | 14.27 | 667 | 14.41 | 14.27 | transferred from sharepoint |  | FALSE | FALSE | 2083 | 2640 | 2200 | 2640 | {E2EA901E-8298-4874-8B1B-2749569DD1BF}
6591 | 4540 | {A0865009-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | PARADISE | Bank 2 | CB 1105 | PGE\JBJ8 | 2017-03-16 21:19:21.8536778 -07:00 | 1028301105 | 022011113 | 7 | 4 | 4 | 1 | 591 | 12.76 | 12.63 | 591 | 12.76 | 12.63 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | transferred from sharepoint |  | FALSE | FALSE | 2083 | 2640 | 2200 | 2640 | {F1082DAA-279E-4B24-B1FB-8A7B4202C2CA}
6592 | 4550 | {BBF46B7A-C0B3-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | BAYSHORE | Bank 1 | CB 3401 (Non-SCADA) | PGE\DMAL | 2017-03-27 11:50:59.6407075 -07:00 |  | 022011116 | 13 | 3 | 3 | 2 | 836 | 49.96 | 49.46 | 836 | 49.96 | 49.46 | 1000 | 59.76 | 59.16 | 1000 | 59.76 | 59.16 | 1000 | 59.76 | 59.16 | 1000 | 59.76 | 59.16 | 1000 | 59.76 | 59.16 | 1000 | 59.76 | 59.16 | Billing Metering CT = 800/5. This is capable of handling 150% of continuous load. MISSING CABLE: 1750MCM LPG 35kV 3/C AL (SN = SE = WN = WE = 1000amp) |  | FALSE | FALSE | 836 | 1087 | 1004 | 1200 | {00000000-0000-0000-0000-000000000000}
6593 | 4551 | {BBF46B7D-C0B3-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | BAYSHORE | Bank 2 | CB 3402 (Non-SCADA) | PGE\DMAL | 2017-03-27 11:52:37.7659655 -07:00 |  | 022011118 | 13 | 3 | 3 | 2 | 836 | 49.96 | 49.46 | 836 | 49.96 | 49.46 | 1000 | 59.76 | 59.16 | 1000 | 59.76 | 59.16 | 1000 | 59.76 | 59.16 | 1000 | 59.76 | 59.16 | 1000 | 59.76 | 59.16 | 1000 | 59.76 | 59.16 | Billing Metering CT = 800/5. This is capable of handling 150% of continuous load. MISSING CABLE: 1750MCM LPG 35kV 3/C AL (SN = SE = WN = WE = 1000amp) |  | FALSE | FALSE | 836 | 1087 | 1004 | 1200 | {00000000-0000-0000-0000-000000000000}
6594 | 4552 | {5A011848-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | 6TH AVENUE | Bank 1 (Non SCADA) | CB 401 (Non-SCADA) | PGE\DMAL | 2017-03-28 17:28:47.8721990 -07:00 | 022530401 | 022011120 | 3 | 3 | 3 | 2 | 277 | 2 | 1.98 | 277 | 2 | 1.98 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | Bank Limited |  | FALSE | FALSE | 277 | 360 | 333 | 400 | {2F4BA124-8AD6-4659-8DF7-6AD107617F78}
6595 | 4553 | {5A01184E-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | 6TH AVENUE | Bank 2 (Non SCADA) | CB 402 (Non-SCADA) | PGE\DMAL | 2017-03-28 17:29:40.5943981 -07:00 | 022530402 | 022011124 | 3 | 3 | 3 | 2 | 277 | 2 | 1.98 | 277 | 2 | 1.98 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | Bank Limited |  | FALSE | FALSE | 277 | 360 | 333 | 400 | {790486E3-FCF7-4FF0-9335-7AB9CD0D2D82}
6628 | 4574 | {A0864F2E-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | PANORAMA | Bank 1 | CB 1102 | PGE\AxDj | 2017-03-27 20:39:46.9223632 -07:00 | 1034601102 | 022011125 | 8 | 4 | 4 | 1 | 514 | 11.22 | 11.11 | 514 | 11.22 | 11.11 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 570 | 12.44 | 12.32 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1370 | 1781 | 1644 | 2055 | {65A7EF2A-11FF-4A98-8544-F341E57DF6D3}
6629 | 4576 | {A6861D4D-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | STILLWATER | Bank 1 | CB 1101 | PGE\AxDj | 2017-03-27 20:48:50.5430021 -07:00 | 1035601101 | 103391101 | 8 | 4 | 4 | 1 | 345 | 7.53 | 7.45 | 345 | 7.53 | 7.45 | 386 | 8.42 | 8.34 | 386 | 8.42 | 8.34 | 443 | 9.67 | 9.57 | 443 | 9.67 | 9.57 | 473 | 10.32 | 10.22 | 473 | 10.32 | 10.22 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {BD9254DD-CB8A-499F-97F1-E365E2B1415A}
6630 | 4576 | {A6861D64-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | STILLWATER | Bank 1 | CB 1102 | PGE\AxDj | 2017-03-27 20:49:43.2339954 -07:00 | 1035601102 | 103391102 | 8 | 4 | 4 | 1 | 345 | 7.53 | 7.45 | 345 | 7.53 | 7.45 | 386 | 8.42 | 8.34 | 386 | 8.42 | 8.34 | 443 | 9.67 | 9.57 | 443 | 9.67 | 9.57 | 473 | 10.32 | 10.22 | 473 | 10.32 | 10.22 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {F2CF8AE3-FF93-44D6-A155-BF2D716EFF2E}
6631 | 4577 | {9A705DE0-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | OREGON TRAIL | Bank 1 | CB 1102 | PGE\AxDj | 2017-03-27 20:54:59.3175436 -07:00 | 1035201102 | 103541103 | 8 | 4 | 4 | 1 | 263 | 5.74 | 5.68 | 263 | 5.74 | 5.68 | 343 | 7.49 | 7.42 | 343 | 7.49 | 7.42 | 316 | 6.9 | 6.83 | 316 | 6.9 | 6.83 | 395 | 8.62 | 8.53 | 395 | 8.62 | 8.53 | limiting factor is the bank: bank capabilities mva/amps: use at your own risk SUMMER NORMAL SUMMER EMERGENCY WINTER NORMAL WINTER EMERGENCY 5.46 / 250 7.10 / 325 6.56 / 301 8.20 / 376 |  | FALSE | FALSE | 263 | 343 | 316 | 395 | {E2774944-24DB-4F14-B60A-9270223838C4}
6632 | 4578 | {9A705E01-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | OREGON TRAIL | Bank 2 | CB 1103 | PGE\AxDj | 2017-03-27 20:57:57.7367051 -07:00 | 1035201103 | 103541104 | 8 | 4 | 4 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {5FB0D40D-F2F5-49B7-8931-544C2AB12270}
6633 | 4578 | {9A705E19-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | OREGON TRAIL | Bank 2 | CB 1104 | PGE\AxDj | 2017-03-27 21:02:50.0882424 -07:00 | 1035201104 | 103541101 | 8 | 4 | 4 | 1 | 383 | 8.36 | 8.28 | 383 | 8.36 | 8.28 | 383 | 8.36 | 8.28 | 383 | 8.36 | 8.28 | 383 | 8.36 | 8.28 | 383 | 8.36 | 8.28 | 383 | 8.36 | 8.28 | 383 | 8.36 | 8.28 | axdj notes: circuit capability: use at your own risk: Summer Winter Nor Emg Nor Emg 380 578 380 711 |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {54C359F5-667A-4573-BF6D-1D0BCE797C14}
6634 | 4532 | {7914A3A6-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB 1108 | PGE\DMAL | 2017-04-10 12:53:00.8797123 -07:00 | 0228001108 | 103541102 | 7 | 3 | 3 | 2 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | Y-1108AB is limited by station length UG splice/connectors SN=SE=WN=WE=600amp: Standby to Federal Building when Y-1109AB is out. Y-1108C is limited 750T - 15kV Shielded PL&N - 4ELC (SN=467_SE=523_WN=481_WE=539). Serves customers. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {7B4426DD-A490-444F-96D3-71769C49E9E5}
7822 | 4635 | {BB6141E7-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CLAYTON | Bank 1 | CB 2216 | PGE\FCR1 | 2017-04-21 14:58:19.1177174 -07:00 | 0120202216 | 103191101 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 792 | 29.93 | 29.63 | 792 | 29.93 | 29.63 | 691 | 26.12 | 25.86 | 691 | 26.12 | 25.86 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {23496C49-007C-43D1-804C-D0B4A8E98C3D}
7823 | 4635 | {BB6141FC-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CLAYTON | Bank 1 | CB 2218 | PGE\FCR1 | 2017-04-21 14:58:37.7007713 -07:00 | 0120202218 | 103201101 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 732 | 27.66 | 27.38 | 732 | 27.66 | 27.38 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {6103EA7A-D539-4E84-8317-C28234811730}
7824 | 4636 | {BB614208-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CLAYTON | Bank 2 | CB 2215 | PGE\FCR1 | 2017-04-21 14:59:50.5351085 -07:00 | 0120202215 | 103201102 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 792 | 29.93 | 29.63 | 792 | 29.93 | 29.63 | 691 | 26.12 | 25.86 | 691 | 26.12 | 25.86 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {3F7B665C-CB98-4CDA-91DC-A46A8249E48C}
7825 | 4636 | {C1A1E374-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CLAYTON | Bank 2 | CB 2217 | PGE\FCR1 | 2017-04-20 16:34:58.8142055 -07:00 | 0120202217 | 103221101 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 674 | 25.47 | 25.22 | 674 | 25.47 | 25.22 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {0A91905E-FA20-4AF6-8BA3-519EF34F3C1D}
7826 | 4637 | {C1A1E392-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CLAYTON | Bank 3 | CB 2211 | PGE\FCR1 | 2017-04-20 16:39:50.2902107 -07:00 | 0120202211 | 102521101 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {89181D23-301D-4F02-BF70-F8F01ED726F1}
7827 | 4639 | {A72330FF-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PLACER | Bank 2 | CB 1101 | PGE\MTN6 | 2017-04-20 17:09:25.4385175 -07:00 | 1524601101 | 102521102 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1146 | 1489 | 1375 | 1718 | {5CD736B3-51EF-4E87-B7E4-C4E3DE573FFD}
7829 | 4637 | {C1A1E3AA-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CLAYTON | Bank 3 | CB 2212 | PGE\FCR1 | 2017-04-20 16:41:27.8700872 -07:00 | 0120202212 | 102521103 | 12 | 3 | 3 | 1 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 | 700 | 26.46 | 26.2 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {3CB5179B-70AA-4056-8961-D2F929587FD5}
7830 | 4637 | {C7A1366A-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CLAYTON | Bank 3 | CB 2214 | PGE\FCR1 | 2017-04-21 15:02:54.5089024 -07:00 | 0120202214 | 102521104 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 674 | 25.47 | 25.22 | 674 | 25.47 | 25.22 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {7658A512-0A0A-49D5-84F3-20C81094FEFC}
7831 | 4631 | {9ED2E416-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | BRITTON | Bank 2 | CB 1107 | PGE\MSJ9 | 2017-04-20 18:11:01.4378666 -07:00 | 0836101107 | 024251103 | 7 | 3 | 3 | 2 | 564 | 12.18 | 12.06 | 564 | 12.18 | 12.06 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | SW 1341 - 8 hour emergency rating of 800 Amps Relay Minimum Phase: 720A T 6 L 3 CT Ratio: 600:5 To Operate Ground: 180A T 1.5 L 3 Ammeter Range 0 to 100 |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {DF6DEE82-8C9A-45E1-A22B-0C9707F10EA4}
7834 | 4631 | {9ED2E434-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | BRITTON | Bank 2 | CB 1108 | PGE\MSJ9 | 2017-04-20 17:02:03.3927576 -07:00 | 0836101108 | 083371112 | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | SW 22995 - 8 hour emergency rating of 800 Amps 1/28/2015:(irb2) Updated OH conductor capability, this increased normal Relay Minimum Phase: 720A T 6 L 3 CT Ratio: 600:5 To Operate Ground: 180A T 1.5 L 1.5 Ammeter Range 0 to 100 |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {629D324F-88FF-4878-A882-15BC03FA9BEC}
7835 | 4639 | {A7233108-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PLACER | Bank 2 | CB 1102 | PGE\MTN6 | 2017-04-20 16:55:20.7755260 -07:00 | 1524601102 | 083371113 | 8 | 3 | 3 | 1 | 900 | 19.64 | 19.44 | 855 | 18.66 | 18.47 | 1000 | 21.82 | 21.6 | 1000 | 21.82 | 21.6 | 900 | 19.64 | 19.44 | 855 | 18.66 | 18.47 | 1000 | 21.82 | 21.6 | 1000 | 21.82 | 21.6 |  |  | FALSE | FALSE | 1146 | 1489 | 1375 | 1718 | {A10EE301-45EF-4C18-BCC4-A680A6B046BC}
7836 | 4638 | {C7A13679-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CLAYTON | Bank 5 | CB 1103 | PGE\FCR1 | 2017-04-21 15:06:47.5070081 -07:00 | 0120201103 | 083371114 | 8 | 3 | 3 | 1 | 282 | 6.15 | 6.09 | 267 | 5.83 | 5.77 | 315 | 6.87 | 6.8 | 299 | 6.53 | 6.46 | 358 | 7.81 | 7.73 | 340 | 7.42 | 7.35 | 382 | 8.34 | 8.26 | 362 | 7.9 | 7.82 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {566C506D-3526-4244-A405-C38C1C93E13D}
7837 | 4638 | {C7A13684-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CLAYTON | Bank 5 | CB 1104 | PGE\FCR1 | 2017-04-20 16:59:11.0461325 -07:00 | 0120201104 | 083371115 | 8 | 3 | 3 | 1 | 422 | 9.21 | 9.12 | 422 | 9.21 | 9.12 | 536 | 11.7 | 11.58 | 536 | 11.7 | 11.58 | 468 | 10.21 | 10.11 | 468 | 10.21 | 10.11 | 566 | 12.35 | 12.23 | 566 | 12.35 | 12.23 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {4831C7A2-3300-433E-AEE7-2A743E56D2B6}
7838 | 4631 | {9ED2E43D-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | BRITTON | Bank 2 | CB 1109 | PGE\MSJ9 | 2017-04-20 18:11:53.5983613 -07:00 | 0836101109 | 083611105 | 7 | 3 | 3 | 2 | 564 | 12.18 | 12.06 | 564 | 12.18 | 12.06 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | SW 10501 - 8 hour emergency rating of 800 Amps Relay Minimum Phase: 720A T 6 L 3 CT Ratio: 600:5 To Operate Ground: 180A T 1.5 L 1.5 Ammeter Range 0 to 100 |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {43E3835D-40BB-4D64-933F-B9B57CDF2DC2}
8123 | 4745 | {DAB1BF62-3C97-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | BEACH (SF Q) | BANK 2 (QF-1) | CB 402 (Non-SCADA) | PGE\DMAL | 2017-05-11 18:04:32.9975819 -07:00 | 022340402 | 102121101 | 3 | 3 | 3 | 2 | 277 | 2 | 1.98 | 277 | 2 | 1.98 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 277 | 360 | 333 | 400 | {E32D8232-7801-4577-BFC2-63A3A3B6243A}
8124 | 4746 | {AE9AF483-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | YOSEMITE | Bank 1 | CB 401 (Non-SCADA) | PGE\DMAL | 2017-05-11 18:27:17.4622211 -07:00 | 022490401 | 102121102 | 3 | 3 | 3 | 2 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 555 | 721 | 666 | 800 | {73A19CE3-89EE-4E07-BF55-437CA55D0C15}
8125 | 4746 | {AE9AF486-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | YOSEMITE | Bank 1 | CB 402 (Non-SCADA) | PGE\DMAL | 2017-05-11 18:31:00.6245126 -07:00 | 022490402 | 022781101 | 3 | 3 | 3 | 2 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 555 | 721 | 666 | 800 | {4B50D8B5-BF85-4C5E-83D4-7BAD0DE866ED}
8126 | 4747 | {AE9AF48C-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | YOSEMITE | Bank 2 | CB 403 (Non-SCADA) | PGE\DMAL | 2017-05-12 14:49:49.3252900 -07:00 | 022490403 | 022781103 | 3 | 3 | 3 | 2 | 319 | 2.3 | 2.28 | 319 | 2.3 | 2.28 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 383 | 2.76 | 2.73 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 319 | 400 | 383 | 400 | {7FB7CC6E-A98B-48F0-894D-6923DAADB071}
8127 | 4269 | {204BF3A3-4AAF-11E6-AFF0-80000BC6CD8D} | EAST BAY | OAKLAND X | Bank 2 | CB 1102 | PGE\C7CF | 2017-05-23 17:09:22.8053566 -07:00 | 012541102 | 022781102 | 7 | 3 | 3 | 2 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {0E8BB8A8-1739-4804-BE11-91BC16B6A2EA}
8128 | 4750 | {AE9AF46E-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | TARAVAL | Bank 1 | CB 401 (Non-SCADA) | PGE\DMAL | 2017-05-12 15:08:51.6553461 -07:00 | 022500401 | 022780401 | 3 | 3 | 3 | 2 | 277 | 2 | 1.98 | 277 | 2 | 1.98 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 277 | 360 | 333 | 416 | {5046044E-BBE4-4E00-BE08-1925B0366DD5}
8129 | 4749 | {AE9AF474-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | TARAVAL | Bank 2 | CB 402 (Non-SCADA) | PGE\DMAL | 2017-05-12 15:14:36.5712224 -07:00 | 022500402 | 022780402 | 3 | 3 | 3 | 2 | 319 | 2.3 | 2.28 | 319 | 2.3 | 2.28 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 383 | 2.76 | 2.73 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 319 | 414 | 383 | 478 | {F7A67E4A-96C1-423B-9AF1-B67CF6D8DDA8}
8130 | 4748 | {AE9AF47A-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | TARAVAL | Bank 3 | CB 403 (Non-SCADA) | PGE\DMAL | 2017-05-12 15:17:54.5909075 -07:00 | 022500403 | 022780403 | 3 | 3 | 3 | 2 | 319 | 2.3 | 2.28 | 319 | 2.3 | 2.28 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 383 | 2.76 | 2.73 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 319 | 414 | 383 | 478 | {329B3629-D8A1-47B9-BE88-E2387537691C}
8131 | 4751 | {66585543-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | CASTRO | Bank 1 | CB 401 (Non-SCADA) | PGE\DMAL | 2017-05-12 19:26:31.7108376 -07:00 | 022480401 | 022780404 | 3 | 3 | 3 | 2 | 319 | 2.3 | 2.28 | 319 | 2.3 | 2.28 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 383 | 2.76 | 2.73 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 319 | 414 | 383 | 432 | {B94CC324-D0C3-4D2A-BF52-66EA45BC8EA9}
8132 | 4752 | {66585549-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | CASTRO | Bank 2 | CB 402 (Non-SCADA) | PGE\DMAL | 2017-05-12 19:30:59.7932664 -07:00 | 022480402 | 082991101 | 3 | 3 | 3 | 2 | 277 | 2 | 1.98 | 277 | 2 | 1.98 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 277 | 360 | 333 | 416 | {87B5E951-A14A-4469-B6A7-914C9A786E23}
8133 | 4613 | {7152DB68-368C-11E7-813A-005056AE4E7D} | SAN FRANCISCO | MARINA (SF F) | 12kv Bus 1 (FY-1, FY-2, FY-3, FY-4) | CB 1103 | PGE\DMAL | 2017-05-12 19:46:48.1130173 -07:00 | 022781103 | 082991102 | 21 | 3 | 3 | 2 | 517 | 10.75 | 10.64 | 517 | 10.75 | 10.64 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 | 527 | 10.95 | 10.84 | 527 | 10.95 | 10.84 | 600 | 12.47 | 12.35 | 600 | 12.47 | 12.35 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {00000000-0000-0000-0000-000000000000}
8134 | 4430 | {E7BAE640-3C97-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | 21ST AVENUE | BANK 2 | CB 402 (Non-SCADA) | PGE\DMAL | 2017-05-12 20:36:06.2397478 -07:00 | 022550402 | 022780405 | 3 | 3 | 3 | 2 | 346 | 2.49 | 2.47 | 346 | 2.49 | 2.47 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 346 | 451 | 416 | 520 | {74DB5C77-316A-41F9-BF2E-E8A3AE9FE4DE}
8135 | 4431 | {77E5E045-3D5A-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | 21ST AVENUE | BANK 3 | CB 403 (Non-SCADA) | PGE\DMAL | 2017-05-12 20:41:20.3442416 -07:00 | 022550403 | 082991103 | 3 | 3 | 3 | 2 | 319 | 2.3 | 2.28 | 319 | 2.3 | 2.28 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 383 | 2.76 | 2.73 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 319 | 414 | 383 | 432 | {ABBE774E-DA58-4273-AF15-FF767CE6F353}
8136 | 4754 | {599CBB8C-3D5A-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | JUDAH | Bank 1 | CB 401 (Non-SCADA) | PGE\DMAL | 2017-05-12 21:23:14.1162340 -07:00 | 022400401 | 082991104 | 3 | 3 | 3 | 2 | 277 | 2 | 1.98 | 277 | 2 | 1.98 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 277 | 360 | 333 | 416 | {5F30A8FF-8EB4-4227-A60D-3BD05C4D31CE}
8137 | 4755 | {5366C451-3D5A-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | JUDAH | Bank 2 | CB 402 (Non-SCADA) | PGE\DMAL | 2017-05-12 21:27:23.9458438 -07:00 | 022400402 | 022780407 | 3 | 3 | 3 | 2 | 277 | 2 | 1.98 | 277 | 2 | 1.98 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 277 | 360 | 333 | 416 | {EDE72AB5-A1B1-46E5-AE7A-66D360B3713A}
8138 | 4756 | {A609EB39-3D5A-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | PORTOLA | BANK 1 | CB 401 (Non-SCADA) | PGE\DMAL | 2017-05-12 21:33:07.4108550 -07:00 | 022610401 | 022780408 | 3 | 3 | 3 | 2 | 277 | 2 | 1.98 | 277 | 2 | 1.98 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 277 | 360 | 333 | 416 | {ECD4ECC7-8FD3-459A-9252-EF4592BFBD9B}
8139 | 4757 | {9E2F7BFB-3D5A-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | PORTOLA | BANK 2 | CB 402 (Non-SCADA) | PGE\DMAL | 2017-05-12 21:37:34.8224537 -07:00 | 022610402 | 082991105 | 3 | 3 | 3 | 2 | 277 | 2 | 1.98 | 277 | 2 | 1.98 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 277 | 360 | 333 | 416 | {F570CD35-375A-4D60-BE9F-0ABCD5DFF8FE}
8140 | 4730 | {58DA2F8F-B8DA-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | SF K | 12kv Main Bus (KX-1, KX-2, KX-3, KX-4) | CB D-E TIE/2 | PGE\DMAL | 2017-05-16 10:44:25.7983842 -07:00 |  | 014101101 | 7 | 3 | 3 | 2 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {0DA8AB29-CA55-4D18-B92F-64BBD34FC5E7}
8142 | 4730 | {E6BD2CC9-B8DC-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | SF K | 12kv Main Bus (KX-1, KX-2, KX-3, KX-4) | CB E BUS TIE/2 (E PAR/2) | PGE\DMAL | 2017-05-16 10:32:55.0773917 -07:00 |  | 082991106 | 7 | 3 | 3 | 2 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {A18E0E0C-7B93-417D-8433-F428093732CD}
8143 | 4730 | {F591336F-B8D9-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | SF K | 12kv Main Bus (KX-1, KX-2, KX-3, KX-4) | CB 1101 | PGE\DMAL | 2017-05-16 10:43:44.7841439 -07:00 |  | 082991107 | 7 | 3 | 3 | 2 | 505 | 10.91 | 10.8 | 505 | 10.91 | 10.8 | 586 | 12.66 | 12.53 | 570 | 12.31 | 12.19 | 515 | 11.12 | 11.01 | 515 | 11.12 | 11.01 | 598 | 12.92 | 12.79 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {F41B15A1-52EF-4CD9-A184-E10DDCC2C5B2}
8145 | 4591 | {71CB6596-2DA0-11E6-B38D-D4BED91EFF1A} | EAST BAY | BERKELEY F | 12kv Bus 1 (FG-1, FG-2, FG-3, FG-4) | CB 1102 | PGE\C7CF | 2017-05-23 10:49:17.7237828 -07:00 | 0120601102 | 082991108 | 7 | 3 | 3 | 2 | 397 | 8.57 | 8.48 | 397 | 8.57 | 8.48 | 448 | 9.68 | 9.58 | 448 | 9.68 | 9.58 | 412 | 8.9 | 8.81 | 412 | 8.9 | 8.81 | 461 | 9.96 | 9.86 | 461 | 9.96 | 9.86 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {BE354560-D959-4AE4-8861-2F9D7EBE7F31}
8148 | 4758 | {B7382973-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WOLFE | Bank 1 | CB 1104 | PGE\MSJ9 | 2017-05-16 17:23:22.3033620 -07:00 | 0836701104 | 082991109 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {CC9CFA76-5672-4D67-B32F-444B8DCCF179}
8150 | 4758 | {B738298A-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WOLFE | Bank 1 | CB 1105 | PGE\MSJ9 | 2017-05-16 17:23:12.8805392 -07:00 | 0836701105 | 082991110 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | Relay Minimum Phase: 720A T 6.0 L 3.0 CT Ratio: 600:5 To Operate Ground: 182A T 1.5 L 2 Ammeter Range 0 to 100 Comments: INSTANTANEOUS = 4800A |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {3C0674AC-88CB-49C4-AA8E-8F39C916FC3D}
8151 | 4758 | {B73829A1-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WOLFE | Bank 1 | CB 1106 | PGE\MSJ9 | 2017-05-16 17:25:11.5082620 -07:00 | 0836701106 | 083611106 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | Relay Minimum Phase: 720A T 6.0 L 3.0 CT Ratio: 600:5 To Operate Ground: 182A T 1.5 L 2.0 Ammeter Range 0 to 100 Comments: INSTANTANEOUS = 4800A |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {B64D9A91-8EC7-4F2B-B1E5-E399C3341768}
8154 | 4759 | {B73829AE-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WOLFE | Bank 2 | CB 1107 | PGE\MSJ9 | 2017-05-16 17:30:28.5456874 -07:00 | 0836701107 | 014101102 | 7 | 3 | 3 | 2 | 564 | 12.18 | 12.06 | 564 | 12.18 | 12.06 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | Relay Minimum Phase: 720A T 6.0 L 2.0 CT Ratio: 600:5 To Operate Ground: 180A T 1.5 L 2.0 Ammeter Range 0 to 100 Comments: INSTANTANEOUS = 4800A |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {6B969BA0-570A-4BEB-AF89-32D86B7D0BEF}
8155 | 4280 | {08EB74F0-22D1-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND K | Bank 2 | CB 1102 | PGE\C7CF | 2017-05-31 16:35:02.7024733 -07:00 | 0121001102 | 014101105 | 7 | 3 | 3 | 2 | 344 | 7.43 | 7.36 | 344 | 7.43 | 7.36 | 447 | 9.65 | 9.55 | 447 | 9.65 | 9.55 | 412 | 8.9 | 8.81 | 412 | 8.9 | 8.81 | 515 | 11.12 | 11.01 | 515 | 11.12 | 11.01 |  |  | FALSE | FALSE | 1736 | 2257 | 2083 | 2604 | {10759ED0-BD2F-4C46-914D-A185F52EA58C}
8156 | 4280 | {08EB74F3-22D1-11E6-AE4A-D4BED91EFF1A} | EAST BAY | OAKLAND K | Bank 2 | CB 1104 | PGE\C7CF | 2017-06-05 15:54:26.8115185 -07:00 | 0121001104 | 013850401 | 7 | 3 | 3 | 2 | 475 | 10.26 | 10.16 | 475 | 10.26 | 10.16 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 489 | 10.56 | 10.45 | 489 | 10.56 | 10.45 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 |  |  | FALSE | FALSE | 1736 | 2257 | 2083 | 2604 | {B1184214-1973-4AC5-8808-44D919C36974}
8159 | 4759 | {B73829C5-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WOLFE | Bank 2 | CB 1108 | PGE\MSJ9 | 2017-05-19 10:52:38.8923809 -07:00 | 0836701108 | 012022213 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | Relay Minimum Phase: 800A T 5.0 L 3.0 CT Ratio: 600:5 To Operate Ground: 161A T 1.0 L 3.0 Ammeter Range 0 to 100 Comments: INSTANTANEOUS = 7200A |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {5CBA095E-B458-4075-977F-894986D73D23}
8160 | 4759 | {B73829CE-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WOLFE | Bank 2 | CB 1109 | PGE\MSJ9 | 2017-05-19 10:56:53.2798171 -07:00 | 0836701109 | 152461103 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | Relay Minimum Phase: 720A T 6.0 L 2.5 CT Ratio: 600:5 To Operate Ground: 182A T 1.5 L 3.0 Ammeter Range 0 to 100 Comments: INSTANTANEOUS = 4800A |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {7DCAB1D0-C0D3-4008-A163-3D8DF68897B7}
8161 | 4759 | {B73829D7-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WOLFE | Bank 2 | CB 1110 | PGE\MSJ9 | 2017-05-19 11:01:50.3995261 -07:00 | 0836701110 | 012960401 | 7 | 4 | 4 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | Relay Minimum Phase: 720A T 6 L 4.0 CT Ratio: 600:5 To Operate Ground: 180A T 1.5 L 1.5 Ammeter Range 0 to 100 Comments: * 3 spans of 397AL on Homestead rated @ 4ft/sec wind speed. |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {EAFDECD7-839F-4937-9BE4-F39988778371}
8162 | 2767 | {EA599E13-5FFE-11E6-9BE4-80000BC6CD8D} | KERN | POSO MOUNTAIN | Bank 2 | CB 2103 | PGE\JCS9 | 2017-05-22 09:19:21.8547539 -07:00 | 253642103 | 083611110 | 12 | 3 | 3 | 1 | 515 | 19.46 | 19.27 | 489 | 18.48 | 18.3 | 578 | 21.84 | 21.62 | 549 | 20.75 | 20.54 | 666 | 25.17 | 24.92 | 632 | 23.89 | 23.65 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 | This is 3W 21kV |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {89FED8D6-BD51-4618-8F08-144DA25FD16F}
8164 | 2745 | {2D2A340A-2F5E-11E6-B38D-D4BED91EFF1A} | KERN | SHAFTER | BANK 3 | CB 1111 | PGE\JCS9 | 2017-05-22 14:34:41.7084200 -07:00 | 2536501111 | 083611111 | 8 | 3 | 3 | 1 | 636 | 13.88 | 13.74 | 636 | 13.88 | 13.74 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {D3B19AF1-57EE-4255-B250-66D289A25D95}
8166 | 2745 | {3453C2E2-2F5E-11E6-B38D-D4BED91EFF1A} | KERN | SHAFTER | BANK 3 | CB 1112 | PGE\JCS9 | 2017-05-22 14:47:20.5947425 -07:00 | 2536501112 | 152461104 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 666 | 14.53 | 14.38 | 632 | 13.79 | 13.65 | 667 | 14.56 | 14.41 | 633 | 13.81 | 13.67 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {6C7F06C7-9667-4D6C-BBD6-B1CD2B246F78}
8167 | 4591 | {DF1B40DA-2DA0-11E6-B38D-D4BED91EFF1A} | EAST BAY | BERKELEY F | 12kv Bus 1 (FG-1, FG-2, FG-3, FG-4) | CB 1103 | PGE\C7CF | 2017-05-23 11:11:16.6069608 -07:00 | 0120601103 | 012960402 | 7 | 3 | 3 | 2 | 397 | 8.57 | 8.48 | 397 | 8.57 | 8.48 | 487 | 10.52 | 10.41 | 487 | 10.52 | 10.41 | 458 | 9.89 | 9.79 | 458 | 9.89 | 9.79 | 509 | 10.99 | 10.88 | 509 | 10.99 | 10.88 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {1649B777-2F73-45A8-A6B5-0C6DDF975B68}
8168 | 4761 | {BC52961F-2D9F-11E6-B38D-D4BED91EFF1A} | EAST BAY | BERKELEY F | 12kv Bus 2 (DWF-1, DWF-2, DWF-3) | CB 1101 | PGE\C7CF | 2017-05-23 11:58:51.5662622 -07:00 | 0120601101 | 013432206 | 7 | 3 | 3 | 2 | 350 | 7.56 | 7.48 | 350 | 7.56 | 7.48 | 392 | 8.47 | 8.39 | 392 | 8.47 | 8.39 | 361 | 7.8 | 7.72 | 361 | 7.8 | 7.72 | 404 | 8.73 | 8.64 | 404 | 8.73 | 8.64 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {F21E0795-5386-4399-A1DA-160D54D20399}
6635 | 4532 | {72FB6773-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB 1120 | PGE\DMAL | 2017-04-10 12:53:34.1138893 -07:00 | 022801120 | 013432207 | 7 | 3 | 3 | 2 | 462 | 9.98 | 9.88 | 462 | 9.98 | 9.88 | 538 | 11.62 | 11.5 | 538 | 11.62 | 11.5 | 471 | 10.17 | 10.07 | 471 | 10.17 | 10.07 | 549 | 11.86 | 11.74 | 549 | 11.86 | 11.74 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {DC9CB8B9-3856-452B-B0C3-42793EEE7EBE}
6636 | 4532 | {72FB678C-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB 1128 | PGE\DMAL | 2017-04-10 12:56:01.2492363 -07:00 | 0228001128 | 013432208 | 7 | 3 | 3 | 2 | 446 | 9.63 | 9.53 | 446 | 9.63 | 9.53 | 549 | 11.86 | 11.74 | 549 | 11.86 | 11.74 | 459 | 9.91 | 9.81 | 459 | 9.91 | 9.81 | 556 | 12.01 | 11.89 | 556 | 12.01 | 11.89 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {9C5BE312-216B-4EEC-B99F-F3D887C74C4B}
6637 | 4532 | {A8CA3D42-5FCD-11E6-9BE4-80000BC6CD8D} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB 1135 | PGE\DMAL | 2017-04-10 13:09:34.0511060 -07:00 | 022801135 | 152491101 | 7 | 3 | 3 | 2 | 446 | 9.63 | 9.53 | 446 | 9.63 | 9.53 | 549 | 11.86 | 11.74 | 549 | 11.86 | 11.74 | 459 | 9.91 | 9.81 | 459 | 9.91 | 9.81 | 556 | 12.01 | 11.89 | 556 | 12.01 | 11.89 | Parallel 4/0XLP-PVC ELC=2 (SN=486, SE=598, WN=500, WE=606) |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {3EC68588-58EF-40D5-B8A7-9D3E054BBB63}
6638 | 4532 | {7914A379-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB 1136 | PGE\DMAL | 2017-04-10 13:12:13.0914657 -07:00 | 022801136 | 152491102 | 7 | 3 | 3 | 2 | 446 | 9.63 | 9.53 | 446 | 9.63 | 9.53 | 549 | 11.86 | 11.74 | 549 | 11.86 | 11.74 | 459 | 9.91 | 9.81 | 459 | 9.91 | 9.81 | 556 | 12.01 | 11.89 | 556 | 12.01 | 11.89 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {8BAE2B30-2BF5-45DE-8E07-3902E59DAB56}
6639 | 4533 | {3787DCF6-5E3E-11E6-9BE4-80000BC6CD8D} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1107 | PGE\DMAL | 2017-04-10 13:17:24.7905990 -07:00 | 022801107 | 022280401 | 7 | 3 | 3 | 2 | 445 | 9.61 | 9.51 | 445 | 9.61 | 9.51 | 494 | 10.67 | 10.56 | 494 | 10.67 | 10.56 | 458 | 9.89 | 9.79 | 458 | 9.89 | 9.79 | 509 | 10.99 | 10.88 | 509 | 10.99 | 10.88 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {0C927E56-C1F4-46A0-87C0-251958D6F7A7}
6641 | 4533 | {72FB677E-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1127 | PGE\DMAL | 2017-04-10 13:37:37.3855754 -07:00 | 0228001127 | 022280403 | 7 | 3 | 3 | 2 | 412 | 8.9 | 8.81 | 412 | 8.9 | 8.81 | 507 | 10.95 | 10.84 | 507 | 10.95 | 10.84 | 424 | 9.16 | 9.07 | 424 | 9.16 | 9.07 | 513 | 11.08 | 10.97 | 513 | 11.08 | 10.97 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {681A123E-AC34-4D63-BF23-354E10647C0D}
6642 | 4533 | {7F8CAAD1-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1137 | PGE\DMAL | 2017-05-16 11:45:55.6759482 -07:00 | 022801137 | 022280405 | 7 | 3 | 3 | 2 | 481 | 10.39 | 10.29 | 481 | 10.39 | 10.29 | 592 | 12.79 | 12.66 | 592 | 12.79 | 12.66 | 495 | 10.69 | 10.58 | 495 | 10.69 | 10.58 | 599 | 12.94 | 12.81 | 599 | 12.94 | 12.81 | Standby to CPUC Building ATS (ATS 20576/20570 - 45amp). |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {7BED3EC9-472C-4D30-83ED-E8FDDB762B4B}
6643 | 4533 | {7F8CAAD6-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1138 | PGE\DMAL | 2017-04-10 14:11:29.1952134 -07:00 | 022801138 | 022280402 | 7 | 3 | 3 | 2 | 517 | 11.17 | 11.06 | 517 | 11.17 | 11.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 527 | 11.38 | 11.27 | 527 | 11.38 | 11.27 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | Normal Source to MUNI Richmond Sub ATS (ATS 152H/252H - 80amp) |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {C97AFEF3-E7EB-481D-9478-A403DC340A03}
6644 | 4533 | {7914A381-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1140 | PGE\DMAL | 2017-04-10 14:11:51.3669343 -07:00 | 022801140 | 022280406 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {FE399EBD-54E8-4D0B-9E41-96E3C8988517}
6645 | 4533 | {7F8CAAF9-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1141 | PGE\DMAL | 2017-05-16 11:47:45.3644699 -07:00 | 022801141 | 022280408 | 7 | 3 | 3 | 2 | 555 | 11.99 | 11.87 | 555 | 11.99 | 11.87 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 566 | 12.22 | 12.1 | 566 | 12.22 | 12.1 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | Feeder shares ductline with Y1108AB and Y1109AB. Either Y1108AB or Y1109AB carries the Federal Building, thus ELC = 3. |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {AE533969-71FC-4F13-BC31-039DA0EF458E}
6646 | 1076 | {7976ACD2-9010-11E6-841B-D4BED91EFF1A} | EAST BAY | EL CERRITO G | Bank 4 | CB BANK 4/2D | PGE\MUSF | 2017-03-29 11:40:08.0542747 -07:00 |  | 083421106 | 7 | 4 | 4 | 2 | 2777 | 59.98 | 59.38 | 2777 | 59.98 | 59.38 | 3000 | 64.8 | 64.15 | 2850 | 61.56 | 60.94 | 3000 | 64.8 | 64.15 | 2850 | 61.56 | 60.94 | 3000 | 64.8 | 64.15 | 2850 | 61.56 | 60.94 |  |  | FALSE | FALSE | 2777 | 3611 | 3333 | 4166 | {ECD21EC8-BC49-4433-8388-224CD1F0952C}
6647 | 4565 | {9A705D34-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | NORD | Bank 1 | CB 1104 | PGE\DRN3 | 2017-03-29 12:59:22.3270169 -07:00 | 1030701104 | 083421108 | 7 | 4 | 4 | 1 | 567 | 12.25 | 12.13 | 567 | 12.25 | 12.13 | 567 | 12.25 | 12.13 | 567 | 12.25 | 12.13 | 567 | 12.25 | 12.13 | 567 | 12.25 | 12.13 | 567 | 12.25 | 12.13 | 567 | 12.25 | 12.13 |  |  | FALSE | FALSE | 740 | 963 | 888 | 1111 | {26BF7E67-57E2-4759-AE81-641C26E40AF3}
6648 | 4566 | {9A705D55-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | NORD | Bank 2 | CB 1105 | PGE\DRN3 | 2017-03-29 13:07:30.9006246 -07:00 | 1030701105 | 083421109 | 7 | 3 | 3 | 1 | 578 | 12.48 | 12.36 | 578 | 12.48 | 12.36 | 583 | 12.59 | 12.46 | 583 | 12.59 | 12.46 | 583 | 12.59 | 12.46 | 583 | 12.59 | 12.46 | 583 | 12.59 | 12.46 | 583 | 12.59 | 12.46 |  |  | FALSE | FALSE | 740 | 963 | 888 | 1111 | {DD43A693-B385-428A-B6C9-0F873C4ABCC4}
6649 | 4566 | {9A705D65-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | NORD | Bank 2 | CB 1106 | PGE\DRN3 | 2017-03-29 13:11:49.0037964 -07:00 | 1030701106 | 083421110 | 7 | 3 | 3 | 1 | 578 | 12.48 | 12.36 | 578 | 12.48 | 12.36 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 740 | 963 | 888 | 1111 | {5CC42699-2273-47C7-8027-8F9E8FD15254}
6650 | 4580 | {A6861D81-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | SYCAMORE CREEK | Bank 1 | CB 1101 | PGE\DRN3 | 2017-03-29 14:04:23.9725880 -07:00 | 1029701101 | 083421111 | 7 | 3 | 3 | 1 | 503 | 10.86 | 10.75 | 503 | 10.86 | 10.75 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {32DAEF1A-9E58-4C60-93B1-4B441EBBFD13}
6651 | 4580 | {A6861D8A-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | SYCAMORE CREEK | Bank 1 | CB 1102 | PGE\DRN3 | 2017-03-29 14:03:26.8503711 -07:00 | 1029701102 | 083421112 | 7 | 3 | 3 | 1 | 503 | 10.86 | 10.75 | 503 | 10.86 | 10.75 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {3E345190-AB65-44AE-8469-4C52D09B5BC8}
6652 | 4580 | {A6861DA8-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | SYCAMORE CREEK | Bank 1 | CB 1103 | PGE\DRN3 | 2017-03-29 14:10:31.4676917 -07:00 | 1029701103 | 083421113 | 7 | 3 | 3 | 1 | 503 | 10.86 | 10.75 | 503 | 10.86 | 10.75 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {3A3CCD24-3E91-4E20-ACD7-1924A66EA5AE}
6653 | 4580 | {A6861DB1-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | SYCAMORE CREEK | Bank 1 | CB 1104 | PGE\DRN3 | 2017-03-29 14:21:48.0562444 -07:00 | 1029701104 | 013532225 | 7 | 3 | 3 | 1 | 575 | 12.42 | 12.3 | 575 | 12.42 | 12.3 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {E1E07F10-FABF-4706-B838-76E93D5E1517}
6654 | 2688 | {A6861DC4-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | SYCAMORE CREEK | Bank 2 | CB 1105 | PGE\DRN3 | 2017-03-29 14:28:52.9700201 -07:00 | 1029701105 | 013532227 | 7 | 3 | 3 | 1 | 575 | 12.42 | 12.3 | 575 | 12.42 | 12.3 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1041 | 1354 | 1250 | 1562 | {496DE9C6-CC5A-481F-9ECC-D6F9AF0D9489}
6656 | 2688 | {A6861DD4-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | SYCAMORE CREEK | Bank 2 | CB 1107 | PGE\DRN3 | 2017-03-29 14:38:49.8277538 -07:00 | 1029701107 | 013532107 | 7 | 3 | 3 | 1 | 512 | 11.06 | 10.95 | 512 | 11.06 | 10.95 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 556 | 12.01 | 11.89 | 556 | 12.01 | 11.89 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  | check share point | FALSE | FALSE | 1041 | 1354 | 1250 | 1562 | {CB32210C-99BE-4549-AED7-38CC4C111BE8}
6657 | 4581 | {A6861DEE-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | SYCAMORE CREEK | Bank 3 | CB 1109 | PGE\DRN3 | 2017-03-29 14:43:55.7538141 -07:00 | 1029701109 | 013532109 | 7 | 3 | 3 | 1 | 575 | 12.42 | 12.3 | 575 | 12.42 | 12.3 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {103755C1-CFC5-4929-B3E6-6BD1719E3EA0}
6658 | 4581 | {ACCC4DFE-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | SYCAMORE CREEK | Bank 3 | CB 1110 | PGE\DRN3 | 2017-03-29 15:24:57.1424949 -07:00 | 1029701110 | 013532226 | 7 | 3 | 3 | 1 | 512 | 11.06 | 10.95 | 512 | 11.06 | 10.95 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 556 | 12.01 | 11.89 | 556 | 12.01 | 11.89 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {3B19E3F6-C66B-4694-9381-0B80F3B7C764}
6659 | 4581 | {ACCC4E0E-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | SYCAMORE CREEK | Bank 3 | CB 1111 | PGE\DRN3 | 2017-03-29 15:30:24.2104847 -07:00 | 1029701111 | 013532108 | 7 | 3 | 3 | 1 | 503 | 10.86 | 10.75 | 503 | 10.86 | 10.75 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 556 | 12.01 | 11.89 | 556 | 12.01 | 11.89 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {2E0390AA-D4A5-4F76-AE62-D30BD47323F5}
6660 | 4567 | {86A61B0D-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CHICO C | Bank 1 | CB 401 | PGE\DRN3 | 2017-03-29 15:46:10.2299146 -07:00 | 102650401 | 014302102 | 3 | 4 | 4 | 1 | 345 | 2.49 | 2.47 | 345 | 2.49 | 2.47 | 386 | 2.78 | 2.75 | 386 | 2.78 | 2.75 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | TRUE | FALSE | 693 | 902 | 832 | 1040 | {BED0777E-85D3-4052-948E-AAC9394D0C45}
6662 | 4579 | {9C31F16F-BB23-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | HUNTERS POINT (SF P) | 12kv Main Bus | CB D-E/12 | PGE\DMAL | 2017-03-30 12:27:13.5842096 -07:00 |  | 014302103 | 7 | 3 | 3 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {C3228FBE-62E9-468B-ACD4-8A1DED0813A9}
6663 | 4586 | {6C94A8BA-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | HUNTERS POINT (SF P) | Bank 6 | CB 1101 | PGE\DMAL | 2017-03-31 14:02:35.2283603 -07:00 | 0223301101 | 083611112 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2314 | 3000 | 2777 | 3000 | {EE30E155-425C-4523-B645-E4F12722C127}
6664 | 4586 | {6C94A8C9-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | HUNTERS POINT (SF P) | Bank 6 | CB 1102 | PGE\DMAL | 2017-03-31 14:03:39.2659328 -07:00 | 0223301102 | 014302104 | 7 | 3 | 3 | 2 | 481 | 10.39 | 10.29 | 481 | 10.39 | 10.29 | 592 | 12.79 | 12.66 | 592 | 12.79 | 12.66 | 495 | 10.69 | 10.58 | 495 | 10.69 | 10.58 | 599 | 12.94 | 12.81 | 599 | 12.94 | 12.81 |  |  | FALSE | FALSE | 2314 | 3000 | 2777 | 3000 | {2AA0BB4B-B110-4E6F-A377-4452A14B175C}
6667 | 4585 | {665855DF-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | HUNTERS POINT (SF P) | Bank 1 | CB 1103 | PGE\DMAL | 2017-03-31 14:02:15.7970228 -07:00 | 0223301103 | 014302105 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2314 | 3000 | 2777 | 3000 | {84259BFB-2009-4C77-BD72-4AACDED7B735}
6668 | 4585 | {665855EE-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | HUNTERS POINT (SF P) | Bank 1 | CB 1104 | PGE\DMAL | 2017-03-31 14:16:53.9921279 -07:00 | 0223301104 | 083611113 | 7 | 3 | 3 | 2 | 581 | 12.55 | 12.42 | 581 | 12.55 | 12.42 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 598 | 12.92 | 12.79 | 598 | 12.92 | 12.79 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2314 | 3000 | 2777 | 3000 | {A27E1E52-AFD1-4CF6-B735-F8B2A7E34431}
6669 | 4585 | {665855F4-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | HUNTERS POINT (SF P) | Bank 1 | CB 1105 | PGE\DMAL | 2017-03-31 14:35:05.5909711 -07:00 | 0223301105 | 014302106 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 750 | 16.2 | 16.04 | 750 | 16.2 | 16.04 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 750 | 16.2 | 16.04 | 750 | 16.2 | 16.04 |  |  | FALSE | FALSE | 2314 | 3000 | 2777 | 3000 | {A85742CF-D79C-49D4-A93D-44C1DAC65A41}
6670 | 4585 | {6C94A8B4-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | HUNTERS POINT (SF P) | Bank 1 | CB 1106 | PGE\DMAL | 2017-03-31 14:40:44.2675185 -07:00 | 0223301106 | 014302107 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2314 | 3000 | 2777 | 3000 | {478FE922-C8F0-4330-B717-0DB248E11BFC}
6671 | 4586 | {665855B2-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | HUNTERS POINT (SF P) | Bank 6 | CB 1107 | PGE\DMAL | 2017-03-31 14:44:25.1109651 -07:00 | 0223301107 | 014302108 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2314 | 3000 | 2777 | 3000 | {D1D7AEE7-B4CB-4C9B-8974-4AB72A1EA88D}
6672 | 4586 | {665855CA-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | HUNTERS POINT (SF P) | Bank 6 | CB 1108 | PGE\DMAL | 2017-03-31 14:47:55.2040136 -07:00 | 0223301108 | 083611114 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2314 | 3000 | 2777 | 3000 | {0F645AC7-5C1D-4D60-8A06-3192B4DC7B67}
6673 | 4586 | {665855D6-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | HUNTERS POINT (SF P) | Bank 6 | CB 1109 | PGE\DMAL | 2017-03-31 15:17:23.7927286 -07:00 | 0223301109 | 083611115 | 7 | 3 | 3 | 2 | 582 | 12.57 | 12.44 | 582 | 12.57 | 12.44 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | Yosemite Sub ATS |  | FALSE | FALSE | 2314 | 3000 | 2777 | 3000 | {A9D8971B-D735-4690-B29D-5A79EA6345D4}
6674 | 4533 | {08A4EE2F-3C99-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1109 | PGE\DMAL | 2017-04-10 13:18:45.9880906 -07:00 | 0228001109 | 014302109 | 7 | 3 | 3 | 2 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | Y-1109AB is limited by station length UG splice/connectors SN=SE=WN=WE=600amp: Serves the Federal Building. Y-1109C is limited 750T - 15kV Shielded PL&N - 6ELC (SN=420_SE=470_WN=433_WE=485). Serves customers. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {3F13111B-6B48-48FE-9BEC-A552DBA2C288}
6679 | 4532 | {8C7093AA-9177-11E6-841B-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB 1114 | PGE\DMAL | 2017-04-04 12:22:19.5462236 -07:00 | 022801114 | 082921108 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {C82046BB-13D5-4020-BD93-78D52768ABD1}
6680 | 4532 | {6B13BBA7-9178-11E6-841B-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB 1115 | PGE\DMAL | 2017-04-04 12:24:26.6006383 -07:00 | 022801115 | 014302110 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {9A39C046-1CDA-4835-8ABB-006542F710B6}
6681 | 4532 | {8F0F568D-9178-11E6-841B-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB 1116 | PGE\DMAL | 2017-04-04 12:25:36.9385115 -07:00 | 022801116 | 014652104 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {E1E3B008-84A9-4BAD-AF87-74C87345A6AA}
6682 | 4532 | {A8C77FCC-9178-11E6-841B-D4BED91EFF1A} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 1 (Banks 1, 3, 5) | CB 1117 | PGE\DMAL | 2017-04-04 12:26:36.2295315 -07:00 | 022801117 | 014652105 | 7 | 3 | 3 | 2 | 420 | 9.07 | 8.98 | 420 | 9.07 | 8.98 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 485 | 10.48 | 10.38 | 485 | 10.48 | 10.38 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {CE254E94-EE49-4316-AF80-C931167848D9}
6683 | 4591 | {6A5FBB04-2DA1-11E6-B38D-D4BED91EFF1A} | EAST BAY | BERKELEY F | 12kv Bus 1 (FG-1, FG-2, FG-3, FG-4) | CB 1105 | PGE\C7CF | 2017-05-23 11:46:07.1007608 -07:00 | 0120601105 | 014652106 | 7 | 3 | 3 | 2 | 400 | 8.64 | 8.55 | 400 | 8.64 | 8.55 | 448 | 9.68 | 9.58 | 448 | 9.68 | 9.58 | 412 | 8.9 | 8.81 | 412 | 8.9 | 8.81 | 461 | 9.96 | 9.86 | 461 | 9.96 | 9.86 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {2AC5FB81-9F4F-427E-8123-C4B9ED1190F4}
6685 | 4533 | {94077FF7-5FCE-11E6-9BE4-80000BC6CD8D} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1110 | PGE\DMAL | 2017-04-10 13:21:27.5249143 -07:00 | 022801110 | 014652107 | 7 | 3 | 3 | 2 | 390 | 8.42 | 8.34 | 390 | 8.42 | 8.34 | 433 | 9.35 | 9.26 | 433 | 9.35 | 9.26 | 402 | 8.68 | 8.59 | 402 | 8.68 | 8.59 | 446 | 9.63 | 9.53 | 446 | 9.63 | 9.53 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {E90A8AF0-F9D9-4E98-8E3E-B65679FEAD40}
6687 | 4533 | {7914A3BE-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1111 | PGE\DMAL | 2017-04-10 13:26:59.6326408 -07:00 | 0228001111 | 014652108 | 7 | 3 | 3 | 2 | 347 | 7.49 | 7.42 | 347 | 7.49 | 7.42 | 385 | 8.32 | 8.24 | 385 | 8.32 | 8.24 | 357 | 7.71 | 7.63 | 357 | 7.71 | 7.63 | 397 | 8.57 | 8.48 | 397 | 8.57 | 8.48 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {205914DF-568D-4931-BA4E-4BCD2DA15F8F}
6689 | 4533 | {7914A3C3-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | LARKIN (SF Y) | 12kv Bus 2 (Banks 2, 4, 6) | CB 1119 | PGE\DMAL | 2017-04-10 13:32:07.6650926 -07:00 | 0228001119 | 014652109 | 7 | 3 | 3 | 2 | 407 | 8.79 | 8.7 | 407 | 8.79 | 8.7 | 456 | 9.85 | 9.75 | 456 | 9.85 | 9.75 | 419 | 9.05 | 8.96 | 419 | 9.05 | 8.96 | 470 | 10.15 | 10.05 | 470 | 10.15 | 10.05 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {19FC6241-931B-41AB-A944-2F492B778286}
6690 | 4593 | {DAAD83FF-B807-11E6-93A9-D4BED91EFF1A} | SF J | 12KV BUS 2 (Non-SCADA) | Bank 2 | CB 402 | PGE\DMAL | 2017-04-11 09:57:02.0249178 -07:00 |  | 014652110 | 3 | 3 | 3 | 2 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2000 | {5F1EA7FA-BD7F-4D11-A4B2-D1968990ADBA}
6691 | 4593 | {E2BA9A64-B807-11E6-93A9-D4BED91EFF1A} | SF J | 12KV BUS 2 (Non-SCADA) | Bank 2 | CB 404 | PGE\DMAL | 2017-04-11 10:01:41.4713004 -07:00 |  | 102911102 | 3 | 3 | 3 | 2 | 365 | 2.63 | 2.6 | 365 | 2.63 | 2.6 | 394 | 2.84 | 2.81 | 394 | 2.84 | 2.81 | 376 | 2.71 | 2.68 | 376 | 2.71 | 2.68 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2000 | {73999E0A-65B0-4CCF-957C-BFB34ECEF6D7}
6692 | 4593 | {EA1199A5-B807-11E6-93A9-D4BED91EFF1A} | SF J | 12KV BUS 2 (Non-SCADA) | Bank 2 | CB 406 | PGE\DMAL | 2017-04-11 10:05:39.7955558 -07:00 |  | 102911103 | 3 | 3 | 3 | 2 | 345 | 2.49 | 2.47 | 345 | 2.49 | 2.47 | 373 | 2.69 | 2.66 | 373 | 2.69 | 2.66 | 355 | 2.56 | 2.53 | 355 | 2.56 | 2.53 | 384 | 2.77 | 2.74 | 384 | 2.77 | 2.74 |  |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2000 | {BBE4D929-89DE-4C5D-9801-1F31390252AD}
6693 | 4593 | {FE9697DE-B807-11E6-93A9-D4BED91EFF1A} | SF J | 12KV BUS 2 (Non-SCADA) | Bank 2 | CB STREET LIGHT 109 | PGE\DMAL | 2017-05-16 10:45:17.6395103 -07:00 |  | 102911105 | 3 | 3 | 3 | 2 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 |  |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2000 | {F751E46D-2AC7-431B-B5BD-3E4DD0222EA2}
6695 | 4594 | {422D6E7B-BD6D-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MARINA (SF F) | 12kv Bus 2 | CB F MUNI TIE | PGE\DMAL | 2017-04-19 17:46:23.5096073 -07:00 |  | 102911106 | 7 | 3 | 3 | 2 | 300 | 6.48 | 6.42 | 300 | 6.48 | 6.42 | 300 | 6.48 | 6.42 | 300 | 6.48 | 6.42 | 300 | 6.48 | 6.42 | 300 | 6.48 | 6.42 | 300 | 6.48 | 6.42 | 300 | 6.48 | 6.42 | MUNI primary switchgear is inside of Station F. Space is leased by MUNI. |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {00000000-0000-0000-0000-000000000000}
6696 | 4594 | {7B165029-BD6D-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MARINA (SF F) | 12kv Bus 2 | CB QF-1 | PGE\DMAL | 2017-04-19 17:43:40.9076804 -07:00 |  | 014150401 | 7 | 3 | 3 | 2 | 228 | 4.92 | 4.87 | 228 | 4.92 | 4.87 | 253 | 5.46 | 5.41 | 253 | 5.46 | 5.41 | 235 | 5.08 | 5.03 | 235 | 5.08 | 5.03 | 261 | 5.64 | 5.58 | 261 | 5.64 | 5.58 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {00000000-0000-0000-0000-000000000000}
6697 | 4588 | {DE7AE92C-BBFB-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section D | CB KX-1 | PGE\DMAL | 2017-04-12 12:03:56.0599171 -07:00 |  | 102911107 | 7 | 3 | 3 | 2 | 455 | 9.83 | 9.73 | 455 | 9.83 | 9.73 | 529 | 11.43 | 11.32 | 529 | 11.43 | 11.32 | 464 | 10.02 | 9.92 | 464 | 10.02 | 9.92 | 540 | 11.66 | 11.54 | 540 | 11.66 | 11.54 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {FB59726E-3C80-470E-A062-E65A9C252CBF}
6698 | 4588 | {FD9070BD-BBFB-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section D | CB KX-2 | PGE\DMAL | 2017-04-12 12:04:08.9612825 -07:00 |  | 102911109 | 7 | 3 | 3 | 2 | 455 | 9.83 | 9.73 | 455 | 9.83 | 9.73 | 529 | 11.43 | 11.32 | 529 | 11.43 | 11.32 | 464 | 10.02 | 9.92 | 464 | 10.02 | 9.92 | 540 | 11.66 | 11.54 | 540 | 11.66 | 11.54 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {ED695BBD-DC7E-4A6A-96FD-BDEFA7170AC6}
6699 | 4588 | {0F8749B1-BBFC-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section D | CB KX-3 | PGE\DMAL | 2017-04-12 12:04:21.1450387 -07:00 |  | 102911110 | 7 | 3 | 3 | 2 | 455 | 9.83 | 9.73 | 455 | 9.83 | 9.73 | 529 | 11.43 | 11.32 | 529 | 11.43 | 11.32 | 464 | 10.02 | 9.92 | 464 | 10.02 | 9.92 | 540 | 11.66 | 11.54 | 540 | 11.66 | 11.54 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {F1ADB439-20AA-498F-A337-26614A47669F}
6700 | 4588 | {1DC1A8C5-BBFC-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section D | CB KX-4 | PGE\DMAL | 2017-04-12 12:04:40.7856905 -07:00 |  | 153711101 | 7 | 3 | 3 | 2 | 455 | 9.83 | 9.73 | 455 | 9.83 | 9.73 | 529 | 11.43 | 11.32 | 529 | 11.43 | 11.32 | 464 | 10.02 | 9.92 | 464 | 10.02 | 9.92 | 540 | 11.66 | 11.54 | 540 | 11.66 | 11.54 | Only NX-4 has a small section of 500EPRcu cable towards Station K. Capability difference is very small so assume all 4 tie cables are limited to 750EPRcu. In the event of N-1 these 2 mainlines are technically equivalent. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {BE4FBFC7-D1F0-4F60-AA26-0ECB612B2184}
6701 | 4588 | {9500AB1C-BBFB-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section D | CB NX-1 | PGE\DMAL | 2017-04-12 12:04:54.3734647 -07:00 |  | 083421102 | 7 | 3 | 3 | 2 | 430 | 9.29 | 9.2 | 430 | 9.29 | 9.2 | 499 | 10.78 | 10.67 | 499 | 10.78 | 10.67 | 439 | 9.48 | 9.39 | 439 | 9.48 | 9.39 | 509 | 10.99 | 10.88 | 509 | 10.99 | 10.88 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {7B16AE1E-E316-4A6E-B994-809C46FAA176}
6702 | 4588 | {B36ECF43-BBFB-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section D | CB NX-2 | PGE\DMAL | 2017-04-12 12:05:09.4744583 -07:00 |  | 083421103 | 7 | 3 | 3 | 2 | 430 | 9.29 | 9.2 | 430 | 9.29 | 9.2 | 499 | 10.78 | 10.67 | 499 | 10.78 | 10.67 | 439 | 9.48 | 9.39 | 439 | 9.48 | 9.39 | 509 | 10.99 | 10.88 | 509 | 10.99 | 10.88 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {D193FEE0-4DFD-4E94-8B97-24F4D3D98822}
6704 | 4588 | {C1591A79-BBFB-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section D | CB NX-3 | PGE\DMAL | 2017-04-12 12:05:21.3150101 -07:00 |  | 083421104 | 7 | 3 | 3 | 2 | 430 | 9.29 | 9.2 | 430 | 9.29 | 9.2 | 499 | 10.78 | 10.67 | 499 | 10.78 | 10.67 | 439 | 9.48 | 9.39 | 439 | 9.48 | 9.39 | 509 | 10.99 | 10.88 | 509 | 10.99 | 10.88 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {8B0A5409-B8C0-420B-8188-D6A7F3E1E421}
6705 | 4588 | {CC6C4282-BBFB-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section D | CB NX-4 | PGE\DMAL | 2017-04-12 12:05:37.2428143 -07:00 |  | 083421105 | 7 | 3 | 3 | 2 | 430 | 9.29 | 9.2 | 430 | 9.29 | 9.2 | 499 | 10.78 | 10.67 | 499 | 10.78 | 10.67 | 439 | 9.48 | 9.39 | 439 | 9.48 | 9.39 | 509 | 10.99 | 10.88 | 509 | 10.99 | 10.88 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {D15E4F81-FF8D-40B8-98B6-2D368EABBAB5}
6707 | 4588 | {9F964F7A-3C97-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section D | CB 1105 | PGE\DMAL | 2017-04-12 11:55:05.4659147 -07:00 | 0220101105 | 153702109 | 7 | 3 | 3 | 2 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {CC5DDDEF-23E3-4346-9E02-9D87648810A1}
6708 | 4588 | {989AB877-3C97-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section D | CB 1106 | PGE\DMAL | 2017-04-12 11:55:21.4717199 -07:00 | 0220101106 | 153711102 | 7 | 3 | 3 | 2 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {F91D7001-88B7-4490-8D09-E1A64B38F29D}
6709 | 4588 | {989AB874-3C97-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section D | CB 1112 | PGE\DMAL | 2017-04-12 11:55:40.7379669 -07:00 | 0220101112 | 153761101 | 7 | 3 | 3 | 2 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {3604B2F8-FA87-43C2-B978-548EE0A8BA54}
6710 | 4588 | {9171E7C3-3C97-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section D | CB 1114 | PGE\DMAL | 2017-04-12 11:55:53.9825367 -07:00 | 0220101114 | 153761102 | 7 | 3 | 3 | 2 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {0EA7509B-79A7-4F36-A3D4-B963790A7F0B}
6711 | 4588 | {9171E7C0-3C97-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section D | CB 1115 | PGE\DMAL | 2017-04-12 11:56:14.0443939 -07:00 | 0220101115 | 153761105 | 7 | 3 | 3 | 2 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {336EC2AA-8A27-4B19-81FC-26DE9A560BF1}
6712 | 4588 | {8B3E4245-3C97-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section D | CB 1121 | PGE\DMAL | 2017-04-12 11:56:29.3949907 -07:00 | 0220101121 | 152811101 | 7 | 3 | 3 | 2 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {C5B83FE4-C228-446D-891A-02D5436459DB}
6713 | 4588 | {79093922-BC00-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section D | CB CAP BK-1 | PGE\DMAL | 2017-04-11 14:55:31.9315747 -07:00 |  | 152811102 | 7 | 3 | 3 | 2 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 | 800 | 17.28 | 17.11 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {503635CA-8233-4CE3-9C8E-F5362936523D}
6715 | 4588 | {43824B7F-BC01-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section D | CB SVC BK-2 | PGE\DMAL | 2017-04-11 14:59:24.6020195 -07:00 |  | 152811104 | 7 | 3 | 3 | 2 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {FC99731B-EF55-4DDA-B0CD-02BDB2FABB98}
6716 | 4590 | {54A8C88D-BC00-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section E | CB CAP BK-2 | PGE\DMAL | 2017-04-11 15:00:17.3710273 -07:00 |  | 152811105 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {B9B88140-AC4E-4030-927B-C1940829F15C}
6717 | 4595 | {A90A5425-BC00-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section F | CB CAP BK-3 | PGE\DMAL | 2017-04-11 15:01:23.8549842 -07:00 |  | 252561101 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {BA0E18F1-5C21-4073-A286-B210696705A3}
6718 | 4595 | {6699E911-BC01-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section F | CB SVC BK-1 | PGE\DMAL | 2017-04-11 15:03:35.2001964 -07:00 |  | 083631101 | 7 | 3 | 3 | 2 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {E4839141-0ABC-4EEA-9ADD-2C6B5341E956}
6719 | 4595 | {677952D1-3C97-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section F | CB 1117 | PGE\DMAL | 2017-04-12 11:56:53.7781033 -07:00 | 0220101117 | 083631102 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {B3316390-21E1-4914-B4D8-46EF06DDA33E}
6721 | 4595 | {5E6168F8-3C97-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section F | CB 1123 | PGE\DMAL | 2017-04-12 11:57:07.6466811 -07:00 | 0220101123 | 083631103 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {3E82C41B-0E7C-42AE-B9D5-8960B140F344}
6722 | 4595 | {DA2E353A-5F59-11E6-9736-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section F | CB 1153 | PGE\DMAL | 2017-04-12 11:57:23.9956907 -07:00 |  | 083631104 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {BD35BC0F-B6F9-483D-B11A-63128337697E}
6723 | 4595 | {F57E192C-5F59-11E6-9736-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section F | CB 1154 | PGE\DMAL | 2017-04-12 11:57:39.8142935 -07:00 |  | 082031102 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {A4E54B49-3174-4CFD-8F46-CBD75ECD04E3}
6724 | 4595 | {01A14867-5F5A-11E6-9736-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section F | CB 1160 | PGE\DMAL | 2017-04-12 11:57:53.6048703 -07:00 |  | 082031103 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {A39F0D35-DD54-4897-BC92-B6884B56B1AC}
6725 | 4595 | {0DC2C9A5-5F5A-11E6-9736-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section F | CB 1162 | PGE\DMAL | 2017-04-12 11:58:16.4123627 -07:00 |  | 082031104 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {CC714314-122A-4495-ADA3-4A35F2CB94AE}
6726 | 4595 | {FA0A984A-BBFD-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section F | CB GX-1 | PGE\DMAL | 2017-04-12 12:27:22.4023469 -07:00 |  | 082031105 | 7 | 3 | 3 | 2 | 455 | 9.83 | 9.73 | 455 | 9.83 | 9.73 | 529 | 11.43 | 11.32 | 529 | 11.43 | 11.32 | 464 | 10.02 | 9.92 | 464 | 10.02 | 9.92 | 540 | 11.66 | 11.54 | 540 | 11.66 | 11.54 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {0F33C061-33EA-497E-996F-9F786E1AE65C}
6727 | 4595 | {113B33CC-BBFE-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section F | CB GX-2 | PGE\DMAL | 2017-04-12 12:27:34.1804979 -07:00 |  | 083631105 | 7 | 3 | 3 | 2 | 455 | 9.83 | 9.73 | 455 | 9.83 | 9.73 | 529 | 11.43 | 11.32 | 529 | 11.43 | 11.32 | 464 | 10.02 | 9.92 | 464 | 10.02 | 9.92 | 540 | 11.66 | 11.54 | 540 | 11.66 | 11.54 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {DAFAE767-DAD2-4E50-B6CF-3DF778019361}
6728 | 4595 | {20124010-BBFE-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section F | CB GX-3 | PGE\DMAL | 2017-04-12 12:27:46.8322601 -07:00 |  | 083631106 | 7 | 3 | 3 | 2 | 462 | 9.98 | 9.88 | 462 | 9.98 | 9.88 | 538 | 11.62 | 11.5 | 538 | 11.62 | 11.5 | 471 | 10.17 | 10.07 | 471 | 10.17 | 10.07 | 549 | 11.86 | 11.74 | 549 | 11.86 | 11.74 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {BF1E92CC-5142-4565-B167-7DBD77F0EB37}
6729 | 4595 | {2BA390C4-BBFE-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section F | CB GX-4 | PGE\DMAL | 2017-04-12 12:27:58.9536155 -07:00 |  | 083631107 | 7 | 3 | 3 | 2 | 455 | 9.83 | 9.73 | 455 | 9.83 | 9.73 | 529 | 11.43 | 11.32 | 529 | 11.43 | 11.32 | 464 | 10.02 | 9.92 | 464 | 10.02 | 9.92 | 540 | 11.66 | 11.54 | 540 | 11.66 | 11.54 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {7B6904F6-0B28-4879-883A-2FA37485B271}
6730 | 4595 | {405FC24E-BBFE-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section F | CB GX-5 | PGE\DMAL | 2017-04-12 12:28:15.0842223 -07:00 |  | 083631108 | 7 | 3 | 3 | 2 | 455 | 9.83 | 9.73 | 455 | 9.83 | 9.73 | 529 | 11.43 | 11.32 | 529 | 11.43 | 11.32 | 464 | 10.02 | 9.92 | 464 | 10.02 | 9.92 | 540 | 11.66 | 11.54 | 540 | 11.66 | 11.54 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {FB45919E-4553-4911-879C-DEBAD19FA889}
6731 | 4596 | {9402A89A-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MISSION (SF X) | 4kv Bus Section D | CB 401 | PGE\DMAL | 2017-04-14 14:16:45.9262018 -07:00 | 022010401 | 252081102 | 3 | 3 | 3 | 2 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 343 | 2.47 | 2.45 | 343 | 2.47 | 2.45 | 370 | 2.67 | 2.64 | 370 | 2.67 | 2.64 |  |  | FALSE | FALSE | 3597 | 3597 | 3597 | 3597 | {EC6F05A2-F009-41B3-826D-A3A575832329}
6732 | 4597 | {9402A891-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MISSION (SF X) | 4kv Bus Section E | CB 402 | PGE\DMAL | 2017-04-14 14:22:38.4907218 -07:00 | 022010402 | 252661105 | 3 | 3 | 3 | 2 | 432 | 3.11 | 3.08 | 432 | 3.11 | 3.08 | 502 | 3.62 | 3.58 | 502 | 3.62 | 3.58 | 441 | 3.18 | 3.15 | 441 | 3.18 | 3.15 | 512 | 3.69 | 3.65 | 512 | 3.69 | 3.65 | Each Branch SW-4096 and SW-4546 is limited by a 250T - 5kV, ELC = 4ELC (SN=257, SE=278, WN=265, WE=286) |  | FALSE | FALSE | 3597 | 3597 | 3597 | 3597 | {74BA72ED-F901-4965-92E1-8D0C86536043}
6733 | 4590 | {85BCDE35-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section E | CB 1101 | PGE\DMAL | 2017-05-17 09:50:54.5432321 -07:00 | 0220101101 | 253411106 | 7 | 3 | 3 | 2 | 320 | 6.91 | 6.84 | 320 | 6.91 | 6.84 | 355 | 7.67 | 7.59 | 355 | 7.67 | 7.59 | 330 | 7.13 | 7.06 | 330 | 7.13 | 7.06 | 366 | 7.91 | 7.83 | 366 | 7.91 | 7.83 | Standby to New Transbay Terminal Center Primary Service2 (Device 285650) on Natoma/1st Street. Normal Source to Building Primary Service1 (Device 573918) on Minna/2nd Street. Internal Customer ATS. |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {A5643E79-F319-46C3-9725-196710CF5885}
6734 | 4590 | {85BCDE3A-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section E | CB 1102 | PGE\DMAL | 2017-04-14 14:36:05.3954666 -07:00 | 0220101102 | 253411107 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | Inspection on 04/2016 found new mainline routed out of Mission are on different ducts than shown in UG duct maps. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {69543376-AA7D-4BA6-B43B-8E1E12243147}
6735 | 4590 | {85BCDE3F-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section E | CB 1104 | PGE\DMAL | 2017-04-14 14:37:27.1873152 -07:00 | 022011104 | 252171101 | 7 | 3 | 3 | 2 | 347 | 7.49 | 7.42 | 347 | 7.49 | 7.42 | 385 | 8.32 | 8.24 | 385 | 8.32 | 8.24 | 357 | 7.71 | 7.63 | 357 | 7.71 | 7.63 | 397 | 8.57 | 8.48 | 397 | 8.57 | 8.48 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {2142C84E-42E4-4D5A-AABB-304F4C9075A6}
6736 | 4590 | {85BCDE42-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section E | CB 1107 | PGE\DMAL | 2017-04-14 14:53:38.8301720 -07:00 | 0220101107 | 083631109 | 7 | 3 | 3 | 2 | 320 | 6.91 | 6.84 | 320 | 6.91 | 6.84 | 355 | 7.67 | 7.59 | 355 | 7.67 | 7.59 | 330 | 7.13 | 7.06 | 330 | 7.13 | 7.06 | 366 | 7.91 | 7.83 | 366 | 7.91 | 7.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {B964A0AF-5C54-476D-8DF8-F7C4F1BC6975}
6737 | 4590 | {8D89850A-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section E | CB 1108 | PGE\DMAL | 2017-04-14 15:15:16.3924072 -07:00 | 022011108 | 083631110 | 7 | 3 | 3 | 2 | 421 | 9.09 | 9 | 421 | 9.09 | 9 | 518 | 11.19 | 11.08 | 518 | 11.19 | 11.08 | 434 | 9.37 | 9.28 | 434 | 9.37 | 9.28 | 551 | 11.9 | 11.78 | 551 | 11.9 | 11.78 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {3E505B29-1677-4E8A-8461-BCFA5A45957A}
6740 | 4590 | {8D898528-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section E | CB 1109 | PGE\DMAL | 2017-04-14 15:05:42.2582466 -07:00 | 0220101109 | 083631111 | 7 | 3 | 3 | 2 | 517 | 11.17 | 11.06 | 517 | 11.17 | 11.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 527 | 11.38 | 11.27 | 527 | 11.38 | 11.27 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | Branch SW-47088 - X1109A and Branch SW-38416 - X1109B are each limited by 500T, 6ELC (SN=320, SE=355, WN=330, WE=366). X1109B serves MUNI Civic Center Station. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {88A4E1E8-4C7A-4B14-8846-D762D8641FDA}
6741 | 4590 | {8D89852B-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section E | CB 1110 | PGE\DMAL | 2017-04-14 15:14:50.0748698 -07:00 | 022011110 | 083631112 | 7 | 3 | 3 | 2 | 421 | 9.09 | 9 | 421 | 9.09 | 9 | 518 | 11.19 | 11.08 | 518 | 11.19 | 11.08 | 434 | 9.37 | 9.28 | 434 | 9.37 | 9.28 | 551 | 11.9 | 11.78 | 551 | 11.9 | 11.78 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {5B1E48E0-0781-44E3-B34E-A53A944EA3F2}
6742 | 4590 | {8D898537-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section E | CB 1111 | PGE\DMAL | 2017-04-14 15:19:07.1817660 -07:00 | 0220101111 | 252171102 | 7 | 3 | 3 | 2 | 517 | 11.17 | 11.06 | 517 | 11.17 | 11.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 527 | 11.38 | 11.27 | 527 | 11.38 | 11.27 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {3BBCF9B8-15F0-492A-BAF1-B7491C31BE46}
6743 | 4590 | {8D89853C-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section E | CB 1113 | PGE\DMAL | 2017-04-14 15:22:22.9330756 -07:00 | 0220101113 | 252171117 | 7 | 3 | 3 | 2 | 320 | 6.91 | 6.84 | 320 | 6.91 | 6.84 | 355 | 7.67 | 7.59 | 355 | 7.67 | 7.59 | 330 | 7.13 | 7.06 | 330 | 7.13 | 7.06 | 366 | 7.91 | 7.83 | 366 | 7.91 | 7.83 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {76ABD245-7167-457B-A2FC-8CBE367F6E63}
6744 | 4590 | {8D898545-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section E | CB 1116 | PGE\DMAL | 2017-04-14 15:25:21.2277614 -07:00 | 022011116 | 082031106 | 7 | 3 | 3 | 2 | 455 | 9.83 | 9.73 | 455 | 9.83 | 9.73 | 529 | 11.43 | 11.32 | 529 | 11.43 | 11.32 | 464 | 10.02 | 9.92 | 464 | 10.02 | 9.92 | 540 | 11.66 | 11.54 | 540 | 11.66 | 11.54 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {4E223C7B-766F-48C1-AC37-1A4AF307A795}
6745 | 4590 | {9402A852-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section E | CB 1118 | PGE\DMAL | 2017-04-14 15:28:56.7289242 -07:00 | 022011118 | 082031107 | 7 | 3 | 3 | 2 | 390 | 8.42 | 8.34 | 390 | 8.42 | 8.34 | 480 | 10.37 | 10.27 | 480 | 10.37 | 10.27 | 402 | 8.68 | 8.59 | 402 | 8.68 | 8.59 | 486 | 10.5 | 10.4 | 486 | 10.5 | 10.4 | Standby MUNI Carl Station (ATS 152D/252D) - 50amp Normal source to MUNI Judah Station. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {5BF1FE46-F585-4DF4-ACC4-C74CFE28668B}
6746 | 4590 | {9402A857-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section E | CB 1120 | PGE\DMAL | 2017-04-14 15:32:57.9080162 -07:00 | 022011120 | 082031108 | 7 | 3 | 3 | 2 | 480 | 10.37 | 10.27 | 480 | 10.37 | 10.27 | 559 | 12.07 | 11.95 | 559 | 12.07 | 11.95 | 490 | 10.58 | 10.47 | 490 | 10.58 | 10.47 | 570 | 12.31 | 12.19 | 570 | 12.31 | 12.19 | Standby MUNI Civic Center Station (ATS 152A/252A) - 80amp. Feeder will become standby for CentralSubway Chinatown Station. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {E3F63943-4E96-4C6A-AF9D-E305304603AD}
6747 | 4590 | {9402A85A-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section E | CB 1124 | PGE\DMAL | 2017-04-14 15:35:55.5942942 -07:00 | 022011124 | 082031109 | 7 | 3 | 3 | 2 | 481 | 10.39 | 10.29 | 481 | 10.39 | 10.29 | 592 | 12.79 | 12.66 | 592 | 12.79 | 12.66 | 495 | 10.69 | 10.58 | 495 | 10.69 | 10.58 | 599 | 12.94 | 12.81 | 599 | 12.94 | 12.81 |  |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {AD9EE46B-E1B5-4CD4-8B10-414365BAC64C}
6748 | 4590 | {9402A85F-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MISSION (SF X) | 12kv Bus Section E | CB 1125 | PGE\DMAL | 2017-04-14 15:42:20.0456230 -07:00 | 022011125 | 082031110 | 7 | 3 | 3 | 2 | 555 | 11.99 | 11.87 | 555 | 11.99 | 11.87 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 566 | 12.22 | 12.1 | 566 | 12.22 | 12.1 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | Branch SW-18010 - 500EPRc, ELC = 2 (SN=513, SE=601, WN=523, WE=613). Branch SW-18008 - 500T, ELC = 3 (SN=360, SE=400, WN=371, WE=412). Branch SW-18008 has very old former FI-1 cable. |  | FALSE | FALSE | 3000 | 3000 | 3000 | 3000 | {B9569071-C631-41B5-8EE3-D3E8203DD54D}
6750 | 4606 | {8D298968-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | GERBER | Bank 1 | CB 1101 | PGE\C8M4 | 2017-04-18 15:47:19.4978167 -07:00 | 1033901101 | 082031111 | 8 | 3 | 3 | 1 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 429 | 558 | 515 | 601 | {213B09BB-F31D-499B-8B6D-7AFBC735BA35}
6751 | 4606 | {8D29897F-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | GERBER | Bank 1 | CB 1102 | PGE\C8M4 | 2017-04-18 15:47:07.6104643 -07:00 | 1033901102 | 082031112 | 8 | 3 | 3 | 1 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 429 | 558 | 515 | 601 | {A1B7D111-15A0-4869-8D47-648F72507460}
7750 | 4608 | {A6861CA2-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | RED BLUFF | Bank 1 | CB 1103 | PGE\CTD7 | 2017-04-19 17:04:20.4565299 -07:00 | 1035401103 | 082031113 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {EBC4BD52-C146-401B-8AD3-EC408AF99D21}
7751 | 4608 | {A6861CAB-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | RED BLUFF | Bank 1 | CB 1104 | PGE\CTD7 | 2017-04-19 17:04:29.0537278 -07:00 | 1035401104 | 082031114 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {B9E68A96-25CD-492B-9C47-B2543FD10BEA}
7754 | 4607 | {A6861CFB-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | RED BLUFF | Bank 3 | CB 1101 | PGE\CTD7 | 2017-04-19 17:09:13.7442412 -07:00 | 1035401101 | 022091102 | 8 | 3 | 3 | 1 | 51 | 1.11 | 1.1 | 51 | 1.11 | 1.1 | 54 | 1.18 | 1.17 | 54 | 1.18 | 1.17 | 56 | 1.22 | 1.21 | 56 | 1.22 | 1.21 | 60 | 1.31 | 1.3 | 60 | 1.31 | 1.3 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 51 | 54 | 56 | 60 | {9C26C82A-7811-4182-970D-35E6B52AEA05}
7755 | 4607 | {A6861D0B-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | RED BLUFF | Bank 3 | CB 1102 | PGE\JZ1S | 2017-06-29 13:02:09.7211301 -07:00 | 1035401102 | 022091101 | 8 | 3 | 3 | 1 | 429 | 9.36 | 9.27 | 429 | 9.36 | 9.27 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 429 | 558 | 515 | 644 | {50438BD4-048E-4839-BD18-8CC8175347EB}
7757 | 4609 | {80988EF7-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | BANGOR | Bank 1 | CB 1101 | PGE\CTD7 | 2017-04-19 16:21:58.8533402 -07:00 | 1031901101 | 082921107 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 572 | 721 | 687 | 721 | {A10E8E72-A610-448E-BE59-C544B0D74F2D}
7758 | 4611 | {809890C8-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | CHALLENGE | Bank 1 | CB 1101 | PGE\CTD7 | 2017-04-19 17:11:19.0667340 -07:00 | 1032001101 | 082921109 | 8 | 3 | 3 | 1 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | 130 | 2.84 | 2.81 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 137 | 150 | 150 | 150 | {875C2F7D-9CC9-4AF2-AFC4-76E3AFA08CED}
7762 | 4611 | {FF363C0F-0E49-11E6-95F2-D4BED91EFF1A} | NORTH VALLEY | CHALLENGE | Bank 1 | CB 1102 | PGE\CTD7 | 2017-04-19 16:48:39.3520135 -07:00 | 1032001102 | 082921110 | 8 | 3 | 3 | 1 | 137 | 2.99 | 2.96 | 137 | 2.99 | 2.96 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | 150 | 3.27 | 3.24 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 137 | 150 | 150 | 150 | {D89DD30A-A9F2-4673-A353-7629BDF56893}
7763 | 4612 | {941FA288-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | KANAKA | Bank 1 | CB 1101 | PGE\CTD7 | 2017-04-19 17:01:02.9082130 -07:00 | 1032201101 | 022090401 | 8 | 3 | 3 | 1 | 137 | 2.99 | 2.96 | 137 | 2.99 | 2.96 | 173 | 3.78 | 3.74 | 164 | 3.58 | 3.54 | 165 | 3.6 | 3.56 | 165 | 3.6 | 3.56 | 206 | 4.5 | 4.46 | 206 | 4.5 | 4.46 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 137 | 179 | 165 | 206 | {A81AF0DB-9EA2-449A-8AE7-3F3EC8D34E15}
7764 | 4614 | {74EA794E-BD6E-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MARINA (SF F) | 4kv Main Bus | CB D-E BUS TIE (Non-SCADA) | PGE\DMAL | 2017-04-19 17:36:19.3723895 -07:00 |  | 022090403 | 3 | 3 | 3 | 2 | 2000 | 14.41 | 14.27 | 2000 | 14.41 | 14.27 | 2000 | 14.41 | 14.27 | 2000 | 14.41 | 14.27 | 2000 | 14.41 | 14.27 | 2000 | 14.41 | 14.27 | 2000 | 14.41 | 14.27 | 2000 | 14.41 | 14.27 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {BB418E3A-CC5C-4CF2-93BF-79E8FAF7ECD4}
7765 | 4617 | {A0864EC7-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | OROVILLE | Bank 2 | CB 1101 | PGE\WRA4 | 2017-05-25 21:36:23.5777422 -07:00 | 1025201101 | 083801101 | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 500 | 10.91 | 10.8 | 600 | 13.09 | 12.96 | 500 | 10.91 | 10.8 | 600 | 13.09 | 12.96 | 500 | 10.91 | 10.8 | 600 | 13.09 | 12.96 | 500 | 10.91 | 10.8 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 733 | 953 | 879 | 962 | {B84CCA5D-4C72-4C5F-9326-05EAFD95825F}
7766 | 4617 | {A0864ED7-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | OROVILLE | Bank 2 | CB 1102 | PGE\CTD7 | 2017-04-19 19:30:31.1072738 -07:00 | 1025201102 | 022090405 | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 733 | 953 | 879 | 962 | {F4411DC9-FE91-4844-BFD6-40EB58FB4FFD}
7767 | 4619 | {A0864EEA-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | OROVILLE | Bank 3 | CB 1103 | PGE\CTD7 | 2017-04-19 20:06:02.2642568 -07:00 | 1025201103 | 083801103 | 8 | 3 | 3 | 1 | 430 | 9.38 | 9.29 | 430 | 9.38 | 9.29 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 430 | 559 | 516 | 646 | {0DAF5302-B91F-45EF-B95F-12AE8F090F32}
7768 | 4619 | {A0864F01-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | OROVILLE | Bank 3 | CB 1104 | PGE\CTD7 | 2017-04-19 20:09:20.1384620 -07:00 | 1025201104 | 022090407 | 8 | 4 | 4 | 2 | 430 | 9.38 | 9.29 | 430 | 9.38 | 9.29 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 430 | 559 | 516 | 646 | {906AFA3B-7B8E-4A78-89EC-9E1676195AA5}
7771 | 4621 | {9405791D-5045-11E6-8DC6-D4BED91EFF1A} | PENINSULA | SF H MARTIN | 12kv Buses | CB 1250/12 | PGE\LMSQ | 2017-04-19 21:57:00.1654136 -07:00 |  | 022090409 | 7 | 4 | 4 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3120 | 3650 | 4115 | 4460 | {F7221E0A-7E23-4458-A763-3D3E05CFC540}
7772 | 4621 | {9D61DA88-BB3F-11E6-93A9-D4BED91EFF1A} | PENINSULA | SF H MARTIN | 12kv Buses | CB 1250/22 | PGE\LMSQ | 2017-04-19 21:57:15.8905160 -07:00 |  | 083801104 | 7 | 4 | 4 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3120 | 3650 | 4115 | 4460 | {01E81591-8F0F-4932-BDF1-42AC44E0C912}
7773 | 4621 | {EFDF1DE0-BB39-11E6-93A9-D4BED91EFF1A} | PENINSULA | SF H MARTIN | 12kv Buses | CB 1350/12 | PGE\LMSQ | 2017-04-19 21:58:08.1671213 -07:00 |  | 022090411 | 7 | 4 | 4 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3120 | 3650 | 4115 | 4460 | {564AA9E5-8471-450F-98AC-AD36E2EC2E1B}
7774 | 4621 | {AE1C1A07-BB3F-11E6-93A9-D4BED91EFF1A} | PENINSULA | SF H MARTIN | 12kv Buses | CB 1350/22 | PGE\LMSQ | 2017-04-19 21:58:31.1463632 -07:00 |  | 022090413 | 7 | 4 | 4 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3120 | 3650 | 4115 | 4460 | {A6C469D2-CB36-415B-8B42-57F04E5A444F}
7775 | 4621 | {FDDD877E-BB39-11E6-93A9-D4BED91EFF1A} | PENINSULA | SF H MARTIN | 12kv Buses | CB 1450/12 | PGE\LMSQ | 2017-04-19 21:58:50.4439343 -07:00 |  | 083801105 | 7 | 4 | 4 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3120 | 3650 | 4115 | 4460 | {D8F41533-34E3-4A38-9BD1-695F5A5C329B}
7776 | 4621 | {BA98CBEE-BB3F-11E6-93A9-D4BED91EFF1A} | PENINSULA | SF H MARTIN | 12kv Buses | CB 1450/22 | PGE\LMSQ | 2017-04-19 21:59:08.8990892 -07:00 |  | 022090402 | 7 | 4 | 4 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3120 | 3650 | 4115 | 4460 | {40CE279A-525F-4674-A11C-7C3A39E815EF}
7778 | 3859 | {32E4384A-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | WOODSIDE | Bank 2 | CB 1103 (Under Construction) | PGE\LMSQ | 2017-04-19 22:03:22.3415630 -07:00 | 024251103 | 022090404 | 8 | 4 | 4 | 2 | 1200 | 26.19 | 25.93 | 1200 | 26.19 | 25.93 | 1200 | 26.19 | 25.93 | 1200 | 26.19 | 25.93 | 1200 | 26.19 | 25.93 | 1200 | 26.19 | 25.93 | 1200 | 26.19 | 25.93 | 1200 | 26.19 | 25.93 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {41A8C867-D2EB-4666-81D6-555AA2FA454E}
7779 | 4623 | {13849469-D828-11E6-8DDC-9CB70D532D7F} | PENINSULA | EAST GRAND | 12kV Buses | CB 1350/12 | PGE\LMSQ | 2017-04-20 10:06:35.6274006 -07:00 |  | 022090406 | 7 | 4 | 4 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3120 | 3650 | 4115 | 4460 | {9350DD9E-FE25-4992-9949-F1E0A1A4405F}
7780 | 4623 | {16839E13-ADE4-11E6-A430-9CB70DEE0A5E} | PENINSULA | EAST GRAND | 12kV Buses | CB 1350/22 | PGE\LMSQ | 2017-04-20 10:06:57.5770227 -07:00 |  | 022090408 | 7 | 4 | 4 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3120 | 3650 | 4115 | 4460 | {1E8DE778-F139-440A-BF49-5D5F595A5824}
7781 | 4623 | {426F005D-D828-11E6-8DDC-9CB70D532D7F} | PENINSULA | EAST GRAND | 12kV Buses | CB 1450/12 | PGE\LMSQ | 2017-04-20 10:07:20.3534607 -07:00 |  | 022090410 | 7 | 4 | 4 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3120 | 3650 | 4115 | 4460 | {55811085-D3B8-49FB-AF3D-7E802C6B209F}
7782 | 4623 | {377A646E-ADE4-11E6-A430-9CB70DEE0A5E} | PENINSULA | EAST GRAND | 12kV Buses | CB 1450/22 | PGE\LMSQ | 2017-04-20 10:07:38.7774150 -07:00 |  | 022090412 | 7 | 4 | 4 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 3120 | 3650 | 4115 | 4460 | {83DB738F-320F-4CBC-9D0D-51026CF31C3D}
7783 | 4232 | {B124873A-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | SARATOGA | Bank 3 | CB 1112 | PGE\RPBK | 2017-04-20 11:02:05.5996827 -07:00 | 0833701112 | 022090414 | 8 | 3 | 3 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Relay Min: Ph.=720A, T=6, L=3.0, Inst=3600 (phase) Grd=182A, T=1.5, L=2.0 |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {FD99926C-881A-4771-8D1D-DF24346AF0B3}
7784 | 4232 | {B1248751-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | SARATOGA | Bank 3 | CB 1113 | PGE\RPBK | 2017-04-20 11:01:43.5564588 -07:00 | 0833701113 | 083801106 | 8 | 3 | 3 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Relay Min: Ph=720A, T=6, L=2.0, Inst=4560A (phase) Grd=183A, T=1.6, L=3.0 |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {8F6BB83F-4221-435B-B70D-AD46C06FC676}
7785 | 4232 | {B124877D-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | SARATOGA | Bank 3 | CB 1114 | PGE\RPBK | 2017-04-20 11:11:24.0124212 -07:00 | 0833701114 | 083801107 | 8 | 3 | 3 | 2 | 581 | 12.68 | 12.55 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 598 | 13.05 | 12.92 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | Relay Min: Ph=720A, T=6, L=3.0, Inst=6000 (phase) Grd=181A, T=1.5, L=3.0, Inst=3388 (ground) |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {CFFD90A6-A09C-4B1C-8506-ED82D1B25498}
7787 | 4232 | {B12487B8-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | SARATOGA | Bank 3 | CB 1115 | PGE\RPBK | 2017-04-20 11:52:37.3307841 -07:00 | 0833701115 | 083801108 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 720 | 15.71 | 15.55 | 684 | 14.93 | 14.78 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 720 | 15.71 | 15.55 | 684 | 14.93 | 14.78 | Relay Min: Ph=720A, T=3, L=3.0, Inst=6000 (Phase) Grd=180A, T=0.75, L=5.5, Inst=3388 (Ground) |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F57FDEDB-B3BC-4D7C-85D0-408159A12E70}
7788 | 4460 | {9ED2E3A6-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | BRITTON | Bank 1 | CB 1105 | PGE\MSJ9 | 2017-04-20 17:50:39.5591647 -07:00 | 0836101105 | 083801109 | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | SW 2349 - 8 hour emergency rating of 800 Amps Relay Minimum Phase: 720A T 6 L 3 CT Ratio: 600:5 To Operate Ground: 183A T 1.5 L 1.5 Ammeter Range 0 to 100 |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {2C8332C9-98DB-4F57-8117-25927CD84A51}
7790 | 4624 | {8D298A2D-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | HAMILTON A | Bank 1 | CB 1101 | PGE\GSD5 | 2017-04-20 14:01:32.2652530 -07:00 | 1021201101 | 083801110 | 8 | 4 | 4 | 1 | 300 | 6.55 | 6.48 | 285 | 6.22 | 6.16 | 300 | 6.55 | 6.48 | 285 | 6.22 | 6.16 | 300 | 6.55 | 6.48 | 285 | 6.22 | 6.16 | 300 | 6.55 | 6.48 | 285 | 6.22 | 6.16 |  |  | FALSE | FALSE | 384 | 500 | 461 | 577 | {FB2016CE-0976-4696-B3CB-891D5E659791}
7791 | 4624 | {8D298A3D-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | HAMILTON A | Bank 1 | CB 1102 | PGE\GSD5 | 2017-04-20 14:05:00.6107767 -07:00 | 1021201102 | 083801111 | 8 | 4 | 4 | 1 | 300 | 6.55 | 6.48 | 285 | 6.22 | 6.16 | 300 | 6.55 | 6.48 | 285 | 6.22 | 6.16 | 300 | 6.55 | 6.48 | 285 | 6.22 | 6.16 | 300 | 6.55 | 6.48 | 285 | 6.22 | 6.16 |  | Information Extracted from Sharepoint. | FALSE | FALSE | 384 | 500 | 461 | 577 | {9A1F9D18-3CDB-4809-A37B-E4FBF06B2D86}
7792 | 4613 | {85BCDE0A-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MARINA (SF F) | 12kv Bus 1 (FY-1, FY-2, FY-3, FY-4) | CB 1101 | PGE\DMAL | 2017-05-06 22:02:03.5181443 -07:00 | 022781101 | 083802114 | 7 | 3 | 3 | 2 | 405 | 8.75 | 8.66 | 405 | 8.75 | 8.66 | 450 | 9.72 | 9.62 | 450 | 9.72 | 9.62 | 417 | 9.01 | 8.92 | 417 | 9.01 | 8.92 | 463 | 10 | 9.9 | 463 | 10 | 9.9 | Alternate source to Doyle Drive (Golden Gate Bridge) |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {00000000-0000-0000-0000-000000000000}
7793 | 4613 | {85BCDE14-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MARINA (SF F) | 12kv Bus 1 (FY-1, FY-2, FY-3, FY-4) | CB 1103 | PGE\DMAL | 2017-04-20 14:11:56.8649429 -07:00 | 022781103 | 083802115 | 7 | 3 | 3 | 2 | 517 | 11.17 | 11.06 | 517 | 11.17 | 11.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 527 | 11.38 | 11.27 | 527 | 11.38 | 11.27 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {00000000-0000-0000-0000-000000000000}
7794 | 4594 | {85BCDE0F-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MARINA (SF F) | 12kv Bus 2 | CB 1102 | PGE\DMAL | 2017-04-20 14:16:07.2290763 -07:00 | 022781102 | 083802116 | 7 | 3 | 3 | 2 | 333 | 7.19 | 7.12 | 333 | 7.19 | 7.12 | 370 | 7.99 | 7.91 | 370 | 7.99 | 7.91 | 343 | 7.41 | 7.34 | 343 | 7.41 | 7.34 | 381 | 8.23 | 8.15 | 381 | 8.23 | 8.15 | Branch SW-11542 - 250T ELC=2 (SN=258, SE=286, WN=266, WE=295) Branch SW-11540 - 500T ELC=5 (SN=333, SE=370, WN=343, WE=381) |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {00000000-0000-0000-0000-000000000000}
7795 | 4616 | {85BCDE22-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MARINA (SF F) | Bank 2 | CB 401 (Non-SCADA) | PGE\DMAL | 2017-04-20 14:31:53.1548888 -07:00 | 022780401 | 083802117 | 3 | 3 | 3 | 2 | 363 | 2.62 | 2.59 | 363 | 2.62 | 2.59 | 392 | 2.82 | 2.79 | 392 | 2.82 | 2.79 | 374 | 2.69 | 2.66 | 374 | 2.69 | 2.66 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 1301 | 1691 | 1561 | 1951 | {DCF398DD-94EA-4A4F-81E6-EEF74783B6EA}
7796 | 4615 | {85BCDDEB-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MARINA (SF F) | Bank 1 | CB 402 (Non-SCADA) | PGE\DMAL | 2017-04-20 14:32:22.4883408 -07:00 | 022780402 | 083802118 | 3 | 3 | 3 | 2 | 363 | 2.62 | 2.59 | 363 | 2.62 | 2.59 | 392 | 2.82 | 2.79 | 392 | 2.82 | 2.79 | 374 | 2.69 | 2.66 | 374 | 2.69 | 2.66 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 1301 | 1691 | 1561 | 1951 | {391B2C4B-F78E-4A31-9909-864822E71960}
7797 | 4615 | {85BCDDF0-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MARINA (SF F) | Bank 1 | CB 403 (Non-SCADA) | PGE\DMAL | 2017-04-20 14:32:47.3125547 -07:00 | 022780403 | 083802119 | 3 | 3 | 3 | 2 | 363 | 2.62 | 2.59 | 363 | 2.62 | 2.59 | 392 | 2.82 | 2.79 | 392 | 2.82 | 2.79 | 374 | 2.69 | 2.66 | 374 | 2.69 | 2.66 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 1301 | 1691 | 1561 | 1951 | {A89718EC-82F4-40F0-B69E-F2C702CE8C92}
7798 | 4616 | {B2FF117C-3C98-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | MARINA (SF F) | Bank 2 | CB 404 (Non-SCADA) | PGE\DMAL | 2017-04-20 14:30:58.0142402 -07:00 | 022780404 | 022260402 | 3 | 3 | 3 | 2 | 363 | 2.62 | 2.59 | 363 | 2.62 | 2.59 | 392 | 2.82 | 2.79 | 392 | 2.82 | 2.79 | 374 | 2.69 | 2.66 | 374 | 2.69 | 2.66 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 1301 | 1691 | 1561 | 1951 | {9A22E702-FDFB-44F9-94A4-F3289A308439}
7799 | 4625 | {B89B4B0B-0B3F-11E6-9D37-D4BED91EFF1A} | DE ANZA | LOCKHEED NO.1 | BANK 1 | CB 1101 | PGE\IRB2 | 2017-04-20 14:41:20.1158493 -07:00 | 0829901101 | 022260404 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {B75F199D-167D-4DE1-863A-0A5DA8AC0CA5}
7800 | 4625 | {C0F57A20-0B3F-11E6-9D37-D4BED91EFF1A} | DE ANZA | LOCKHEED NO.1 | BANK 1 | CB 1102 | PGE\IRB2 | 2017-06-01 15:14:00.3685166 -07:00 | 0829901102 | 022260406 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {0A9BB923-BF55-4647-99B2-B17EFD3A06BE}
7801 | 4616 | {85BCDE25-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MARINA (SF F) | Bank 2 | CB 405 (Non-SCADA) | PGE\DMAL | 2017-04-20 14:34:39.8094637 -07:00 | 022780405 | 022260408 | 3 | 3 | 3 | 2 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 1301 | 1691 | 1561 | 1951 | {294AA7EE-DFBC-4232-AB88-BCDB92F63259}
7803 | 4625 | {B89B4B0E-0B3F-11E6-9D37-D4BED91EFF1A} | DE ANZA | LOCKHEED NO.1 | BANK 1 | CB 1103 | PGE\IRB2 | 2017-04-20 14:40:56.9650041 -07:00 | 0829901103 | 022260401 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {F8617BAD-7D23-48C0-8877-83B8FEE49819}
7804 | 4625 | {AF9B6F80-0B3F-11E6-9D37-D4BED91EFF1A} | DE ANZA | LOCKHEED NO.1 | BANK 1 | CB 1104 | PGE\IRB2 | 2017-04-20 14:40:39.6642714 -07:00 | 0829901104 | 022260403 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {BE96DCFF-D4F8-44E7-831D-5BFFDF12A6D3}
7805 | 4615 | {85BCDDFF-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MARINA (SF F) | Bank 1 | CB 407 (Non-SCADA) | PGE\DMAL | 2017-04-20 14:36:03.6282425 -07:00 | 022780407 | 022260405 | 3 | 3 | 3 | 2 | 363 | 2.62 | 2.59 | 363 | 2.62 | 2.59 | 392 | 2.82 | 2.79 | 392 | 2.82 | 2.79 | 374 | 2.69 | 2.66 | 374 | 2.69 | 2.66 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 1301 | 1691 | 1561 | 1951 | {04C80A55-D90F-42E5-9FE4-73E3D9765B19}
7806 | 4616 | {85BCDE2A-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | MARINA (SF F) | Bank 2 | CB 408 (Non-SCADA) | PGE\DMAL | 2017-04-20 14:37:27.2597865 -07:00 | 022780408 | 022260407 | 3 | 3 | 3 | 2 | 363 | 2.62 | 2.59 | 363 | 2.62 | 2.59 | 392 | 2.82 | 2.79 | 392 | 2.82 | 2.79 | 374 | 2.69 | 2.66 | 374 | 2.69 | 2.66 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 1301 | 1691 | 1561 | 1951 | {527F40D6-93A7-4E36-BE8B-EE7610515DA3}
7807 | 4625 | {8FA36210-FDBD-11E5-9D37-D4BED91EFF1A} | DE ANZA | LOCKHEED NO.1 | BANK 1 | CB 1105 | PGE\IRB2 | 2017-04-20 15:04:47.4759995 -07:00 | 0829901105 | 022260409 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {09C4CCC2-650E-49DC-A04C-A1E93586B42D}
7808 | 4628 | {9059BE23-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | ALHAMBRA | Bank 1 | CB 1101 | PGE\FCR1 | 2017-04-20 15:11:27.4451640 -07:00 | 0141001101 | 083392108 | 8 | 3 | 3 | 1 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {04D4B1F2-EBE2-4EB9-ACF0-590ECCDFBE75}
7809 | 4626 | {9EA96105-0B3F-11E6-9D37-D4BED91EFF1A} | DE ANZA | LOCKHEED NO.1 | BANK 2 | CB 1106 (Under Construction) | PGE\IRB2 | 2017-04-20 14:53:51.5042988 -07:00 | 0829901106 | 254071108 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {BD5B3DFB-CDA1-4D58-BD3F-03B74AAD617C}
7810 | 4626 | {AF9B6F7B-0B3F-11E6-9D37-D4BED91EFF1A} | DE ANZA | LOCKHEED NO.1 | BANK 2 | CB 1107 (Under Construction) | PGE\IRB2 | 2017-04-20 14:53:22.5033411 -07:00 | 0829901107 | 082921101 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {144BEC62-B6B0-4E6C-9B79-70BBB771327D}
7811 | 4626 | {A75B5CC6-0B3F-11E6-9D37-D4BED91EFF1A} | DE ANZA | LOCKHEED NO.1 | BANK 2 | CB 1108 (Under Construction) | PGE\IRB2 | 2017-04-20 14:55:25.0124970 -07:00 | 0829901108 | 082921102 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {3219F2FC-D634-4C2E-8DE3-166496D423CC}
7812 | 4626 | {A75B5CC3-0B3F-11E6-9D37-D4BED91EFF1A} | DE ANZA | LOCKHEED NO.1 | BANK 2 | CB 1109 (Under Construction) | PGE\IRB2 | 2017-04-20 14:56:13.7322339 -07:00 | 0829901109 | 082921103 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {6A07DDF3-F688-4307-AA42-8EA4902757A7}
7813 | 4626 | {BE88055E-FDBD-11E5-9D37-D4BED91EFF1A} | DE ANZA | LOCKHEED NO.1 | BANK 2 | CB 1110 (Under Construction) | PGE\IRB2 | 2017-04-20 14:57:59.7723490 -07:00 | 0829901110 | 082921104 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {96EA1B44-E81E-422E-8A6F-56E9C63EADCD}
7815 | 4460 | {9ED2E3CB-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | BRITTON | Bank 1 | CB 1106 | PGE\MSJ9 | 2017-04-20 17:49:18.5801137 -07:00 | 0836101106 | 082921105 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | SW 19421 - 8 hour emergency rating of 800 Amps Relay Minimum Phase: 720A T 6 L 3 CT Ratio: 600:5 To Operate Ground: 183A T 1.5 L 1.5 Ammeter Range 0 to 100 |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {9562CF94-22B9-47FC-9158-4A2842706AA6}
7818 | 4628 | {9059BE28-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | ALHAMBRA | Bank 1 | CB 1102 | PGE\FCR1 | 2017-04-21 14:46:33.8822403 -07:00 | 0141001102 | 082921111 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {68F27854-D5F2-49B0-A27E-33AA3380B455}
7819 | 4629 | {96C8A4A4-FDB3-11E5-9D37-D4BED91EFF1A} | DIABLO | ALHAMBRA | BANK 2 | CB 1105 | PGE\FCR1 | 2017-04-21 14:47:38.9307304 -07:00 | 0141001105 | 082921112 | 8 | 3 | 3 | 1 | 457 | 9.97 | 9.87 | 457 | 9.97 | 9.87 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 549 | 11.98 | 11.86 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 481 | 625 | 577 | 721 | {C02AF08E-0647-4D6F-8E43-C90431B8C7A9}
7820 | 4633 | {077C4B7D-0E49-11E6-95F2-D4BED91EFF1A} | DIABLO | BABEL | BANK 1 | CB 401 (Non-SCADA) | PGE\FCR1 | 2017-04-21 14:53:18.3250112 -07:00 | 013850401 | 082921113 | 4 | 3 | 3 | 1 | 303 | 2.29 | 2.27 | 303 | 2.29 | 2.27 | 393 | 2.97 | 2.94 | 393 | 2.97 | 2.94 | 364 | 2.76 | 2.73 | 364 | 2.76 | 2.73 | 400 | 3.03 | 3 | 400 | 3.03 | 3 |  |  | FALSE | FALSE | 303 | 395 | 364 | 455 | {5962F492-6436-48F3-B9B3-483856FC4F62}
7821 | 4635 | {B53783D9-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | CLAYTON | Bank 1 | CB 2213 | PGE\FCR1 | 2017-04-21 14:56:06.3058326 -07:00 | 0120202213 | 082921114 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {973ADADF-4294-4DCC-ADB8-2184A78BABFA}
7839 | 4639 | {A7233111-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PLACER | Bank 2 | CB 1103 | PGE\MTN6 | 2017-04-20 17:06:08.6859485 -07:00 | 1524601103 | 082921116 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 667 | 14.56 | 14.41 | 667 | 14.56 | 14.41 |  |  | FALSE | FALSE | 1146 | 1489 | 1375 | 1718 | {E85AEC24-778D-452C-8D23-1B1D0142B5CD}
7840 | 4640 | {C07E0030-0E48-11E6-95F2-D4BED91EFF1A} | DIABLO | CONCORD NO 1 | UNIT SUB 401 | CB 401 (Non-SCADA) | PGE\FCR1 | 2017-04-21 15:26:40.2082870 -07:00 | 012960401 | 082921117 | 4 | 3 | 3 | 1 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 429 | 3.25 | 3.22 | 429 | 3.25 | 3.22 | 396 | 3 | 2.97 | 396 | 3 | 2.97 | 495 | 3.75 | 3.71 | 495 | 3.75 | 3.71 |  |  | FALSE | FALSE | 330 | 429 | 396 | 495 | {0C952AB9-AC9B-451F-A92C-0F32769AB38E}
7841 | 4631 | {9ED2E454-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | BRITTON | Bank 2 | CB 1110 | PGE\MSJ9 | 2017-04-20 18:12:39.1744322 -07:00 | 0836101110 | 082921118 | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | SW 1319 - 8 hour emergency rating of 800 Amps |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {A2A583FF-DCBD-40A1-B950-C01486E53574}
7842 | 4631 | {9ED2E479-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | BRITTON | Bank 2 | CB 1111 | PGE\MSJ9 | 2017-04-20 18:13:04.1858809 -07:00 | 0836101111 | 082921119 | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | Relay Minimum Phase: 720A T 6 L 3.5 CT Ratio: 600:5 To Operate Ground: 180A T 1.5 L 1.5 Ammeter Range 0 to 100 |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {D219AAF7-B746-4B91-9812-81995D6EF976}
7845 | 4641 | {A7233124-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | PLACER | Bank 3 | CB 1104 | PGE\MTN6 | 2017-04-20 17:17:38.3341285 -07:00 | 1524601104 | 022130403 | 8 | 3 | 3 | 1 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 | 700 | 15.28 | 15.13 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {410FA947-A24F-4BEF-A434-792524F80D49}
7847 | 4642 | {CB3A2E82-0E48-11E6-95F2-D4BED91EFF1A} | DIABLO | CONCORD NO 1 | UNIT SUB 402 | CB 402 (Non-SCADA) | PGE\FCR1 | 2017-04-21 15:28:33.2981062 -07:00 | 012960402 | 022130406 | 4 | 3 | 3 | 1 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 429 | 3.25 | 3.22 | 429 | 3.25 | 3.22 | 396 | 3 | 2.97 | 396 | 3 | 2.97 | 495 | 3.75 | 3.71 | 495 | 3.75 | 3.71 |  |  | FALSE | FALSE | 330 | 429 | 396 | 495 | {E0BB0CAF-0A8D-422A-86F6-C68066BB19A8}
7848 | 4643 | {E6BCD5E5-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | FAIRVIEW | Bank 5 | CB 2206 | PGE\FCR1 | 2017-04-21 15:30:18.7112986 -07:00 | 0134302206 | 022270401 | 12 | 3 | 3 | 2 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 668 | 25.25 | 25 | 668 | 25.25 | 25 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 668 | 25.25 | 25 | 668 | 25.25 | 25 |  |  | FALSE | FALSE | 1325 | 1723 | 1590 | 1988 | {DF2D4564-83C1-4256-AFA5-5224F8C9F99C}
7849 | 4643 | {813217E8-FDB8-11E5-9D37-D4BED91EFF1A} | DIABLO | FAIRVIEW | Bank 5 | CB 2207 | PGE\FCR1 | 2017-04-20 17:31:18.6192005 -07:00 | 0134302207 | 253911107 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 792 | 29.93 | 29.63 | 792 | 29.93 | 29.63 | 691 | 26.12 | 25.86 | 691 | 26.12 | 25.86 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 |  |  | FALSE | FALSE | 1325 | 1723 | 1590 | 1988 | {5625A360-AB3D-4613-98AF-F1347FEE8DBC}
7850 | 4644 | {3E9235BE-B8CC-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | SF N | 12kv Bus 1 (NX-1, NX-2, NX-3, NX-4) | CB 1101 | PGE\DMAL | 2017-05-17 16:58:13.5373389 -07:00 |  | 252821105 | 7 | 3 | 3 | 2 | 490 | 10.58 | 10.47 | 490 | 10.58 | 10.47 | 549 | 11.86 | 11.74 | 549 | 11.86 | 11.74 | 505 | 10.91 | 10.8 | 505 | 10.91 | 10.8 | 565 | 12.2 | 12.08 | 565 | 12.2 | 12.08 | Mainline reconfiguration as part of new 12kV switchgear project 05/2017. |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {00000000-0000-0000-0000-000000000000}
7851 | 4644 | {4B1DAF56-B8CC-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | SF N | 12kv Bus 1 (NX-1, NX-2, NX-3, NX-4) | CB 1102 | PGE\DMAL | 2017-05-17 17:03:17.5462311 -07:00 |  | 022270403 | 7 | 3 | 3 | 2 | 473 | 10.22 | 10.12 | 473 | 10.22 | 10.12 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 482 | 10.41 | 10.31 | 482 | 10.41 | 10.31 | 568 | 12.27 | 12.15 | 568 | 12.27 | 12.15 | Mainline reconfiguration as part of new 12kV switchgear project 05/2017. |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {00000000-0000-0000-0000-000000000000}
7852 | 4643 | {E6BCD600-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | FAIRVIEW | Bank 5 | CB 2208 | PGE\FCR1 | 2017-04-21 15:31:20.6392087 -07:00 | 0134302208 | 022270402 | 12 | 3 | 3 | 1 | 515 | 19.46 | 19.27 | 489 | 18.48 | 18.3 | 578 | 21.84 | 21.62 | 549 | 20.75 | 20.54 | 666 | 25.17 | 24.92 | 632 | 23.89 | 23.65 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1325 | 1723 | 1590 | 1988 | {50B429DC-42B6-42D6-B5D9-8264DA61C2B6}
7855 | 4646 | {B413E6CD-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | WEIMAR | Bank 1 | CB 1101 | PGE\MTN6 | 2017-04-20 17:34:54.1014392 -07:00 | 1524901101 | 022270404 | 8 | 3 | 3 | 1 | 429 | 9.36 | 9.27 | 429 | 9.36 | 9.27 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 429 | 558 | 515 | 644 | {08D8577B-FC5C-4D38-A009-092F550A2A88}
7856 | 4646 | {B413E6DD-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | WEIMAR | Bank 1 | CB 1102 | PGE\MTN6 | 2017-04-20 17:38:32.5732450 -07:00 | 1524901102 | 022270405 | 8 | 3 | 3 | 1 | 429 | 9.36 | 9.27 | 429 | 9.36 | 9.27 | 558 | 12.18 | 12.06 | 549 | 11.98 | 11.86 | 515 | 11.24 | 11.13 | 515 | 11.24 | 11.13 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 429 | 558 | 515 | 644 | {04202EC9-781E-43FC-9441-482AEE415992}
7858 | 4647 | {A8368921-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF N | Bank 1 | CB 401 | PGE\DMAL | 2017-05-17 16:42:45.5710850 -07:00 | 022280401 | 022270406 | 3 | 3 | 3 | 2 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 2220 | 2886 | 2664 | 3000 | {8076FFCB-B7AE-40EC-A365-CF187165B381}
7860 | 4647 | {D002CE6A-3C97-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | SF N | Bank 1 | CB 403 | PGE\DMAL | 2017-05-17 16:45:14.5829809 -07:00 | 022280403 | 022130401 | 3 | 3 | 3 | 2 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 2220 | 2886 | 2664 | 3000 | {8D94EE6C-1BDE-489D-AAA4-E9253835CA42}
7861 | 4647 | {C9E49519-3C97-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | SF N | Bank 1 | CB 405 | PGE\DMAL | 2017-04-20 18:07:19.7362605 -07:00 | 022280405 | 022130405 | 3 | 3 | 3 | 2 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 2220 | 2886 | 2664 | 3000 | {1E046943-D5F4-4A26-B578-3DF9FB03DEED}
7862 | 4648 | {C9E49516-3C97-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | SF N | Bank 2 | CB 402 | PGE\DMAL | 2017-04-20 18:10:09.7766647 -07:00 | 022280402 | 022130407 | 3 | 3 | 3 | 2 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 2220 | 2886 | 2664 | 3000 | {4565D559-B156-4502-8E33-53D35C098376}
7863 | 4648 | {C31AFA77-3C97-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | SF N | Bank 2 | CB 406 | PGE\DMAL | 2017-05-17 16:50:58.5050704 -07:00 | 022280406 | 022130409 | 3 | 3 | 3 | 2 | 378 | 2.72 | 2.69 | 378 | 2.72 | 2.69 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 389 | 2.8 | 2.77 | 389 | 2.8 | 2.77 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 2220 | 2886 | 2664 | 3000 | {FC60008A-B3C3-4CD5-B39B-154A2DA345D0}
7864 | 4648 | {C31AFA72-3C97-11E6-B38D-D4BED91EFF1A} | SAN FRANCISCO | SF N | Bank 2 | CB 408 | PGE\DMAL | 2017-04-20 18:04:21.5199367 -07:00 | 022280408 | 022130411 | 3 | 3 | 3 | 2 | 378 | 2.72 | 2.69 | 378 | 2.72 | 2.69 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 | 389 | 2.8 | 2.77 | 389 | 2.8 | 2.77 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 2220 | 2886 | 2664 | 3000 | {E36AE476-D2E8-4AD4-AFB1-3E09C3C33FB2}
7867 | 4650 | {A4FD4410-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LAWRENCE | Bank 2 | CB 1106 | PGE\IRB2 | 2017-04-21 08:39:33.9811265 -07:00 | 0834201106 | 022130402 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {D10B4123-B79A-406F-8F9F-CC9D5AE824C2}
7868 | 4650 | {A4FD4419-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LAWRENCE | Bank 2 | CB 1108 | PGE\IRB2 | 2017-04-21 08:38:45.3156814 -07:00 | 0834201108 | 022130404 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {95C6F74F-6D74-49B1-A4DC-1E79431A8BC7}
7869 | 4650 | {A4FD4422-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LAWRENCE | Bank 2 | CB 1109 | PGE\IRB2 | 2017-04-21 08:38:00.1920946 -07:00 | 0834201109 | 022130408 | 7 | 3 | 3 | 2 | 564 | 12.18 | 12.06 | 564 | 12.18 | 12.06 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {9F1A4D1C-B01E-414A-9D5F-B0256FA5F7F8}
7871 | 4652 | {AC1BD67B-654E-11E6-9BE4-80000BC6CD8D} | DE ANZA | LAWRENCE | Bank 3 | CB 1110 | PGE\ACT0 | 2017-05-03 14:17:24.9644614 -07:00 | 083421110 | 022130410 | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 552 | 12.05 | 11.93 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2200 | 2640 | 2200 | 2640 | {F7826C8F-257E-4CB3-9E9F-5D5D2A9E51EF}
7872 | 4652 | {A4FD4445-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LAWRENCE | Bank 3 | CB 1111 | PGE\IRB2 | 2017-04-21 08:36:28.9775412 -07:00 | 0834201111 | 022781102 | 7 | 3 | 3 | 2 | 454 | 9.81 | 9.71 | 454 | 9.81 | 9.71 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 468 | 10.11 | 10.01 | 468 | 10.11 | 10.01 | 566 | 12.22 | 12.1 | 566 | 12.22 | 12.1 |  |  | FALSE | FALSE | 2200 | 2640 | 2200 | 2640 | {18BB6148-E827-4ECC-A6B1-CB5AD3A4DA88}
7873 | 4652 | {A4FD444E-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LAWRENCE | Bank 3 | CB 1112 | PGE\IRB2 | 2017-04-21 08:30:07.0029463 -07:00 | 0834201112 | 022781101 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 2200 | 2640 | 2200 | 2640 | {0FDB8B09-C028-40D6-B931-337B868CB83D}
7874 | 4652 | {A4FD445E-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LAWRENCE | Bank 3 | CB 1113 | PGE\IRB2 | 2017-04-21 08:29:25.9829222 -07:00 | 0834201113 | 012061104 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 2200 | 2640 | 2200 | 2640 | {4CB55E31-E23C-4BC8-AE8D-80852EC02CED}
7876 | 4661 | {FF012CB7-78E3-11E5-8C7B-9CB70D532D7F} | DIABLO | LAKEWOOD | Bank 1 | CB 2225 | PGE\FCR1 | 2017-04-21 15:54:17.2518699 -07:00 | 0135302225 | 012541103 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 489 | 18.48 | 18.3 | 578 | 21.84 | 21.62 | 549 | 20.75 | 20.54 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1600 | {B8B1486E-7980-478B-A77C-CD63012DC1BE}
7877 | 4661 | {0507CEB8-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | LAKEWOOD | Bank 1 | CB 2227 | PGE\FCR1 | 2017-04-21 15:55:03.2804249 -07:00 | 0135302227 | 013471118 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 732 | 27.66 | 27.38 | 732 | 27.66 | 27.38 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1600 | {B7C009D7-6481-4072-9951-C2DDB2135770}
7878 | 4664 | {0B349629-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | LAKEWOOD | Bank 4 | CB 2107 | PGE\FCR1 | 2017-04-21 15:56:24.7275629 -07:00 | 0135302107 | 013471120 | 12 | 3 | 3 | 1 | 530 | 20.03 | 19.83 | 530 | 20.03 | 19.83 | 728 | 27.51 | 27.23 | 728 | 27.51 | 27.23 | 634 | 23.96 | 23.72 | 634 | 23.96 | 23.72 | 768 | 29.03 | 28.74 | 768 | 29.03 | 28.74 |  |  | FALSE | FALSE | 1322 | 1719 | 1587 | 1984 | {F71DD69C-9C5D-43E1-BC34-13FD22D12531}
7880 | 4664 | {1147BB2F-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | LAKEWOOD | Bank 4 | CB 2109 | PGE\FCR1 | 2017-04-21 15:57:10.0851932 -07:00 | 0135302109 | 013471121 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 674 | 25.47 | 25.22 | 674 | 25.47 | 25.22 |  |  | FALSE | FALSE | 1322 | 1719 | 1587 | 1984 | {0FF1F448-4047-413F-A173-729A0E75FCE0}
7882 | 4661 | {0507CEA0-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | LAKEWOOD | Bank 1 | CB 2226 | PGE\MFN3 | 2017-04-21 09:52:25.9024233 -07:00 | 0135302226 | 013471123 | 12 | 3 | 1 | 1 | 503 | 19.01 | 18.82 | 489 | 18.48 | 18.3 | 578 | 21.84 | 21.62 | 549 | 20.75 | 20.54 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 | 600 | 22.68 | 22.45 | 570 | 21.54 | 21.32 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1600 | {060C690B-BAEB-449D-8D7B-7F1F227BB3E3}
7885 | 4664 | {1147BB21-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | LAKEWOOD | Bank 4 | CB 2108 | PGE\MFN3 | 2017-04-21 09:57:51.0438759 -07:00 | 0135302108 | 013471124 | 12 | 3 | 1 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 666 | 25.17 | 24.92 | 666 | 25.17 | 24.92 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 |  |  | FALSE | FALSE | 1322 | 1719 | 1587 | 1984 | {BE093D6C-68A5-4AFF-9F11-A590AC8B4020}
7888 | 4666 | {307BB336-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | MEADOW LANE | Bank 1 | CB 2102 | PGE\FCR1 | 2017-04-21 16:02:32.6751507 -07:00 | 0143002102 | 013471122 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 674 | 25.47 | 25.22 | 674 | 25.47 | 25.22 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {9E5F713C-19E1-4377-B41F-95C9AA0E4A4E}
7889 | 4666 | {307BB33B-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | MEADOW LANE | Bank 1 | CB 2103 | PGE\FCR1 | 2017-04-21 10:11:02.4470949 -07:00 | 0143002103 | 013471127 | 12 | 3 | 3 | 1 | 540 | 20.41 | 20.21 | 540 | 20.41 | 20.21 | 686 | 25.93 | 25.67 | 686 | 25.93 | 25.67 | 598 | 22.6 | 22.37 | 598 | 22.6 | 22.37 | 760 | 28.72 | 28.43 | 760 | 28.72 | 28.43 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {233B554F-5B66-491B-849E-6C4D700A28DE}
7890 | 4649 | {A4FD41EC-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | BRITTON | Bank 3 | CB 1112 | PGE\MSJ9 | 2017-04-21 11:13:43.3022320 -07:00 | 0836101112 | 013471129 | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | CO 3739 - Part 57 with maximum ratings of 600 A cc. |  | FALSE | FALSE | 1200 | 1200 | 1200 | 1200 | {F6FF36E0-350D-4625-9108-3D7532F9A8A9}
7892 | 4666 | {36749994-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | MEADOW LANE | Bank 1 | CB 2104 | PGE\FCR1 | 2017-04-21 16:06:34.2704543 -07:00 | 0143002104 | 043051101 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1786 | {C13C30C0-0C49-47D7-B7F8-945BBEB9E156}
7894 | 4667 | {367499AE-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | MEADOW LANE | Bank 2 | CB 2105 | PGE\FCR1 | 2017-04-21 16:31:27.0467060 -07:00 | 0143002105 | 258591101 | 12 | 3 | 3 | 1 | 515 | 19.46 | 19.27 | 489 | 18.48 | 18.3 | 578 | 21.84 | 21.62 | 549 | 20.75 | 20.54 | 666 | 25.17 | 24.92 | 632 | 23.89 | 23.65 | 700 | 26.46 | 26.2 | 675 | 25.51 | 25.25 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {7AC0A45C-FCBE-4F15-BCFD-ED293DC85427}
7896 | 4649 | {A4FD41F5-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | BRITTON | Bank 3 | CB 1113 | PGE\MSJ9 | 2017-04-21 11:24:56.1928974 -07:00 | 0836101113 | 253161112 | 7 | 3 | 3 | 2 | 200 | 4.32 | 4.28 | 200 | 4.32 | 4.28 | 200 | 4.32 | 4.28 | 200 | 4.32 | 4.28 | 200 | 4.32 | 4.28 | 200 | 4.32 | 4.28 | 200 | 4.32 | 4.28 | 200 | 4.32 | 4.28 | SW 3079 - 8 hour emergency rating of 800 Amps |  | FALSE | FALSE | 1200 | 1200 | 1200 | 1200 | {285AC04B-0035-41DB-8FE8-006A6C3F16D2}
7899 | 4667 | {3C8155FA-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | MEADOW LANE | Bank 2 | CB 2106 | PGE\FCR1 | 2017-04-21 16:32:11.0624869 -07:00 | 0143002106 | 083671113 | 12 | 3 | 3 | 1 | 515 | 19.46 | 19.27 | 489 | 18.48 | 18.3 | 578 | 21.84 | 21.62 | 549 | 20.75 | 20.54 | 598 | 22.6 | 22.37 | 570 | 21.54 | 21.32 | 711 | 26.87 | 26.6 | 675 | 25.51 | 25.25 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {DAC07B3B-6796-4B3A-B0C2-7F9CA5C80599}
7900 | 4667 | {3C815617-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | MEADOW LANE | Bank 2 | CB 2107 | PGE\FCR1 | 2017-04-21 16:33:22.4613573 -07:00 | 0143002107 | 083671114 | 12 | 3 | 3 | 1 | 457 | 17.27 | 17.1 | 457 | 17.27 | 17.1 | 630 | 23.81 | 23.57 | 630 | 23.81 | 23.57 | 549 | 20.75 | 20.54 | 549 | 20.75 | 20.54 | 697 | 26.34 | 26.08 | 697 | 26.34 | 26.08 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {87FCC17B-868F-40C2-9ECF-16A4A84EBBD9}
7902 | 4668 | {42C06CD3-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | MEADOW LANE | Bank 3 | CB 2108 | PGE\FCR1 | 2017-04-21 16:34:48.6205711 -07:00 | 0143002108 | 042021102 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 489 | 18.48 | 18.3 | 578 | 21.84 | 21.62 | 549 | 20.75 | 20.54 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 674 | 25.47 | 25.22 | 674 | 25.47 | 25.22 |  |  | FALSE | FALSE | 1322 | 1719 | 1587 | 1984 | {A0D4C6BB-01DF-4B9F-A5CB-1154F302AE0A}
7903 | 4649 | {A4FD41FE-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | BRITTON | Bank 3 | CB 1114 | PGE\MSJ9 | 2017-04-21 11:28:00.4475435 -07:00 | 0836101114 | 042021103 | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | SW 3151 - 8 hour emergency rating of 800 Amps |  | FALSE | FALSE | 1200 | 1200 | 1200 | 1200 | {8F2B5BF3-A9D4-45C1-B825-A5241ABBF8F6}
7904 | 4649 | {A4FD4207-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | BRITTON | Bank 3 | CB 1115 | PGE\MSJ9 | 2017-04-21 11:29:58.5146878 -07:00 | 0836101115 | 042021104 | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 |  |  | FALSE | FALSE | 1200 | 1200 | 1200 | 1200 | {462B7D29-AE36-48C8-BDF4-3181E70E157D}
7905 | 4668 | {42C06CFC-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | MEADOW LANE | Bank 3 | CB 2109 | PGE\FCR1 | 2017-04-21 11:30:23.1906459 -07:00 | 0143002109 | 042021109 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1322 | 1719 | 1587 | 1984 | {F47A631F-0F81-4823-9AFA-288719790659}
7906 | 4669 | {A4FD429D-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | EL PATIO | Bank 2 | CB 1108 | PGE\IRB2 | 2017-05-08 10:45:31.1318291 -07:00 | 0829201108 | 042021110 | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {6ABBACC6-0CF5-48CC-84EA-7BB4395AD246}
7907 | 4668 | {42C06D07-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | MEADOW LANE | Bank 3 | CB 2110 | PGE\FCR1 | 2017-04-21 16:41:24.1852919 -07:00 | 0143002110 | 042021112 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 503 | 19.01 | 18.82 | 639 | 24.15 | 23.91 | 639 | 24.15 | 23.91 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 667 | 25.21 | 24.96 | 667 | 25.21 | 24.96 |  |  | FALSE | FALSE | 1322 | 1719 | 1587 | 1984 | {8915DC2F-EAE1-425D-A891-422EFA43AB43}
7909 | 4671 | {938A62B3-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | TIDEWATER | Bank 1 | CB 2104 | PGE\FCR1 | 2017-04-21 16:48:56.3261281 -07:00 | 0146502104 | 012090401 | 12 | 3 | 3 | 1 | 636 | 24.04 | 23.8 | 636 | 24.04 | 23.8 | 792 | 29.93 | 29.63 | 792 | 29.93 | 29.63 | 691 | 26.12 | 25.86 | 691 | 26.12 | 25.86 | 842 | 31.82 | 31.5 | 842 | 31.82 | 31.5 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {79FA7026-D070-4B0A-8D77-32AF29B9F26B}
7910 | 4671 | {A032095E-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | TIDEWATER | Bank 1 | CB 2105 | PGE\FCR1 | 2017-04-21 13:47:56.4736846 -07:00 | 0146502105 | 012090408 | 12 | 3 | 3 | 1 | 503 | 19.01 | 18.82 | 489 | 18.48 | 18.3 | 578 | 21.84 | 21.62 | 549 | 20.75 | 20.54 | 557 | 21.05 | 20.84 | 557 | 21.05 | 20.84 | 674 | 25.47 | 25.22 | 674 | 25.47 | 25.22 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {B4BFD9FB-BF37-480E-BC80-3FAB73834289}
7911 | 4671 | {A0320975-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | TIDEWATER | Bank 1 | CB 2106 | PGE\FCR1 | 2017-04-21 13:50:35.1083689 -07:00 | 0146502106 | 083421107 | 12 | 3 | 3 | 1 | 745 | 28.16 | 27.88 | 707 | 26.72 | 26.45 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 | 750 | 28.35 | 28.07 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {DEA5E27E-1727-40BF-844B-147694DED636}
7912 | 4672 | {A64AF6DC-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | TIDEWATER | Bank 2 | CB 2107 | PGE\FCR1 | 2017-04-21 13:52:50.9628192 -07:00 | 0146502107 | 012111103 | 12 | 3 | 3 | 1 | 745 | 28.16 | 27.88 | 707 | 26.72 | 26.45 | 800 | 30.23 | 29.93 | 796 | 30.08 | 29.78 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 | 800 | 30.23 | 29.93 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {95A3AB2E-86CA-43CF-BFCC-5213E8238635}
7913 | 4672 | {ACC404D0-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | TIDEWATER | Bank 2 | CB 2108 | PGE\FCR1 | 2017-04-21 13:56:49.0162645 -07:00 | 0146502108 | 012111104 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 732 | 27.66 | 27.38 | 732 | 27.66 | 27.38 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {7AA3C39D-409C-43AB-B8F0-322E03A1B1DD}
7914 | 4672 | {B2EDBAE3-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | TIDEWATER | Bank 2 | CB 2109 | PGE\FCR1 | 2017-04-21 13:59:42.2708661 -07:00 | 0146502109 | 012111106 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 732 | 27.66 | 27.38 | 732 | 27.66 | 27.38 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {976D378C-B752-4E23-A3E4-3A391CF88F76}
7915 | 4672 | {B8F47FFA-78E4-11E5-8C7B-9CB70D532D7F} | DIABLO | TIDEWATER | Bank 2 | CB 2110 | PGE\FCR1 | 2017-04-21 14:01:38.8557349 -07:00 | 0146502110 | 012111108 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 689 | 26.04 | 25.78 | 689 | 26.04 | 25.78 | 627 | 23.7 | 23.46 | 627 | 23.7 | 23.46 | 732 | 27.66 | 27.38 | 732 | 27.66 | 27.38 |  |  | FALSE | FALSE | 1984 | 2579 | 2381 | 2976 | {82D7C65A-765B-4887-ABEC-B0F732DAF69B}
7916 | 4675 | {ACCC4FA5-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | WYANDOTTE | Bank 1 | CB 1102 | PGE\CTD7 | 2017-04-21 17:17:37.7189022 -07:00 | 1029101102 | 024120401 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {FF73163F-85C1-482D-B8EF-00CFCBE8E36B}
7917 | 4675 | {ACCC4FC3-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | WYANDOTTE | Bank 1 | CB 1103 | PGE\CTD7 | 2017-04-21 14:47:37.4846241 -07:00 | 1029101103 | 024120402 | 8 | 4 | 4 | 2 | 100 | 2.18 | 2.16 | 95 | 2.07 | 2.05 | 100 | 2.18 | 2.16 | 95 | 2.07 | 2.05 | 100 | 2.18 | 2.16 | 95 | 2.07 | 2.05 | 100 | 2.18 | 2.16 | 95 | 2.07 | 2.05 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {D32B5EA1-656B-4E44-BBA3-9BF9EFABE94F}
7918 | 4679 | {ACCC4FF3-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | WYANDOTTE | Bank 2 | CB 1105 | PGE\CTD7 | 2017-04-21 17:14:59.4850593 -07:00 | 1029101105 | 024120403 | 8 | 3 | 3 | 1 | 290 | 6.33 | 6.27 | 290 | 6.33 | 6.27 | 290 | 6.33 | 6.27 | 290 | 6.33 | 6.27 | 290 | 6.33 | 6.27 | 290 | 6.33 | 6.27 | 290 | 6.33 | 6.27 | 290 | 6.33 | 6.27 | Transferred info from old capability sheets. Did not field verify. Actual Phase MTT is 350 Amps. 350 Amps is not a choice on this sheet, so used IAC-53 w/ MTT of 350amps = 291.67 Limit. |  | FALSE | FALSE | 1370 | 1781 | 1644 | 2055 | {8B388E4B-B6DC-46A5-8D1A-8D7CD78F799D}
7919 | 4679 | {B2D173F2-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | WYANDOTTE | Bank 2 | CB 1106 | PGE\CTD7 | 2017-04-21 17:14:30.2812977 -07:00 | 1029101106 | 024120404 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 1370 | 1781 | 1644 | 2055 | {F2C62FCB-A59A-4D30-8681-7C45891BA357}
7920 | 4670 | {1453D299-0E49-11E6-95F2-D4BED91EFF1A} | DIABLO | SINCLAIR | BANK 1 | CB 401 (Non-SCADA) | PGE\FCR1 | 2017-04-21 16:47:12.2079764 -07:00 | 014150401 | 024161103 | 4 | 3 | 3 | 1 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 429 | 3.25 | 3.22 | 429 | 3.25 | 3.22 | 396 | 3 | 2.97 | 396 | 3 | 2.97 | 450 | 3.41 | 3.38 | 450 | 3.41 | 3.38 |  |  | FALSE | FALSE | 330 | 429 | 396 | 495 | {41978B19-2C8B-4496-8281-DB2D0BF43FAC}
7921 | 4683 | {B2D17436-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | WYANDOTTE | Bank 3 | CB 1107 | PGE\CTD7 | 2017-04-21 16:59:53.7160410 -07:00 | 1029101107 | 024130403 | 8 | 3 | 3 | 1 | 573 | 12.51 | 12.38 | 573 | 12.51 | 12.38 | 728 | 15.89 | 15.73 | 728 | 15.89 | 15.73 | 634 | 13.84 | 13.7 | 634 | 13.84 | 13.7 | 768 | 16.76 | 16.59 | 768 | 16.76 | 16.59 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 2923 | {97AEE908-547E-4BD7-8924-713704A977E0}
7922 | 4683 | {B2D17469-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | WYANDOTTE | Bank 3 | CB 1109 | PGE\CTD7 | 2017-04-21 17:13:04.8228543 -07:00 | 1029101109 | 024130404 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 2923 | {545A57E0-F157-487B-8AA6-66DD5228CCEC}
7923 | 4683 | {B2D174B1-0B21-11E6-9D37-D4BED91EFF1A} | NORTH VALLEY | WYANDOTTE | Bank 3 | CB 1110 | PGE\CTD7 | 2017-04-21 17:10:29.4906672 -07:00 | 1029101110 | 024130402 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Transferred info from old capability sheets. Did not field verify. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 2923 | {9D9DAF9A-800D-4D96-AB75-A74B0D4C7B80}
7925 | 4684 | {7B288D10-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | TUDOR | Bank 1 | CB 1101 | PGE\HSA1 | 2017-04-24 10:37:18.9560411 -07:00 | 153711101 | 083481102 | 8 | 3 | 3 | 1 | 229 | 5 | 4.95 | 229 | 5 | 4.95 | 297 | 6.48 | 6.42 | 297 | 6.48 | 6.42 | 274 | 5.98 | 5.92 | 274 | 5.98 | 5.92 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 229 | 297 | 274 | 343 | {61B3B3C4-06C9-4FBF-955C-E087E2F36D5F}
7927 | 4662 | {A4FD43D1-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LAWRENCE | Bank 1 | CB 1102 | PGE\IRB2 | 2017-04-24 07:04:22.8665382 -07:00 | 0834201102 | 083481103 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2291 | 2978 | 2749 | 3437 | {0B5B45EE-C93B-4D00-AD18-87CACA3DC0D7}
7928 | 4662 | {A4FD43DA-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LAWRENCE | Bank 1 | CB 1103 | PGE\IRB2 | 2017-04-24 07:12:04.7602206 -07:00 | 0834201103 | 083481104 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2291 | 2978 | 2749 | 3437 | {57304C00-0A9A-4BAE-B2FE-4C6671600844}
7929 | 4662 | {A4FD43E3-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LAWRENCE | Bank 1 | CB 1104 | PGE\IRB2 | 2017-04-24 07:11:38.9105235 -07:00 | 0834201104 | 083481105 | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2291 | 2978 | 2749 | 3437 | {FFF6C4F6-1836-4879-BA32-C075F5523898}
7930 | 4662 | {A4FD43FB-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | LAWRENCE | Bank 1 | CB 1105 | PGE\IRB2 | 2017-04-24 07:11:04.4806614 -07:00 | 0834201105 | 083481106 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2291 | 2978 | 2749 | 3437 | {6C00AA2E-E2DB-4608-9B47-FC8F7E96F44F}
7931 | 1056 | {3D0767CA-2F5B-11E6-B38D-D4BED91EFF1A} | SIERRA | LINCOLN | Bank 2 | CB 2109 | PGE\SDK6 | 2017-04-24 09:17:08.8009263 -07:00 | 1537002109 | 083481107 | 12 | 3 | 3 | 1 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 1190 | 1547 | 1428 | 1688 | {5AB4F327-CD71-4EDD-8831-BFB54CDA6BBD}
7932 | 4684 | {7B288D19-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | TUDOR | Bank 1 | CB 1102 | PGE\HSA1 | 2017-04-24 10:34:36.0461622 -07:00 | 153711102 | 083481108 | 8 | 3 | 3 | 1 | 229 | 5 | 4.95 | 229 | 5 | 4.95 | 297 | 6.48 | 6.42 | 297 | 6.48 | 6.42 | 274 | 5.98 | 5.92 | 274 | 5.98 | 5.92 | 333 | 7.27 | 7.2 | 333 | 7.27 | 7.2 |  |  | FALSE | FALSE | 229 | 297 | 274 | 343 | {38271B20-70AF-4FE6-BFC8-9D90238D128F}
7941 | 4687 | {946B52AF-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | CATLETT | Bank 1 | CB 1101 | PGE\TEJ2 | 2017-05-17 12:46:13.2493343 -07:00 | 153761101 | 083481109 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 467 | 10.19 | 10.09 | 456 | 9.95 | 9.85 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 467 | 10.19 | 10.09 | 456 | 9.95 | 9.85 |  |  | TRUE | FALSE | 429 | 558 | 515 | 644 | {FEEF28F2-2061-4DDF-A8F6-730E25AC570A}
7944 | 4687 | {946B52B8-0B22-11E6-9D37-D4BED91EFF1A} | SIERRA | CATLETT | Bank 1 | CB 1102 | PGE\TEJ2 | 2017-05-17 12:45:49.9574892 -07:00 | 153761102 | 083481110 | 8 | 3 | 3 | 1 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 467 | 10.19 | 10.09 | 456 | 9.95 | 9.85 | 400 | 8.73 | 8.64 | 380 | 8.29 | 8.21 | 467 | 10.19 | 10.09 | 456 | 9.95 | 9.85 |  |  | FALSE | FALSE | 429 | 558 | 515 | 644 | {4D0AB42D-60B1-4465-97EC-91779FA9BE6D}
7947 | 4691 | {634A363A-0B41-11E6-9D37-D4BED91EFF1A} | SIERRA | CATLETT | BANK 2 | CB 1105 | PGE\HSA1 | 2017-04-24 13:21:33.3004540 -07:00 | 1537601105 | 083481111 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Alternate Phase Min Trip = 440A as a short term bypass plan (If loading allows) for downstream Recloser 1232. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2000 | {E510ED6E-CBA4-42B6-ACF3-78DE6FC1C00A}
7951 | 4693 | {812C063B-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WHEATLAND | Bank 1 | CB 1101 | PGE\HSA1 | 2017-04-24 14:25:38.3061462 -07:00 | 1528101101 | 083481112 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | The Selector #2 has Phase Min setting 360A for LR bypass if the loading allows. | Reg/HS Fuse | TRUE | FALSE | 609 | 721 | 721 | 721 | {F91A69BF-A2CB-49A8-BACC-B5483A8D7929}
7953 | 4693 | {812C0644-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WHEATLAND | Bank 1 | CB 1102 | PGE\HSA1 | 2017-04-24 14:32:37.6652895 -07:00 | 1528101102 | 083481113 | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | The setting Group# 2 has Phase min trip=360A. Use this setting per LR bypass instructions if the loading allows. |  | TRUE | FALSE | 609 | 721 | 721 | 721 | {4F6534D8-A3B3-4959-8713-504D45394C8B}
7954 | 4696 | {872F7C20-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WHEATLAND | Bank 2 | CB 1104 | PGE\HSA1 | 2017-04-24 15:08:18.1491260 -07:00 | 1528101104 | 252761116 | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {4F75300B-9C45-4D6E-950D-50B4A6D28B12}
7955 | 4696 | {872F7C4C-0B22-11E6-9D37-D4BED91EFF1A} | SACRAMENTO | WHEATLAND | Bank 2 | CB 1105 | PGE\HSA1 | 2017-04-24 15:08:27.4796602 -07:00 | 1528101105 | 182402107 | 8 | 3 | 3 | 1 | 345 | 7.53 | 7.45 | 327 | 7.14 | 7.07 | 386 | 8.42 | 8.34 | 366 | 7.99 | 7.91 | 443 | 9.67 | 9.57 | 420 | 9.17 | 9.08 | 473 | 10.32 | 10.22 | 449 | 9.8 | 9.7 | The Selector #2 (LR BYPASS) setting for Phase Min Trip is 360A per old capability sheet. |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {2ACB7A7F-3FF1-47EF-8D14-BAE7F4315AF8}
7960 | 4698 | {C5114135-671D-11E5-80CA-005056A729E5} | FRESNO | KERCKHOFF | Bank 4 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\KRBk | 2017-04-26 12:59:56.9046604 -07:00 | 2525601101 | 183011101 | 8 | 2 | 2 | 1 | 90 | 1.96 | 1.94 | 90 | 1.96 | 1.94 | 90 | 1.96 | 1.94 | 90 | 1.96 | 1.94 | 90 | 1.96 | 1.94 | 90 | 1.96 | 1.94 | 90 | 1.96 | 1.94 | 90 | 1.96 | 1.94 |  |  | FALSE | FALSE | 90 | 90 | 90 | 90 | {31AD395E-7DF0-45E3-8C82-105A3B34708C}
7963 | 4704 | {B73828BE-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WHISMAN | Bank 1 | CB 1101 | PGE\MSJ9 | 2017-04-26 12:25:39.5534735 -07:00 | 0836301101 | 183011102 | 7 | 3 | 3 | 2 | 492 | 10.63 | 10.52 | 492 | 10.63 | 10.52 | 554 | 11.97 | 11.85 | 554 | 11.97 | 11.85 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 598 | 12.92 | 12.79 | 598 | 12.92 | 12.79 | New Breaker on 2-26-2010 Relay Settings (SEL-351) Phase: Tap = 3.0 (720 A), TD = 2, Curve = VI, Inst = 6000 A CT Ratio: 1200:5 Ground: Tap = 0.75 (180 A), TD = 3, Curve = VI, Inst = 6000 A |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {D330487B-23CB-43B6-90F7-4C89793B4D43}
7968 | 4704 | {B73828C7-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WHISMAN | Bank 1 | CB 1102 | PGE\MSJ9 | 2017-04-26 13:22:45.4729553 -07:00 | 0836301102 | 182131101 | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | Relay Minimum Phase: 720 A Tap: 6 Lever: 2 Pha Inst: 6000 A To Operate Ground: 180 A Tap: 1.5 Lever: 3 Gnd Inst: None CT Ratio: 600:5 |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {F55FBEF4-88FE-4E37-BE93-A8CAB1333B6E}
7969 | 4704 | {B73828D0-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WHISMAN | Bank 1 | CB 1103 | PGE\MSJ9 | 2017-04-26 14:19:27.4771772 -07:00 | 0836301103 | 182131102 | 7 | 3 | 3 | 2 | 454 | 9.81 | 9.71 | 454 | 9.81 | 9.71 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 468 | 10.11 | 10.01 | 468 | 10.11 | 10.01 | 566 | 12.22 | 12.1 | 566 | 12.22 | 12.1 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {87AF2334-3E40-4B26-B184-AA7C5736F1BA}
7973 | 4704 | {B73828E0-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WHISMAN | Bank 1 | CB 1104 | PGE\MSJ9 | 2017-04-26 14:50:59.6063636 -07:00 | 0836301104 | 251511101 | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 514 | 11.1 | 10.99 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 558 | 12.05 | 11.93 | 530 | 11.45 | 11.34 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | Reclosing relay is normally cut-out Relay Minimum Phase: 720 A Tap: 6 Lever: 2.5 Pha Inst: 6600 A To Operate Ground: 180 A Tap: 1.5 Lever: 2 Gnd Inst: None CT Ratio: 600:5 |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {77C163C9-57BC-49EC-9B83-64C03B39CA95}
7974 | 4680 | {AB2669BB-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | MOUNTAIN VIEW | Bank 2 | CB 1102 | PGE\MTTA | 2017-04-27 18:01:49.7591730 -07:00 | 0820301102 | 182852203 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1832 | 2382 | 2000 | 2400 | {A7A569C2-D174-4F45-9460-806F144DE577}
7975 | 4680 | {AB2669E7-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | MOUNTAIN VIEW | Bank 2 | CB 1103 | PGE\MTTA | 2017-04-27 19:05:04.1412530 -07:00 | 0820301103 | 022101112 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 665 | 14.51 | 14.36 | 665 | 14.51 | 14.36 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 674 | 14.71 | 14.56 | 674 | 14.71 | 14.56 |  |  | FALSE | FALSE | 1832 | 2382 | 2000 | 2400 | {1131D0D2-FC93-4708-A29A-BF45D4C21718}
7976 | 4680 | {AB2669F0-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | MOUNTAIN VIEW | Bank 2 | CB 1104 | PGE\MTTA | 2017-04-27 19:12:46.0823082 -07:00 | 0820301104 | 255361112 | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 665 | 14.51 | 14.36 | 665 | 14.51 | 14.36 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 674 | 14.71 | 14.56 | 674 | 14.71 | 14.56 |  |  | FALSE | FALSE | 1832 | 2382 | 2000 | 2400 | {B39CB836-FF9B-4186-942C-55A47266FB78}
7977 | 4680 | {AB266A07-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | MOUNTAIN VIEW | Bank 2 | CB 1105 | PGE\MTTA | 2017-04-28 07:14:38.3398163 -07:00 | 0820301105 |  | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1832 | 2382 | 2000 | 2400 | {606388DB-1159-4F32-A264-0933EB3B0EA5}
7978 | 4708 | {B73828EC-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WHISMAN | Bank 2 | CB 1105 | PGE\MSJ9 | 2017-04-28 09:53:18.0813514 -07:00 | 0836301105 |  | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | Relay Minimum Phase: 720 A Tap: 6 Lever: 2 Pha Inst: 6000 A To Operate Ground: 180 A Tap: 1.5 Lever: 3 Gnd Inst: None CT Ratio: 600:5 |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {F3CDDD12-C92D-4863-81C7-7A22756D93CC}
7979 | 4708 | {B73828F5-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WHISMAN | Bank 2 | CB 1106 | PGE\MSJ9 | 2017-04-28 09:56:22.0400890 -07:00 | 0836301106 |  | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | New breaker on 5-18-2010 Relay Settings (SEL-351) Phase: Tap = 3.0 (720 A), TD = 3, Curve = VI, Inst = 6000 A CT Ratio: 1200:5 Ground: Tap = 0.75 (180 A), TD = 3, Curve = VI, Inst = none |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {6F8EA3E0-B5C0-4335-97F5-AC51590D3067}
7980 | 4708 | {B7382905-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WHISMAN | Bank 2 | CB 1107 | PGE\MSJ9 | 2017-04-28 10:02:25.9794877 -07:00 | 0836301107 |  | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | Relay Minimum Phase: 720 A Tap: 6 Lever: 3 Pha Inst: 6000 A To Operate Ground: 180 A Tap: 1.5 Lever: 3 Gnd Inst: None CT Ratio: 600:5 |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {C4727457-F1C5-40C8-B690-C949E345A8AC}
7981 | 4708 | {B738290E-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WHISMAN | Bank 2 | CB 1108 | PGE\MSJ9 | 2017-04-28 10:27:15.8393383 -07:00 | 0836301108 |  | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | Relay Minimum Phase: 720 A Tap: 6 Lever: 3 Pha Inst: 5400 A To Operate Ground: 180 A Tap: 1.5 Lever: 4 Gnd Inst: None CT Ratio: 600:5 |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {08A7A859-F764-494F-AA9C-91E9454AA9B4}
7985 | 2721 | {B00CC465-DA91-11E5-BF25-2016D89D35F7} | KERN | TAFT | Bank 4 | CB 1102 | PGE\JCS9 | 2017-04-28 14:29:37.5222090 -07:00 | 2520801102 |  | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | F60 with SEL 351 backup. |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {B287488B-F1D5-4F2F-804F-9BE01FD6F67B}
7987 | 1162 | {2717D5BF-A5BE-11E5-A1F0-D4BED91EFF1A} | FRESNO | GUERNSEY | Bank 2 | CB 1105 | PGE\JJV7 | 2017-05-01 09:01:16.8081070 -07:00 | 2526601105 |  | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | Solar Feeder |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {DD9FA6F4-05C2-42EC-BC30-F3E32D568B2A}
7988 | 3876 | {310ABD2A-6000-11E6-9BE4-80000BC6CD8D} | KERN | LAKEVIEW | BANK 2 | CB 1106 | PGE\JJV7 | 2017-05-01 09:07:48.4224379 -07:00 | 253411106 |  | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | OLD 1103 |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {A49E8388-A63C-4263-9912-6C3CA905DF4B}
7990 | 3876 | {310ABD34-6000-11E6-9BE4-80000BC6CD8D} | KERN | LAKEVIEW | BANK 2 | CB 1107 | PGE\JJV7 | 2017-05-01 10:07:10.3453351 -07:00 | 253411107 |  | 8 | 4 | 4 | 2 | 515 | 11.24 | 11.13 | 489 | 10.67 | 10.56 | 578 | 12.61 | 12.48 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 711 | 15.52 | 15.36 | 675 | 14.73 | 14.58 | Old 1101 |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {9337DB4D-0C66-4543-8E3D-C2527E01C6E3}
7991 | 1141 | {BE51AB59-0B42-11E6-9D37-D4BED91EFF1A} | FRESNO | CORCORAN | Bank 4 | CB 1101 | PGE\VxLa | 2017-05-02 13:05:49.6961725 -07:00 | 2521701101 |  | 8 | 3 | 3 | 1 | 578 | 12.61 | 12.48 | 578 | 12.61 | 12.48 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {F81DDDA1-31E0-482D-B6F7-8FBA807BC7A6}
7992 | 4703 | {B7382944-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WHISMAN | Bank 3 | CB 1109 | PGE\RPBK | 2017-05-02 09:17:28.6852483 -07:00 | 0836301109 |  | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | Relay min: Phase=720A, Tap=6, Pha Inst=5760A GND=180, Tap=1.5, Lever=0.4, GND Inst=5580A |  | FALSE | FALSE | 2083 | 2640 | 2200 | 2640 | {924C9836-5E19-4BB5-8483-4E2BDB903B25}
7993 | 4703 | {B738294D-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WHISMAN | Bank 3 | CB 1110 | PGE\RPBK | 2017-05-02 09:26:48.3639483 -07:00 | 0836301110 |  | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | Relay Min: Phase=720A, Tap=6, Lever=4, Pha Inst=6000A GND=180A, Tap=1.6, Lever=20, GND Inst=4800A |  | FALSE | FALSE | 2083 | 2640 | 2200 | 2640 | {5BADC103-3936-4A2D-B1B2-816D6B0864CB}
7994 | 4703 | {B738295D-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WHISMAN | Bank 3 | CB 1111 | PGE\RPBK | 2017-05-02 09:39:29.0589563 -07:00 | 0836301111 |  | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | Relay Min: Phase=720A, Tap=6, Lever=3, Phase Inst=6000A GND=180A, Tap=1.5, Lever=3, GND Inst=4800A |  | FALSE | FALSE | 2083 | 2640 | 2200 | 2640 | {0D6084AC-D89B-4864-A640-618FB254DC3D}
7995 | 4703 | {1D51DF22-FDBE-11E5-9D37-D4BED91EFF1A} | DE ANZA | WHISMAN | Bank 3 | CB 1112 (Non-SCADA) | PGE\RPBK | 2017-05-02 09:55:17.9464147 -07:00 | 0836301112 |  | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | Realy Min: Phase=720A, Tap=3, Lever=3, Phase Inst=6000A GND=180A, Tap=0.75, Lever=4, GND Inst=6000A 1112 installed on July 2014. Bank 3 replaced with 45KVA on July 2014 |  | FALSE | FALSE | 2083 | 2640 | 2200 | 2640 | {6A15A03B-9F55-4822-9AEE-9231CE38A77C}
7996 | 1141 | {C5627D97-0B42-11E6-9D37-D4BED91EFF1A} | FRESNO | CORCORAN | Bank 4 | CB 1102 | PGE\VxLa | 2017-05-02 13:00:56.3793319 -07:00 | 2521701102 |  | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {1AF49A80-1433-4955-AA02-2F8353193DC2}
7997 | 1140 | {C5627D9D-0B42-11E6-9D37-D4BED91EFF1A} | FRESNO | CORCORAN | Bank 3 | CB 1117 | PGE\VxLa | 2017-05-02 13:10:18.2709373 -07:00 | 2521701117 |  | 8 | 3 | 3 | 1 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {31295FA4-0F74-4507-A184-11C79DEB3E8C}
7999 | 4677 | {AB266962-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | MOUNTAIN VIEW | Bank 1 | CB 1106 | PGE\MTTA | 2017-05-02 15:58:53.6468098 -07:00 | 0820301106 |  | 8 | 3 | 3 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {0870F2BE-AE41-4DAA-953B-E27B1438A59A}
8000 | 4677 | {AB266979-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | MOUNTAIN VIEW | Bank 1 | CB 1107 | PGE\MTTA | 2017-05-02 16:01:52.4319778 -07:00 | 0820301107 |  | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {B834359B-FF9C-46E8-9300-EE85F7F09C93}
8001 | 4677 | {AB26698A-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | MOUNTAIN VIEW | Bank 1 | CB 1108 | PGE\MTTA | 2017-05-02 16:01:35.8639282 -07:00 | 0820301108 |  | 8 | 3 | 3 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {89F4D935-FBF2-4949-9703-A24A87D75094}
8002 | 4677 | {AB2669A8-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | MOUNTAIN VIEW | Bank 1 | CB 1109 | PGE\MTTA | 2017-05-02 16:03:48.3771234 -07:00 | 0820301109 |  | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {28F46546-6E9F-4BE5-B3D3-82F94A1C2312}
8003 | 4681 | {AB266A36-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | MOUNTAIN VIEW | Bank 3 | CB 1110 | PGE\MTTA | 2017-05-02 16:08:10.6109706 -07:00 | 0820301110 |  | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1945 | 2380 | 2000 | 2400 | {677A2139-942E-4D8C-9783-34B1882946A8}
8004 | 4681 | {AB266A3F-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | MOUNTAIN VIEW | Bank 3 | CB 1111 | PGE\MTTA | 2017-05-02 16:09:58.9429258 -07:00 | 0820301111 |  | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1945 | 2380 | 2000 | 2400 | {12BB784D-1B91-4328-8505-56F3577E1434}
8005 | 4681 | {AB266A4F-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | MOUNTAIN VIEW | Bank 3 | CB 1112 | PGE\MTTA | 2017-05-02 16:12:01.9084314 -07:00 | 0820301112 |  | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1945 | 2380 | 2000 | 2400 | {96F4A8E8-6D8F-4EDE-AA44-E7C01B7648EF}
8006 | 4681 | {AB266A58-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | MOUNTAIN VIEW | Bank 3 | CB 1113 | PGE\MTTA | 2017-05-02 16:14:51.6451354 -07:00 | 0820301113 |  | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 665 | 14.51 | 14.36 | 665 | 14.51 | 14.36 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 674 | 14.71 | 14.56 | 674 | 14.71 | 14.56 |  |  | FALSE | FALSE | 1945 | 2380 | 2000 | 2400 | {DE41D610-440D-4E8B-BC52-A9CB2339A486}
8007 | 4681 | {AB266A6F-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | MOUNTAIN VIEW | Bank 3 | CB 1114 | PGE\MTTA | 2017-05-02 16:22:05.7217946 -07:00 | 0820301114 |  | 8 | 3 | 3 | 2 | 545 | 11.89 | 11.77 | 517 | 11.28 | 11.17 | 600 | 13.09 | 12.96 | 583 | 12.72 | 12.59 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1945 | 2380 | 2000 | 2400 | {A310F1FF-FA73-486F-B366-3A89EC19057A}
8009 | 4500 | {C8A81F7C-1A57-11E7-8137-005056AE4E7D} | SAN FRANCISCO | SF E | Bank 2 | CB 405/3 (Non-SCADA) | PGE\DMAL | 2017-05-02 17:13:56.6412544 -07:00 |  |  | 3 | 3 | 3 | 2 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | E405/E410 share 1200amp OCB |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2185 | {00000000-0000-0000-0000-000000000000}
8010 | 4500 | {C8A81F7F-1A57-11E7-8137-005056AE4E7D} | SAN FRANCISCO | SF E | Bank 2 | CB 410/3 (Non-SCADA) | PGE\DMAL | 2017-05-02 17:17:47.6348965 -07:00 |  |  | 3 | 3 | 3 | 2 | 278 | 2 | 1.98 | 278 | 2 | 1.98 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 286 | 2.06 | 2.04 | 286 | 2.06 | 2.04 | 309 | 2.23 | 2.21 | 309 | 2.23 | 2.21 | E405/E410 share 1200amp OCB |  | FALSE | FALSE | 1457 | 1894 | 1748 | 2185 | {00000000-0000-0000-0000-000000000000}
8011 | 4711 | {E14FD589-BBFA-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kV Buses | 12KV CB D-E/12 | PGE\DMAL | 2017-05-02 17:49:34.4907661 -07:00 |  |  | 7 | 3 | 3 | 2 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {AD470083-5229-4722-ABF3-9412B490FDA7}
8012 | 4711 | {938E2908-BBFD-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kV Buses | 12KV CB E-F/12 | PGE\DMAL | 2017-05-02 17:48:37.4560693 -07:00 |  |  | 7 | 3 | 3 | 2 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {261A740F-678A-4054-A8EB-A1673C6F3C2C}
8013 | 4711 | {A29C1BE5-BBFD-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kV Buses | 12KV CB E-F/22 | PGE\DMAL | 2017-05-02 17:49:06.6598309 -07:00 |  |  | 7 | 3 | 3 | 2 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {1BF599D9-2859-4BFC-B6FA-B328C47A707D}
8015 | 4711 | {78C38376-BBFC-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | MISSION (SF X) | 12kV Buses | 12KV CB D-E/22 | PGE\DMAL | 2017-05-16 11:20:38.1958592 -07:00 |  |  | 7 | 3 | 3 | 2 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 | 4000 | 86.39 | 85.53 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {B578ECAD-ADFE-4DB8-9292-95A5129BB475}
8016 | 4713 | {13DD3C7D-B7F8-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | SF G | Bank 2 | CB SS (4KV AUX BUS TO 4KV MAIN BUS) | PGE\DMAL | 2017-05-04 12:53:16.4646591 -07:00 |  |  | 3 | 3 | 3 | 2 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 | 1200 | 8.65 | 8.56 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {93182C10-C682-4259-9F4F-4E73492756C7}
8017 | 4525 | {5D0FD8C3-B7F7-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | SF G | 12kv Bus 1 (GX-1, GX-2, GX-3, GX-4, GX-5) | CB STA SERV | PGE\DMAL | 2017-05-02 18:10:11.5633555 -07:00 |  |  | 7 | 3 | 3 | 2 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {00000000-0000-0000-0000-000000000000}
8018 | 4714 | {A28D5CCB-B8B9-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | SF L | 12kv Bus 1 (HL-1, HL-2, HL-3, HL-4) | CB 1101 | PGE\DMAL | 2017-05-02 19:09:45.6621463 -07:00 |  |  | 7 | 3 | 3 | 2 | 383 | 8.27 | 8.19 | 383 | 8.27 | 8.19 | 429 | 9.27 | 9.18 | 429 | 9.27 | 9.18 | 394 | 8.51 | 8.42 | 394 | 8.51 | 8.42 | 442 | 9.55 | 9.45 | 442 | 9.55 | 9.45 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {FBE84E17-2EDC-47AE-9097-0DEE0492F04E}
8019 | 4714 | {BCCED4A0-B8B9-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | SF L | 12kv Bus 1 (HL-1, HL-2, HL-3, HL-4) | CB 1103 | PGE\DMAL | 2017-05-02 19:43:45.1673668 -07:00 |  |  | 7 | 3 | 3 | 2 | 517 | 11.17 | 11.06 | 517 | 11.17 | 11.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 527 | 11.38 | 11.27 | 527 | 11.38 | 11.27 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | Branch 19688 - Limited by 500EPRcu - 3ELC (462/538/471/549) - Alternate source to MUNI west portal/laguna honda stations. Branch 19690 - Limited by 750EPRcu - 4ELC (517/604/527/616). |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {C5321B38-6DCD-43C4-B66B-8BF696704B8A}
8020 | 4715 | {B1458FF5-B8B9-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | SF L | 12kv Bus 2 | CB 1102 | PGE\DMAL | 2017-05-02 19:49:14.6769034 -07:00 |  |  | 7 | 3 | 3 | 2 | 445 | 9.61 | 9.51 | 445 | 9.61 | 9.51 | 494 | 10.67 | 10.56 | 494 | 10.67 | 10.56 | 458 | 9.89 | 9.79 | 458 | 9.89 | 9.79 | 509 | 10.99 | 10.88 | 509 | 10.99 | 10.88 | Normal source to MUNI West Portal/Laguna Honda stations |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {CF372E0C-111A-4C14-8090-BE0217E1A043}
8021 | 4526 | {A23BBA64-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF G | 12kv Bus 2 | CB 1102 | PGE\DMAL | 2017-05-03 14:58:04.7306054 -07:00 | 022091102 |  | 7 | 3 | 3 | 2 | 543 | 11.73 | 11.61 | 543 | 11.73 | 11.61 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 554 | 11.97 | 11.85 | 554 | 11.97 | 11.85 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {BF3003E5-FC92-448D-BBAA-602EC657EBA7}
8022 | 4525 | {A23BBA5E-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF G | 12kv Bus 1 (GX-1, GX-2, GX-3, GX-4, GX-5) | CB 1101 | PGE\DMAL | 2017-05-03 11:52:11.0076554 -07:00 | 022091101 |  | 7 | 3 | 3 | 2 | 573 | 12.38 | 12.26 | 573 | 12.38 | 12.26 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 584 | 12.61 | 12.48 | 584 | 12.61 | 12.48 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | ATS - Alternate source to MUNI Richmond Station (N.O. switch 152H). Normal source Y1138 (N.C switch 252H). |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {43C7F32D-864D-4F01-BF80-D89D35940F81}
8023 | 4669 | {A4FD4286-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | EL PATIO | Bank 2 | CB 1107 | PGE\IRB2 | 2017-05-08 11:30:22.7674022 -07:00 | 0829201107 |  | 7 | 3 | 3 | 2 | 582 | 12.57 | 12.44 | 552 | 11.92 | 11.8 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {1D0B1CF2-5C89-469F-ACAC-EB5642F7E15A}
8024 | 4669 | {A4FD42A0-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | EL PATIO | Bank 2 | CB 1109 | PGE\IRB2 | 2017-05-08 12:19:18.6007324 -07:00 | 0829201109 |  | 7 | 3 | 3 | 2 | 564 | 12.18 | 12.06 | 564 | 12.18 | 12.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {67540F6D-AAE4-4200-B549-C164CCBF07E4}
8025 | 4669 | {A4FD42CC-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | EL PATIO | Bank 2 | CB 1110 | PGE\IRB2 | 2017-05-08 12:19:45.8395546 -07:00 | 0829201110 |  | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {0BEED1B9-2AAB-4CDD-B9F6-63AEDD57CCA0}
8026 | 2421 | {D4A21088-26B9-11E7-8139-005056AE4E7D} | YOSEMITE | INDIAN FLAT | Bank 1 (Non SCADA) | CB 1101 (Non-SCADA) | PGE\JJV7 | 2017-05-04 09:31:03.8461440 -07:00 |  |  | 8 | 3 | 3 | 1 | 190 | 4.15 | 4.11 | 190 | 4.15 | 4.11 | 190 | 4.15 | 4.11 | 190 | 4.15 | 4.11 | 190 | 4.15 | 4.11 | 190 | 4.15 | 4.11 | 190 | 4.15 | 4.11 | 190 | 4.15 | 4.11 |  |  | FALSE | FALSE | 197 | 257 | 237 | 296 | {0BAFC7CA-82AD-402C-A42A-CCFBE48704EB}
8027 | 4712 | {9A1BD0F6-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF G | Bank 1 | CB 401 | PGE\DMAL | 2017-05-04 11:41:14.5107462 -07:00 | 02209401 |  | 3 | 3 | 3 | 2 | 350 | 2.52 | 2.49 | 350 | 2.52 | 2.49 | 378 | 2.72 | 2.69 | 378 | 2.72 | 2.69 | 361 | 2.6 | 2.57 | 361 | 2.6 | 2.57 | 389 | 2.8 | 2.77 | 389 | 2.8 | 2.77 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {E5DA4D46-3C0F-42D2-AB20-9B482830D80E}
8028 | 4712 | {9A1BD0F9-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF G | Bank 1 | CB 403 | PGE\DMAL | 2017-05-04 11:47:24.1130538 -07:00 | 02209403 |  | 3 | 3 | 3 | 2 | 350 | 2.52 | 2.49 | 350 | 2.52 | 2.49 | 378 | 2.72 | 2.69 | 378 | 2.72 | 2.69 | 361 | 2.6 | 2.57 | 361 | 2.6 | 2.57 | 389 | 2.8 | 2.77 | 389 | 2.8 | 2.77 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {8B440FD3-74AF-4547-B89E-8BAB28E19635}
8029 | 4729 | {00C22869-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | TRIMBLE | Bank 1 | CB 1101 | PGE\ALWK | 2017-05-04 11:51:33.3278463 -07:00 | 0838001101 |  | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {6D451FAB-A218-4D97-834E-BD2C81456A98}
8030 | 4712 | {9A1BD0FC-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF G | Bank 1 | CB 405 | PGE\DMAL | 2017-05-04 12:51:15.6247353 -07:00 | 02209405 |  | 3 | 3 | 3 | 2 | 350 | 2.52 | 2.49 | 350 | 2.52 | 2.49 | 378 | 2.72 | 2.69 | 378 | 2.72 | 2.69 | 361 | 2.6 | 2.57 | 361 | 2.6 | 2.57 | 389 | 2.8 | 2.77 | 389 | 2.8 | 2.77 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {7BFD8251-D24F-4A3E-8C50-0D3FB41A937A}
8031 | 4729 | {00C22880-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | TRIMBLE | Bank 1 | CB 1103 | PGE\ALWK | 2017-05-04 11:59:49.1833818 -07:00 | 0838001103 |  | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {4147DD89-1194-4496-AF9E-AB9E1491ECD3}
8032 | 4712 | {9A1BD0FF-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF G | Bank 1 | CB 407 | PGE\DMAL | 2017-05-04 12:50:58.5892077 -07:00 | 02209407 |  | 3 | 3 | 3 | 2 | 350 | 2.52 | 2.49 | 350 | 2.52 | 2.49 | 378 | 2.72 | 2.69 | 378 | 2.72 | 2.69 | 361 | 2.6 | 2.57 | 361 | 2.6 | 2.57 | 389 | 2.8 | 2.77 | 389 | 2.8 | 2.77 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {EA916F32-040E-4BA7-8181-EE11DAE37038}
8033 | 4712 | {9A1BD102-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF G | Bank 1 | CB 409 | PGE\DMAL | 2017-05-04 12:50:42.3024945 -07:00 | 02209409 |  | 3 | 3 | 3 | 2 | 350 | 2.52 | 2.49 | 350 | 2.52 | 2.49 | 378 | 2.72 | 2.69 | 378 | 2.72 | 2.69 | 361 | 2.6 | 2.57 | 361 | 2.6 | 2.57 | 389 | 2.8 | 2.77 | 389 | 2.8 | 2.77 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {A061C58B-0BF3-4196-89C2-CB996F8CEA69}
8034 | 4729 | {00C22890-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | TRIMBLE | Bank 1 | CB 1104 | PGE\ALWK | 2017-05-04 12:05:59.2536984 -07:00 | 0838001104 |  | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {3DB421F0-A458-4F2F-8097-140BA1E4B695}
8035 | 4712 | {9A1BD105-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF G | Bank 1 | CB 411 | PGE\DMAL | 2017-05-04 12:49:39.1836807 -07:00 | 02209411 |  | 3 | 3 | 3 | 2 | 265 | 1.91 | 1.89 | 265 | 1.91 | 1.89 | 286 | 2.06 | 2.04 | 286 | 2.06 | 2.04 | 273 | 1.97 | 1.95 | 273 | 1.97 | 1.95 | 295 | 2.13 | 2.11 | 295 | 2.13 | 2.11 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {FB593254-A962-4AB3-9B6E-BA1526E7C9CF}
8036 | 4712 | {9A1BD108-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF G | Bank 1 | CB 413 | PGE\DMAL | 2017-05-04 12:50:18.5588379 -07:00 | 02209413 |  | 3 | 3 | 3 | 2 | 350 | 2.52 | 2.49 | 350 | 2.52 | 2.49 | 378 | 2.72 | 2.69 | 378 | 2.72 | 2.69 | 361 | 2.6 | 2.57 | 361 | 2.6 | 2.57 | 389 | 2.8 | 2.77 | 389 | 2.8 | 2.77 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {3DC6559D-2DD8-4CD6-AFF4-646C01DB4082}
8037 | 4729 | {00C22899-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | TRIMBLE | Bank 1 | CB 1105 | PGE\ALWK | 2017-05-04 12:13:01.5070185 -07:00 | 0838001105 |  | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {8641FD53-9148-4C75-8212-76640FF4E2E6}
8038 | 4713 | {A23BBA6D-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF G | Bank 2 | CB 402 | PGE\DMAL | 2017-05-04 12:51:49.0717785 -07:00 | 02209402 |  | 3 | 3 | 3 | 2 | 350 | 2.52 | 2.49 | 350 | 2.52 | 2.49 | 378 | 2.72 | 2.69 | 378 | 2.72 | 2.69 | 361 | 2.6 | 2.57 | 361 | 2.6 | 2.57 | 389 | 2.8 | 2.77 | 389 | 2.8 | 2.77 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {6A6648F7-39C9-499C-8142-659111EFCA37}
8039 | 4713 | {A23BBA70-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF G | Bank 2 | CB 404 | PGE\DMAL | 2017-05-04 12:52:03.7516608 -07:00 | 02209404 |  | 3 | 3 | 3 | 2 | 290 | 2.09 | 2.07 | 290 | 2.09 | 2.07 | 313 | 2.26 | 2.24 | 313 | 2.26 | 2.24 | 299 | 2.15 | 2.13 | 299 | 2.15 | 2.13 | 323 | 2.33 | 2.31 | 323 | 2.33 | 2.31 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {9699A2AB-BD73-468D-8804-F84021909302}
8041 | 4713 | {A23BBA73-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF G | Bank 2 | CB 406 | PGE\DMAL | 2017-05-04 12:52:18.4315431 -07:00 | 02209406 |  | 3 | 3 | 3 | 2 | 350 | 2.52 | 2.49 | 350 | 2.52 | 2.49 | 378 | 2.72 | 2.69 | 378 | 2.72 | 2.69 | 361 | 2.6 | 2.57 | 361 | 2.6 | 2.57 | 389 | 2.8 | 2.77 | 389 | 2.8 | 2.77 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {6232D2C4-C42F-470F-826B-BDC235AE8692}
8042 | 4713 | {A23BBA76-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF G | Bank 2 | CB 408 | PGE\DMAL | 2017-05-04 12:52:30.3033714 -07:00 | 02209408 |  | 3 | 3 | 3 | 2 | 350 | 2.52 | 2.49 | 350 | 2.52 | 2.49 | 378 | 2.72 | 2.69 | 378 | 2.72 | 2.69 | 361 | 2.6 | 2.57 | 361 | 2.6 | 2.57 | 389 | 2.8 | 2.77 | 389 | 2.8 | 2.77 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {4D4836C4-6B73-49D6-B7C2-983BE43AFEE7}
8043 | 4713 | {A23BBA79-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF G | Bank 2 | CB 410 | PGE\DMAL | 2017-05-04 12:52:41.8163928 -07:00 | 02209410 |  | 3 | 3 | 3 | 2 | 350 | 2.52 | 2.49 | 350 | 2.52 | 2.49 | 378 | 2.72 | 2.69 | 378 | 2.72 | 2.69 | 361 | 2.6 | 2.57 | 361 | 2.6 | 2.57 | 389 | 2.8 | 2.77 | 389 | 2.8 | 2.77 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {45A093EA-FC4C-46F2-A1C8-85AD9E11EB57}
8044 | 4713 | {A23BBA7C-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF G | Bank 2 | CB 412 | PGE\DMAL | 2017-05-04 12:52:55.0142466 -07:00 | 02209412 |  | 3 | 3 | 3 | 2 | 350 | 2.52 | 2.49 | 350 | 2.52 | 2.49 | 378 | 2.72 | 2.69 | 378 | 2.72 | 2.69 | 361 | 2.6 | 2.57 | 361 | 2.6 | 2.57 | 389 | 2.8 | 2.77 | 389 | 2.8 | 2.77 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {AC7C7934-2E9E-4E67-9096-B072600EE4DF}
8045 | 4713 | {A23BBA7F-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF G | Bank 2 | CB 414 | PGE\DMAL | 2017-05-04 12:53:05.5756497 -07:00 | 02209414 |  | 3 | 3 | 3 | 2 | 350 | 2.52 | 2.49 | 350 | 2.52 | 2.49 | 378 | 2.72 | 2.69 | 378 | 2.72 | 2.69 | 361 | 2.6 | 2.57 | 361 | 2.6 | 2.57 | 389 | 2.8 | 2.77 | 389 | 2.8 | 2.77 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {81C5BF79-C52A-4F5C-B972-970E8042E10A}
8046 | 4729 | {00C228D4-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | TRIMBLE | Bank 1 | CB 1106 | PGE\ALWK | 2017-05-04 13:48:49.7291206 -07:00 | 0838001106 |  | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {5C2F19B1-84D4-4479-9EEF-1098C398FF71}
8048 | 4735 | {00C228E0-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | TRIMBLE | Bank 2 | CB 1107 | PGE\ALWK | 2017-05-04 14:49:40.9949521 -07:00 | 0838001107 |  | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {C346A0C9-397D-4A87-84E0-F18BB56C1C5C}
8049 | 4735 | {00C228F7-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | TRIMBLE | Bank 2 | CB 1108 | PGE\ALWK | 2017-05-04 15:12:02.4835444 -07:00 | 0838001108 |  | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {8374ED88-3FDB-4555-A992-79F2813EEF27}
8050 | 4735 | {06B87BD6-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | TRIMBLE | Bank 2 | CB 1109 | PGE\ALWK | 2017-05-04 15:19:05.6837333 -07:00 | 0838001109 |  | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {81D4FE17-787F-4B1D-BA2A-4566013E517A}
8051 | 4735 | {06B87BDF-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | TRIMBLE | Bank 2 | CB 1110 | PGE\ALWK | 2017-05-04 15:46:23.8352368 -07:00 | 0838001110 |  | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {56B272EF-3C44-4065-AECC-FF3EC55D78F8}
8053 | 4735 | {06B87BEB-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | TRIMBLE | Bank 2 | CB 1111 | PGE\ALWK | 2017-05-04 16:05:15.9000323 -07:00 | 0838001111 |  | 7 | 3 | 3 | 2 | 542 | 11.71 | 11.59 | 542 | 11.71 | 11.59 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 558 | 12.05 | 11.93 | 558 | 12.05 | 11.93 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {FEE32523-5E5F-4F43-BAC2-0ACA4227ACD9}
8055 | 4737 | {06B87BFE-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | TRIMBLE | Bank 3 | CB 2114 | PGE\ALWK | 2017-05-04 16:19:37.9323115 -07:00 | 0838002114 |  | 8 | 3 | 3 | 2 | 542 | 11.83 | 11.71 | 542 | 11.83 | 11.71 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {D661CE88-DC13-415D-996B-7F867506E3E1}
8056 | 4737 | {06B87C2A-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | TRIMBLE | Bank 3 | CB 2115 | PGE\ALWK | 2017-05-04 16:34:16.5481348 -07:00 | 0838002115 |  | 8 | 3 | 3 | 2 | 542 | 11.83 | 11.71 | 514 | 11.22 | 11.11 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 558 | 12.18 | 12.06 | 530 | 11.57 | 11.45 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {D819C9F2-EDFA-41B1-97E1-38904AF07523}
8057 | 4737 | {06B87C4B-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | TRIMBLE | Bank 3 | CB 2116 | PGE\ALWK | 2017-05-04 16:40:11.4640598 -07:00 | 0838002116 |  | 8 | 3 | 3 | 2 | 542 | 11.83 | 11.71 | 542 | 11.83 | 11.71 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {C1FFA31B-E67A-40AF-8A98-E03423A42789}
8058 | 4739 | {06B87CCE-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | TRIMBLE | Bank 5 | CB 2117 | PGE\ALWK | 2017-05-04 17:21:37.1391915 -07:00 | 0838002117 |  | 8 | 3 | 3 | 2 | 200 | 4.36 | 4.32 | 200 | 4.36 | 4.32 | 250 | 5.46 | 5.41 | 250 | 5.46 | 5.41 | 204 | 4.45 | 4.41 | 204 | 4.45 | 4.41 | 255 | 5.57 | 5.51 | 255 | 5.57 | 5.51 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {353A492D-CF77-4875-A538-278DF0B1D3EC}
8059 | 4739 | {06B87D2C-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | TRIMBLE | Bank 5 | CB 2118 | PGE\ALWK | 2017-05-04 17:29:26.4394489 -07:00 | 0838002118 |  | 8 | 3 | 3 | 2 | 542 | 11.83 | 11.71 | 542 | 11.83 | 11.71 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {4AEE759E-337E-46A3-9BC6-F87F2D89B5B6}
8060 | 4739 | {06B87DAC-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | TRIMBLE | Bank 5 | CB 2119 | PGE\ALWK | 2017-05-04 17:33:59.2644905 -07:00 | 0838002119 |  | 8 | 3 | 3 | 2 | 542 | 11.83 | 11.71 | 542 | 11.83 | 11.71 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {CB32D1EC-9479-4A69-BF95-C6472F2314C2}
8061 | 4717 | {E34D96AE-3ED6-11E6-A936-80000BC6CD8D} | SF L | 12KV BUS 2 (Non-SCADA) | Bank 2 (12kv) | CB 402 | PGE\S3AC | 2017-05-05 10:39:28.6951963 -07:00 | 02226402 |  | 3 | 3 | 3 | 2 | 363 | 2.62 | 2.59 | 363 | 2.62 | 2.59 | 392 | 2.82 | 2.79 | 392 | 2.82 | 2.79 | 374 | 2.69 | 2.66 | 374 | 2.69 | 2.66 | 404 | 2.91 | 2.88 | 404 | 2.91 | 2.88 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {CDF65EDC-5474-4D0E-AC96-993DC9BAB274}
8062 | 4717 | {A83688EE-78E2-11E5-8C7B-9CB70D532D7F} | SF L | 12KV BUS 2 (Non-SCADA) | Bank 2 (12kv) | CB 404 | PGE\S3AC | 2017-05-05 12:08:43.2133206 -07:00 | 022260404 |  | 3 | 3 | 3 | 2 | 363 | 2.62 | 2.59 | 363 | 2.62 | 2.59 | 392 | 2.82 | 2.79 | 392 | 2.82 | 2.79 | 374 | 2.69 | 2.66 | 374 | 2.69 | 2.66 | 404 | 2.91 | 2.88 | 404 | 2.91 | 2.88 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {E1B7DB31-ED1C-416A-98F3-DF05CABD187A}
8064 | 4717 | {A83688F7-78E2-11E5-8C7B-9CB70D532D7F} | SF L | 12KV BUS 2 (Non-SCADA) | Bank 2 (12kv) | CB 406 | PGE\S3AC | 2017-05-05 12:01:53.9082495 -07:00 | 022260406 |  | 3 | 3 | 3 | 2 | 363 | 2.62 | 2.59 | 363 | 2.62 | 2.59 | 392 | 2.82 | 2.79 | 392 | 2.82 | 2.79 | 374 | 2.69 | 2.66 | 374 | 2.69 | 2.66 | 404 | 2.91 | 2.88 | 404 | 2.91 | 2.88 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {704C22EC-C35E-409A-BD3B-E8A6CF68B710}
8065 | 4717 | {A83688FA-78E2-11E5-8C7B-9CB70D532D7F} | SF L | 12KV BUS 2 (Non-SCADA) | Bank 2 (12kv) | CB 408 | PGE\S3AC | 2017-05-05 12:07:01.1093571 -07:00 | 022260408 |  | 3 | 3 | 3 | 2 | 363 | 2.62 | 2.59 | 363 | 2.62 | 2.59 | 392 | 2.82 | 2.79 | 392 | 2.82 | 2.79 | 374 | 2.69 | 2.66 | 374 | 2.69 | 2.66 | 404 | 2.91 | 2.88 | 404 | 2.91 | 2.88 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {E2D176DB-68CC-43F3-9995-C29C707252ED}
8066 | 4716 | {A83688EB-78E2-11E5-8C7B-9CB70D532D7F} | SF L | 12KV BUS 1 (HL-1, HL-2, HL-3, HL-4) (Non-SCADA) | Bank 1 (12kv) | CB 401 | PGE\S3AC | 2017-05-05 12:26:17.1071874 -07:00 | 02226401 |  | 3 | 3 | 3 | 2 | 466 | 3.36 | 3.33 | 466 | 3.36 | 3.33 | 539 | 3.88 | 3.84 | 539 | 3.88 | 3.84 | 475 | 3.42 | 3.39 | 475 | 3.42 | 3.39 | 550 | 3.96 | 3.92 | 550 | 3.96 | 3.92 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {2F57ECA2-9A09-4AB9-A4A2-4A24A87AF398}
8067 | 4716 | {A23BBB02-78E2-11E5-8C7B-9CB70D532D7F} | SF L | 12KV BUS 1 (HL-1, HL-2, HL-3, HL-4) (Non-SCADA) | Bank 1 (12kv) | CB 403 | PGE\S3AC | 2017-05-05 12:28:32.8609980 -07:00 | 022260403 |  | 3 | 3 | 3 | 2 | 363 | 2.62 | 2.59 | 363 | 2.62 | 2.59 | 392 | 2.82 | 2.79 | 392 | 2.82 | 2.79 | 374 | 2.69 | 2.66 | 374 | 2.69 | 2.66 | 404 | 2.91 | 2.88 | 404 | 2.91 | 2.88 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {AAA5D51E-3379-4FE8-B1C9-60E0BC47EB82}
8068 | 4716 | {A83688F4-78E2-11E5-8C7B-9CB70D532D7F} | SF L | 12KV BUS 1 (HL-1, HL-2, HL-3, HL-4) (Non-SCADA) | Bank 1 (12kv) | CB 405 | PGE\S3AC | 2017-05-05 12:33:32.0591517 -07:00 | 02226405 |  | 3 | 3 | 3 | 2 | 363 | 2.62 | 2.59 | 363 | 2.62 | 2.59 | 392 | 2.82 | 2.79 | 392 | 2.82 | 2.79 | 374 | 2.69 | 2.66 | 374 | 2.69 | 2.66 | 404 | 2.91 | 2.88 | 404 | 2.91 | 2.88 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {85BF08A0-0A2D-4E08-A9AF-87E1E8F054FE}
8069 | 4716 | {A23BBB05-78E2-11E5-8C7B-9CB70D532D7F} | SF L | 12KV BUS 1 (HL-1, HL-2, HL-3, HL-4) (Non-SCADA) | Bank 1 (12kv) | CB 407 | PGE\S3AC | 2017-05-05 12:33:02.8241895 -07:00 | 022260407 |  | 3 | 3 | 3 | 2 | 363 | 2.62 | 2.59 | 363 | 2.62 | 2.59 | 392 | 2.82 | 2.79 | 392 | 2.82 | 2.79 | 374 | 2.69 | 2.66 | 374 | 2.69 | 2.66 | 404 | 2.91 | 2.88 | 404 | 2.91 | 2.88 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {500B2B3A-D04C-4529-824D-6E577AC7540B}
8071 | 4716 | {A23BBB08-78E2-11E5-8C7B-9CB70D532D7F} | SF L | 12KV BUS 1 (HL-1, HL-2, HL-3, HL-4) (Non-SCADA) | Bank 1 (12kv) | CB 409 | PGE\S3AC | 2017-05-05 12:36:04.9732923 -07:00 | 022260409 |  | 3 | 3 | 3 | 2 | 363 | 2.62 | 2.59 | 363 | 2.62 | 2.59 | 392 | 2.82 | 2.79 | 392 | 2.82 | 2.79 | 374 | 2.69 | 2.66 | 374 | 2.69 | 2.66 | 404 | 2.91 | 2.88 | 404 | 2.91 | 2.88 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {E990126C-5EA6-4804-A0BE-C71450D83467}
8072 | 4438 | {00C227C4-D1CB-11E5-8ECE-9CB70D532D7F} | SAN JOSE | SWIFT | Bank 2 | CB 2108 | PGE\RPBK | 2017-05-05 14:42:03.2406408 -07:00 | 0833902108 |  | 11 | 3 | 3 | 2 | 541 | 20.24 | 20.04 | 541 | 20.24 | 20.04 | 665 | 24.88 | 24.63 | 665 | 24.88 | 24.63 | 557 | 20.84 | 20.63 | 557 | 20.84 | 20.63 | 674 | 25.22 | 24.97 | 674 | 25.22 | 24.97 | Phase Relay: 799A Min Trip, Tap=0.667, Time Dial=0.7, Very Inverse, INST=6000 Ground Relay: 240A Min Trip, Tap=0.2, Time Dial=0.7, Very Inverse, INST=6000 Reclose= 5, 25 Reset=90 sec |  | FALSE | FALSE | 1202 | 1563 | 1443 | 1600 | {84F17882-5AEE-47D9-8EE7-12D520B9AB34}
8074 | 2735 | {10A6A93F-6007-11E6-9BE4-80000BC6CD8D} | KERN | STOCKDALE | BANK 4 | CB 1108 | PGE\JCS9 | 2017-05-05 16:20:05.3337558 -07:00 | 254071108 |  | 8 | 4 | 4 | 2 | 534 | 11.65 | 11.53 | 507 | 11.06 | 10.95 | 620 | 13.53 | 13.39 | 589 | 12.85 | 12.72 | 545 | 11.89 | 11.77 | 517 | 11.28 | 11.17 | 632 | 13.79 | 13.65 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {DEB7F8AF-123E-4D77-9243-7F17648FCF52}
8075 | 4724 | {A4FD422B-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | EL PATIO | Bank 1 | CB 1101 | PGE\IRB2 | 2017-05-08 09:46:37.9320952 -07:00 | 0829201101 |  | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {9DDDECB3-37B8-4B6F-B3B7-48DBF310CD14}
8076 | 4724 | {A4FD4234-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | EL PATIO | Bank 1 | CB 1102 | PGE\IRB2 | 2017-05-08 09:49:49.0094688 -07:00 | 0829201102 |  | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {F86D77BE-4B16-4C8E-85C0-4353D4AEF530}
8077 | 4724 | {A4FD423D-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | EL PATIO | Bank 1 | CB 1103 | PGE\IRB2 | 2017-05-08 10:30:36.8373023 -07:00 | 0829201103 |  | 8 | 3 | 3 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 598 | 13.05 | 12.92 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {806FE411-8106-4CEF-A649-3B6216439A59}
8078 | 4724 | {A4FD4254-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | EL PATIO | Bank 1 | CB 1104 | PGE\IRB2 | 2017-05-08 10:25:32.8576628 -07:00 | 0829201104 |  | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {007FE8F2-3A37-433E-9F39-BAB502BB1A8F}
8079 | 4724 | {A4FD427A-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | EL PATIO | Bank 1 | CB 1105 | PGE\IRB2 | 2017-05-08 10:31:24.5442429 -07:00 | 0829201105 |  | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {3C2B3432-41E3-42C2-96D8-2A066B0BC9D2}
8080 | 4726 | {A4FD42DF-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | EL PATIO | Bank 3 | CB 1111 | PGE\IRB2 | 2017-05-08 12:28:17.9949349 -07:00 | 0829201111 |  | 8 | 3 | 3 | 2 | 492 | 10.74 | 10.63 | 467 | 10.19 | 10.09 | 554 | 12.09 | 11.97 | 526 | 11.48 | 11.37 | 560 | 12.22 | 12.1 | 532 | 11.61 | 11.49 | 598 | 13.05 | 12.92 | 568 | 12.4 | 12.28 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {7768CFEC-AF1B-4C43-8A8A-D34F962D9745}
8082 | 4726 | {A4FD42E8-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | EL PATIO | Bank 3 | CB 1112 | PGE\IRB2 | 2017-05-08 12:34:59.3541438 -07:00 | 0829201112 |  | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {813F60A2-A55A-4F2B-A286-E987E728366F}
8083 | 4726 | {A4FD431B-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | EL PATIO | Bank 3 | CB 1113 | PGE\IRB2 | 2017-05-08 12:38:05.5016962 -07:00 | 0829201113 |  | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {BAF20330-4057-42EE-948A-40215F5CF317}
8084 | 4726 | {A4FD432B-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | EL PATIO | Bank 3 | CB 1114 | PGE\IRB2 | 2017-05-08 12:42:12.9287982 -07:00 | 0829201114 |  | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {B04CD6E5-9F82-4FDA-81E3-A1757D303BA9}
8085 | 4727 | {A4FD433E-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | EL PATIO | Bank 4 | CB 1116 | PGE\IRB2 | 2017-05-08 12:48:20.3876860 -07:00 | 0829201116 |  | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2434 | 2474 | 3000 | {6F9EF4CF-26F1-4EFB-B9D1-F014931524CA}
8086 | 4727 | {A4FD4355-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | EL PATIO | Bank 4 | CB 1117 | PGE\IRB2 | 2017-05-08 12:51:38.5321767 -07:00 | 0829201117 |  | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2434 | 2474 | 3000 | {A50E9C1B-4607-4E9C-8859-2DC81EE34A58}
8087 | 4727 | {A4FD4381-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | EL PATIO | Bank 4 | CB 1118 | PGE\IRB2 | 2017-05-08 12:56:56.8488595 -07:00 | 0829201118 |  | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2434 | 2474 | 3000 | {781CDE9D-D474-4631-BBF1-31DC3E9B61C9}
8088 | 4727 | {A4FD43A6-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | EL PATIO | Bank 4 | CB 1119 | PGE\IRB2 | 2017-05-08 14:32:23.6921964 -07:00 | 0829201119 |  | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 2061 | 2434 | 2474 | 3000 | {C2A143B8-318B-43A0-AA43-39DCDDF9530A}
8089 | 4733 | {A23BBAEA-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF K | Bank 3 | CB 403 (Non-SCADA) | PGE\S3AC | 2017-05-10 11:56:37.2064012 -07:00 | 022130403 |  | 3 | 3 | 3 | 2 | 277 | 2 | 1.98 | 277 | 2 | 1.98 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 277 | 360 | 333 | 416 | {BEF36D73-C3D3-4D86-BE2E-75E4E359B5EB}
8091 | 4734 | {A23BBAF0-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF K | Bank 4 | CB 406 (Non-SCADA) | PGE\S3AC | 2017-05-10 12:02:08.9779813 -07:00 | 022130406 |  | 3 | 3 | 3 | 2 | 277 | 2 | 1.98 | 277 | 2 | 1.98 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 400 | 2.88 | 2.85 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 277 | 360 | 333 | 416 | {C2959D6E-3E08-43C2-B919-931C88D5715E}
8093 | 4721 | {A8368903-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF M | Bank 1 | CB 401 (Non-SCADA) | PGE\DMAL | 2017-05-11 15:10:25.5234728 -07:00 | 022270401 |  | 3 | 3 | 3 | 2 | 321 | 2.31 | 2.29 | 321 | 2.31 | 2.29 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 358 | 2.58 | 2.55 | 358 | 2.58 | 2.55 | 382 | 2.75 | 2.72 | 382 | 2.75 | 2.72 |  |  | FALSE | FALSE | 600 | 600 | 600 | 600 | {2F8CA44F-A218-4864-BD08-EBBDA685B6A2}
8094 | 3869 | {7ADE0ECF-4927-11E6-AFF0-80000BC6CD8D} | KERN | LAMONT | BANK 3 | CB 1107 | PGE\VxLa | 2017-05-10 09:25:22.6902262 -07:00 | 253911107 |  | 8 | 3 | 3 | 1 | 575 | 12.55 | 12.42 | 546 | 11.92 | 11.8 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {74C33044-8EB9-44FD-BAA4-326EFFDCFFCF}
8097 | 2775 | {0A0140AE-0B43-11E6-9D37-D4BED91EFF1A} | KERN | OLD RIVER | Bank 1 | CB 1105 (Non-SCADA) | PGE\VxLa | 2017-05-09 11:47:27.1846660 -07:00 | 2528201105 |  | 8 | 3 | 3 | 1 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 | 733 | 16 | 15.84 |  |  | FALSE | FALSE | 1123 | 1123 | 1123 | 1123 | {076ECD10-5A3B-4182-B567-91880938A21B}
8101 | 4744 | {25604323-491A-11E6-AFF0-80000BC6CD8D} | STOCKTON | TRACY | BANK 1 TERTIARY (Non-SCADA) | CB 405 | PGE\VxLa | 2017-05-18 10:54:10.4852887 -07:00 |  |  | 3 | 3 | 3 | 1 | 282 | 2.03 | 2.01 | 267 | 1.92 | 1.9 | 315 | 2.27 | 2.25 | 299 | 2.15 | 2.13 | 330 | 2.38 | 2.36 | 330 | 2.38 | 2.36 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 |  |  | FALSE | FALSE | 1110 | 1443 | 1332 | 1665 | {3FBCFBAE-CA0B-4998-9A5F-3345F2DC6E09}
8103 | 4721 | {A8368906-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF M | Bank 1 | CB 403 (Non-SCADA) | PGE\DMAL | 2017-05-11 15:11:35.0852105 -07:00 | 022270403 |  | 3 | 3 | 3 | 2 | 378 | 2.72 | 2.69 | 378 | 2.72 | 2.69 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 389 | 2.8 | 2.77 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 600 | 600 | 600 | 600 | {78A15C9F-3133-4F91-A2A8-C7428982C85B}
8105 | 4722 | {A836890C-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF M | Bank 2 | CB 402 (Non-SCADA) | PGE\DMAL | 2017-05-11 15:13:56.7983357 -07:00 | 022270402 |  | 3 | 3 | 3 | 2 | 356 | 2.57 | 2.54 | 356 | 2.57 | 2.54 | 392 | 2.82 | 2.79 | 392 | 2.82 | 2.79 | 367 | 2.64 | 2.61 | 367 | 2.64 | 2.61 | 403 | 2.9 | 2.87 | 400 | 2.88 | 2.85 |  |  | FALSE | FALSE | 600 | 600 | 600 | 600 | {E781E698-28EF-4FC0-9FB5-ABAEBE80AC1E}
8106 | 4722 | {A836890F-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF M | Bank 2 | CB 404 (Non-SCADA) | PGE\DMAL | 2017-05-11 15:16:51.4592945 -07:00 | 022270404 |  | 3 | 3 | 3 | 2 | 378 | 2.72 | 2.69 | 378 | 2.72 | 2.69 | 416 | 3 | 2.97 | 416 | 3 | 2.97 | 389 | 2.8 | 2.77 | 389 | 2.8 | 2.77 | 428 | 3.08 | 3.05 | 428 | 3.08 | 3.05 |  |  | FALSE | FALSE | 600 | 600 | 600 | 600 | {3FDC57C7-9E18-4047-A2B0-5AAFC9F90AFE}
8108 | 4723 | {A8368915-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF M | Bank 3 | CB 405 (Non-SCADA) | PGE\DMAL | 2017-05-11 15:18:56.8233053 -07:00 | 022270405 |  | 3 | 3 | 3 | 2 | 356 | 2.57 | 2.54 | 356 | 2.57 | 2.54 | 392 | 2.82 | 2.79 | 380 | 2.74 | 2.71 | 367 | 2.64 | 2.61 | 367 | 2.64 | 2.61 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 600 | 600 | 600 | 600 | {6AE5AA33-20A7-470D-81B2-77CEE1577392}
8109 | 4723 | {A8368918-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF M | Bank 3 | CB 406 (Non-SCADA) | PGE\DMAL | 2017-05-11 15:21:07.9438268 -07:00 | 022270406 |  | 3 | 3 | 3 | 2 | 378 | 2.72 | 2.69 | 378 | 2.72 | 2.69 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 389 | 2.8 | 2.77 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 600 | 600 | 600 | 600 | {3F604492-6BE3-4518-8FA9-A9F2218C70C6}
8110 | 4731 | {A23BBAAF-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF K | Bank 1 | CB 401 | PGE\DMAL | 2017-05-11 17:16:21.3259739 -07:00 | 02213401 |  | 3 | 3 | 3 | 2 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {34CCF95E-717D-48B7-AAF5-CE7D3B5901BD}
8111 | 4731 | {A23BBAB5-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF K | Bank 1 | CB 405 | PGE\DMAL | 2017-05-11 17:27:13.5433163 -07:00 | 02213405 |  | 3 | 3 | 3 | 2 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {A25316DB-B18F-47CD-A23C-37B727FDCD31}
8112 | 4731 | {A23BBADB-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF K | Bank 1 | CB 407 | PGE\DMAL | 2017-05-11 17:33:02.9588357 -07:00 | 02213407 |  | 3 | 3 | 3 | 2 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {31359F03-0E6E-4B9A-ABE8-6C8657F048FA}
8113 | 4731 | {A23BBADE-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF K | Bank 1 | CB 409 | PGE\DMAL | 2017-05-11 17:36:02.8926959 -07:00 | 02213409 |  | 3 | 3 | 3 | 2 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {FD1C15CB-9B7E-470A-93E8-71E353347D78}
8114 | 4731 | {A23BBAE4-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF K | Bank 1 | CB 411 | PGE\DMAL | 2017-05-11 17:36:47.2131482 -07:00 | 02213411 |  | 3 | 3 | 3 | 2 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {F9DD1C05-CE12-4654-9E40-B6ADD4E23D61}
8115 | 4732 | {A23BBAB2-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF K | Bank 2 | CB 402 | PGE\DMAL | 2017-05-11 17:37:27.9299312 -07:00 | 02213402 |  | 3 | 3 | 3 | 2 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {5CA3FDF3-B28C-4C3F-A3EF-4D679E6AD04D}
8116 | 4732 | {A23BBAD8-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF K | Bank 2 | CB 404 | PGE\DMAL | 2017-05-11 17:38:04.9338428 -07:00 | 02213404 |  | 3 | 3 | 3 | 2 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {553D3CB8-B0C8-4D44-93DB-A935A97C79C1}
8117 | 4732 | {A23BBAB8-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF K | Bank 2 | CB 408 | PGE\DMAL | 2017-05-11 17:38:42.2341601 -07:00 | 02213408 |  | 3 | 3 | 3 | 2 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {575CA653-7BD7-4DAD-954D-E545EAA6A3B5}
8118 | 4732 | {A23BBAE1-78E2-11E5-8C7B-9CB70D532D7F} | SAN FRANCISCO | SF K | Bank 2 | CB 410 | PGE\DMAL | 2017-05-11 17:39:14.2303754 -07:00 | 02213410 |  | 3 | 3 | 3 | 2 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 | 300 | 2.16 | 2.14 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {7B21CBAD-B0CF-4DCB-B11E-E7974E76A8B4}
8119 | 4720 | {335CEF3A-C0B6-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | SF M | 4kv Main Bus | CB D-E/2 (Non-SCADA) | PGE\DMAL | 2017-05-11 17:05:30.4502573 -07:00 |  |  | 3 | 3 | 3 | 2 | 600 | 4.32 | 4.28 | 600 | 4.32 | 4.28 | 600 | 4.32 | 4.28 | 600 | 4.32 | 4.28 | 600 | 4.32 | 4.28 | 600 | 4.32 | 4.28 | 600 | 4.32 | 4.28 | 600 | 4.32 | 4.28 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {00000000-0000-0000-0000-000000000000}
8120 | 4594 | {7B459175-368C-11E7-813A-005056AE4E7D} | SAN FRANCISCO | MARINA (SF F) | 12kv Bus 2 | CB 1102 | PGE\DMAL | 2017-05-12 19:43:23.6034410 -07:00 | 022781102 |  | 21 | 3 | 3 | 2 | 333 | 6.92 | 6.85 | 333 | 6.92 | 6.85 | 370 | 7.69 | 7.61 | 370 | 7.69 | 7.61 | 343 | 7.13 | 7.06 | 343 | 7.13 | 7.06 | 381 | 7.92 | 7.84 | 381 | 7.92 | 7.84 | Branch 11542 - 250T P&L NS - ELC=2. Branch 11540 - 500T P&L NS - ELC=2. |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {00000000-0000-0000-0000-000000000000}
8121 | 4613 | {60B1149C-368C-11E7-813A-005056AE4E7D} | SAN FRANCISCO | MARINA (SF F) | 12kv Bus 1 (FY-1, FY-2, FY-3, FY-4) | CB 1101 | PGE\DMAL | 2017-05-12 20:05:26.0903807 -07:00 | 022781101 |  | 21 | 3 | 3 | 2 | 397 | 8.25 | 8.17 | 397 | 8.25 | 8.17 | 450 | 9.35 | 9.26 | 450 | 9.35 | 9.26 | 417 | 8.67 | 8.58 | 417 | 8.67 | 8.58 | 463 | 9.62 | 9.52 | 463 | 9.62 | 9.52 | Standby Feeder to Golden Gate Bridge ATS-77652_37548. |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {00000000-0000-0000-0000-000000000000}
8122 | 4720 | {51671A4A-C0B6-11E6-93A9-D4BED91EFF1A} | SAN FRANCISCO | SF M | 4kv Main Bus | CB E-F/2 (Non-SCADA) | PGE\DMAL | 2017-05-11 17:06:06.1905446 -07:00 |  |  | 3 | 3 | 3 | 2 | 600 | 4.32 | 4.28 | 600 | 4.32 | 4.28 | 600 | 4.32 | 4.28 | 600 | 4.32 | 4.28 | 600 | 4.32 | 4.28 | 600 | 4.32 | 4.28 | 600 | 4.32 | 4.28 | 600 | 4.32 | 4.28 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {00000000-0000-0000-0000-000000000000}
8169 | 4761 | {2C74442D-2DA1-11E6-B38D-D4BED91EFF1A} | EAST BAY | BERKELEY F | 12kv Bus 2 (DWF-1, DWF-2, DWF-3) | CB 1104 | PGE\C7CF | 2017-05-23 13:24:04.1585079 -07:00 | 0120601104 |  | 7 | 3 | 3 | 2 | 407 | 8.79 | 8.7 | 407 | 8.79 | 8.7 | 430 | 9.29 | 9.2 | 430 | 9.29 | 9.2 | 419 | 9.05 | 8.96 | 419 | 9.05 | 8.96 | 430 | 9.29 | 9.2 | 430 | 9.29 | 9.2 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {BDAE6D83-6306-474D-9C3B-425A7185A04C}
8170 | 4283 | {5E235365-C24B-11E6-93A9-D4BED91EFF1A} | EAST BAY | BERKELEY F | Bank 1 | CB F-1 | PGE\C7CF | 2017-05-23 13:50:17.3285284 -07:00 |  |  | 3 | 3 | 3 | 2 | 356 | 2.57 | 2.54 | 356 | 2.57 | 2.54 | 392 | 2.82 | 2.79 | 380 | 2.74 | 2.71 | 367 | 2.64 | 2.61 | 367 | 2.64 | 2.61 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {56E0775D-F8C6-44FB-9851-9099BCDF591B}
8171 | 4582 | {C8053B30-C24B-11E6-93A9-D4BED91EFF1A} | EAST BAY | BERKELEY F | Bank 2 | CB F-2 | PGE\C7CF | 2017-05-23 14:25:44.6283089 -07:00 |  |  | 3 | 3 | 3 | 2 | 356 | 2.57 | 2.54 | 356 | 2.57 | 2.54 | 392 | 2.82 | 2.79 | 380 | 2.74 | 2.71 | 367 | 2.64 | 2.61 | 367 | 2.64 | 2.61 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {D423003C-313D-4192-83BA-0AD286E45AD8}
8172 | 4283 | {722662BE-C24B-11E6-93A9-D4BED91EFF1A} | EAST BAY | BERKELEY F | Bank 1 | CB F-3 | PGE\C7CF | 2017-05-23 14:34:05.5759644 -07:00 |  |  | 3 | 3 | 3 | 2 | 356 | 2.57 | 2.54 | 356 | 2.57 | 2.54 | 392 | 2.82 | 2.79 | 380 | 2.74 | 2.71 | 367 | 2.64 | 2.61 | 367 | 2.64 | 2.61 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {BC83A8D6-2B17-40C9-9E74-472FCD4F8B7B}
8173 | 4582 | {D9F2C69F-C24B-11E6-93A9-D4BED91EFF1A} | EAST BAY | BERKELEY F | Bank 2 | CB F-4 | PGE\C7CF | 2017-05-23 14:38:57.0401059 -07:00 |  |  | 3 | 3 | 3 | 2 | 356 | 2.57 | 2.54 | 356 | 2.57 | 2.54 | 392 | 2.82 | 2.79 | 380 | 2.74 | 2.71 | 367 | 2.64 | 2.61 | 367 | 2.64 | 2.61 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {F56AE0DB-4374-45F1-841B-ED8537A4D033}
8174 | 4283 | {988403AC-C24B-11E6-93A9-D4BED91EFF1A} | EAST BAY | BERKELEY F | Bank 1 | CB F-5 | PGE\C7CF | 2017-05-23 14:48:36.9106909 -07:00 |  |  | 3 | 3 | 3 | 2 | 293 | 2.11 | 2.09 | 293 | 2.11 | 2.09 | 316 | 2.28 | 2.26 | 316 | 2.28 | 2.26 | 302 | 2.18 | 2.16 | 302 | 2.18 | 2.16 | 326 | 2.35 | 2.33 | 326 | 2.35 | 2.33 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {3F896C92-BC08-4EC9-B5B0-DFB592E4428A}
8175 | 4582 | {FB29E2C0-C24B-11E6-93A9-D4BED91EFF1A} | EAST BAY | BERKELEY F | Bank 2 | CB F-6 | PGE\C7CF | 2017-05-23 14:56:55.3310654 -07:00 |  |  | 3 | 3 | 3 | 2 | 207 | 1.49 | 1.48 | 207 | 1.49 | 1.48 | 224 | 1.61 | 1.59 | 224 | 1.61 | 1.59 | 213 | 1.53 | 1.51 | 213 | 1.53 | 1.51 | 230 | 1.66 | 1.64 | 230 | 1.66 | 1.64 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {0CC09A28-6F13-44A6-BE43-5487CD54BEF4}
8176 | 4283 | {8264915E-C24B-11E6-93A9-D4BED91EFF1A} | EAST BAY | BERKELEY F | Bank 1 | CB F-7 | PGE\C7CF | 2017-05-23 15:03:50.7567799 -07:00 |  |  | 3 | 3 | 3 | 2 | 293 | 2.11 | 2.09 | 293 | 2.11 | 2.09 | 316 | 2.28 | 2.26 | 316 | 2.28 | 2.26 | 302 | 2.18 | 2.16 | 302 | 2.18 | 2.16 | 326 | 2.35 | 2.33 | 326 | 2.35 | 2.33 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {C6057146-E218-4A62-B2FE-EB9FFBC835D8}
8177 | 4582 | {EB119268-C24B-11E6-93A9-D4BED91EFF1A} | EAST BAY | BERKELEY F | Bank 2 | CB F-8 | PGE\C7CF | 2017-05-23 15:36:46.4509014 -07:00 |  |  | 3 | 3 | 3 | 2 | 356 | 2.57 | 2.54 | 356 | 2.57 | 2.54 | 392 | 2.82 | 2.79 | 380 | 2.74 | 2.71 | 367 | 2.64 | 2.61 | 367 | 2.64 | 2.61 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {24A7E9CE-A937-4986-8D32-367ED71EF7D1}
8178 | 4283 | {A39C70F2-C24B-11E6-93A9-D4BED91EFF1A} | EAST BAY | BERKELEY F | Bank 1 | CB F-9 | PGE\C7CF | 2017-05-23 15:56:03.9611999 -07:00 |  |  | 3 | 3 | 3 | 2 | 302 | 2.18 | 2.16 | 302 | 2.18 | 2.16 | 326 | 2.35 | 2.33 | 326 | 2.35 | 2.33 | 311 | 2.24 | 2.22 | 311 | 2.24 | 2.22 | 336 | 2.42 | 2.4 | 336 | 2.42 | 2.4 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {A78DAB74-B35C-4D73-95F4-DFF1BA2CF1A8}
8179 | 4582 | {0F98232B-C24C-11E6-93A9-D4BED91EFF1A} | EAST BAY | BERKELEY F | Bank 2 | CB F-10 | PGE\C7CF | 2017-05-23 16:06:27.6067879 -07:00 |  |  | 3 | 3 | 3 | 2 | 378 | 2.72 | 2.69 | 378 | 2.72 | 2.69 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 | 389 | 2.8 | 2.77 | 380 | 2.74 | 2.71 | 400 | 2.88 | 2.85 | 380 | 2.74 | 2.71 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {3C762502-53DE-47E6-A5BF-86AF564CD9DF}
8180 | 4283 | {6B94419A-C24C-11E6-93A9-D4BED91EFF1A} | EAST BAY | BERKELEY F | Bank 1 | CB F-11 | PGE\C7CF | 2017-05-23 16:19:15.4643172 -07:00 |  |  | 3 | 3 | 3 | 2 | 333 | 2.4 | 2.38 | 333 | 2.4 | 2.38 | 360 | 2.59 | 2.56 | 360 | 2.59 | 2.56 | 343 | 2.47 | 2.45 | 343 | 2.47 | 2.45 | 370 | 2.67 | 2.64 | 370 | 2.67 | 2.64 |  |  | FALSE | FALSE | 1734 | 2000 | 2000 | 2000 | {22839F1D-2751-4413-ADAD-A8299FBF4DE1}
8181 | 4271 | {EEB8919F-4AAF-11E6-AFF0-80000BC6CD8D} | EAST BAY | OAKLAND X | Bank 5 | CB 1103 | PGE\C7CF | 2017-05-23 17:28:37.5075651 -07:00 | 012541103 |  | 7 | 3 | 3 | 2 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {3E7C4D4D-1652-4069-8B5F-93E4827379A4}
8182 | 4269 | {1A06DC31-D2D6-11E6-B89B-9CB70D532D7F} | EAST BAY | OAKLAND X | Bank 2 | CB 1113 | PGE\C7CF | 2017-05-23 17:36:51.1541866 -07:00 |  |  | 7 | 3 | 3 | 2 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 | 500 | 10.8 | 10.69 |  |  | FALSE | FALSE | 1388 | 1805 | 1666 | 2083 | {6B8A9A4F-AB57-469A-8068-A9A54B51FA93}
8183 | 4763 | {E1DAEDB9-D1E4-11E6-B89B-9CB70D532D7F} | EAST BAY | RICHMOND R | 12kv BUS 1 | CB D-E/12 | PGE\C7CF | 2017-05-23 17:44:28.2020351 -07:00 |  |  | 7 | 4 | 4 | 2 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 | 2000 | 43.2 | 42.77 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {BA7316B5-1472-4EE2-8951-D5094E5A3F92}
8184 | 4763 | {152265C5-D1E5-11E6-B89B-9CB70D532D7F} | EAST BAY | RICHMOND R | 12kv BUS 1 | CB E-F/12 | PGE\C7CF | 2017-05-23 17:45:11.2438146 -07:00 |  |  | 7 | 4 | 4 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {1AF7EBC0-EE9D-4E3D-A49E-5EBA2D4D057D}
8185 | 4764 | {341C2389-D1E5-11E6-B89B-9CB70D532D7F} | EAST BAY | RICHMOND R | 12kv BUS 2 | CB E-F/22 | PGE\C7CF | 2017-05-23 17:47:06.2194996 -07:00 |  |  | 7 | 4 | 4 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {A1CDC589-BDFA-4AB1-9138-7BFE01D4E4EE}
8186 | 4764 | {FD0B8440-D1E4-11E6-B89B-9CB70D532D7F} | EAST BAY | RICHMOND R | 12kv BUS 2 | CB D-E/22 | PGE\C7CF | 2017-05-23 17:47:26.3441446 -07:00 |  |  | 7 | 4 | 4 | 2 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 4000 | 4000 | 4000 | 4000 | {6D895BB9-3965-4FC1-AAC7-61B3FE440CC5}
8187 | 3850 | {FA7767B8-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | RICHMOND R | Bank 2 | CB 1118 | PGE\C7CF | 2017-05-23 17:58:53.0157526 -07:00 | 0134701118 |  | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {EAAB7607-5C12-4C0D-B996-00CBAF7EE7C5}
8188 | 3850 | {FA7767BE-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | RICHMOND R | Bank 2 | CB 1120 | PGE\C7CF | 2017-05-23 18:21:42.8176551 -07:00 | 0134701120 |  | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {B33689BA-95E7-4819-A932-51CAB2F2498D}
8189 | 3850 | {FA7767C4-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | RICHMOND R | Bank 2 | CB 1121 | PGE\C7CF | 2017-05-23 18:20:40.0100421 -07:00 | 0134701121 |  | 7 | 3 | 3 | 2 | 425 | 9.18 | 9.09 | 425 | 9.18 | 9.09 | 476 | 10.28 | 10.18 | 476 | 10.28 | 10.18 | 438 | 9.46 | 9.37 | 438 | 9.46 | 9.37 | 490 | 10.58 | 10.47 | 490 | 10.58 | 10.47 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {0805F67F-9F16-4AAC-8A38-9A2C5A958D11}
8191 | 3850 | {FA7767D3-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | RICHMOND R | Bank 2 | CB 1123 | PGE\C7CF | 2017-05-24 09:34:58.4763347 -07:00 | 0134701123 |  | 7 | 3 | 3 | 2 | 425 | 9.18 | 9.09 | 425 | 9.18 | 9.09 | 476 | 10.28 | 10.18 | 476 | 10.28 | 10.18 | 438 | 9.46 | 9.37 | 438 | 9.46 | 9.37 | 490 | 10.58 | 10.47 | 490 | 10.58 | 10.47 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {1F6C894F-C3B5-45EA-B486-EDF916F7F00D}
8192 | 3850 | {FA7767D6-78E4-11E5-8C7B-9CB70D532D7F} | EAST BAY | RICHMOND R | Bank 2 | CB 1124 | PGE\C7CF | 2017-05-24 09:40:41.8901412 -07:00 | 0134701124 |  | 7 | 3 | 3 | 2 | 492 | 10.63 | 10.52 | 467 | 10.09 | 9.99 | 554 | 11.97 | 11.85 | 526 | 11.36 | 11.25 | 557 | 12.03 | 11.91 | 532 | 11.49 | 11.38 | 598 | 12.92 | 12.79 | 568 | 12.27 | 12.15 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {4B0088FD-255D-40C2-973E-7438DCFCA966}
8193 | 3851 | {06D72FE7-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | RICHMOND R | Bank 3 | CB 1122 | PGE\C7CF | 2017-05-24 09:58:53.7691362 -07:00 | 0134701122 |  | 7 | 3 | 3 | 2 | 545 | 11.77 | 11.65 | 545 | 11.77 | 11.65 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 556 | 12.01 | 11.89 | 556 | 12.01 | 11.89 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {CAE6F08A-AAF3-4B3D-9AB2-FD33E7B34877}
8194 | 3851 | {06D72FF0-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | RICHMOND R | Bank 3 | CB 1127 | PGE\C7CF | 2017-05-24 10:06:47.5875222 -07:00 | 0134701127 |  | 7 | 3 | 3 | 2 | 541 | 11.68 | 11.56 | 541 | 11.68 | 11.56 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 557 | 12.03 | 11.91 | 557 | 12.03 | 11.91 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {599EAD0D-62F3-4EE7-88BE-400C33894016}
8195 | 3851 | {0D3AE151-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | RICHMOND R | Bank 3 | CB 1129 | PGE\C7CF | 2017-05-24 10:25:17.8153974 -07:00 | 0134701129 |  | 7 | 3 | 3 | 2 | 446 | 9.63 | 9.53 | 446 | 9.63 | 9.53 | 549 | 11.86 | 11.74 | 549 | 11.86 | 11.74 | 459 | 9.91 | 9.81 | 459 | 9.91 | 9.81 | 556 | 12.01 | 11.89 | 556 | 12.01 | 11.89 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {EDF85CC9-426B-4D22-A88B-18BAE3C08454}
8196 | 4772 | {196F1740-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | MONTICELLO | Bank 1 | CB 1101 | PGE\C7CF | 2017-05-24 17:56:38.2842908 -07:00 | 0430501101 |  | 8 | 3 | 3 | 2 | 219 | 4.78 | 4.73 | 219 | 4.78 | 4.73 | 285 | 6.22 | 6.16 | 285 | 6.22 | 6.16 | 263 | 5.74 | 5.68 | 263 | 5.74 | 5.68 | 329 | 7.18 | 7.11 | 329 | 7.18 | 7.11 |  |  | FALSE | FALSE | 219 | 285 | 263 | 329 | {73A3C4E9-1F65-436B-A3A0-34B6BBF51C68}
8197 | 4425 | {35B1CA20-0B44-11E6-9D37-D4BED91EFF1A} | FRESNO | TULE POWER HOUSE | BANK 2 | CB 1101 (Non-SCADA) | PGE\KRBk | 2017-05-25 14:49:36.7632325 -07:00 | 2585901101 |  | 8 | 2 | 2 | 1 | 68 | 1.48 | 1.47 | 64 | 1.4 | 1.39 | 80 | 1.75 | 1.73 | 76 | 1.66 | 1.64 | 80 | 1.75 | 1.73 | 76 | 1.66 | 1.64 | 80 | 1.75 | 1.73 | 76 | 1.66 | 1.64 |  |  | TRUE | FALSE | 68 | 80 | 80 | 80 | {82BA4885-FDFF-4689-8F32-5B336780827C}
8199 | 1169 | {C51140CC-671D-11E5-80CA-005056A729E5} | FRESNO | HURON | Bank 1 | CB 1112 | PGE\JCS9 | 2017-05-26 09:13:45.2801245 -07:00 | 2531601112 |  | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 916 | 1125 | 1100 | 1200 | {01B745AF-D8CE-4015-BC9B-864A0DA383DA}
8200 | 4760 | {B73829F3-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WOLFE | Bank 3 | CB 1113 | PGE\MSJ9 | 2017-05-27 09:15:49.6724752 -07:00 | 0836701113 |  | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | 600 | 12.96 | 12.83 | 570 | 12.31 | 12.19 | Relay Minimum Phase: 720A T 3 L 2 CT Ratio: 1200:5 To Operate Ground: 180A T 0.75 L 4 Ammeter Range 0 to 100 |  | FALSE | FALSE | 2083 | 2640 | 2200 | 2640 | {4567FDF4-1BC6-441D-8E11-4AD4A66316A6}
8201 | 4760 | {B7382A03-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | WOLFE | Bank 3 | CB 1114 | PGE\MSJ9 | 2017-05-27 09:17:48.1426722 -07:00 | 0836701114 |  | 7 | 3 | 3 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | Relay Minimum Phase: 700 T 3 L 3.5 CT Ratio: 1200:5 To Operate Ground: 180 T 0.75 L 4 Ammeter Range 0 to 100 |  | FALSE | FALSE | 2083 | 2640 | 2200 | 2640 | {0A8793FB-0B94-4F4E-A9C5-5354BB9A4593}
8202 | 2769 | {1FE69E93-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | NAPA | Bank 1 | CB 1102 | PGE\C7CF | 2017-05-30 10:51:27.1853401 -07:00 | 0420201102 |  | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 552 | 12.05 | 11.93 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {7D837840-8F76-4D4C-8A34-3D21D53CDEB7}
8203 | 2769 | {1FE69E9B-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | NAPA | Bank 1 | CB 1103 | PGE\C7CF | 2017-05-30 10:56:33.7195646 -07:00 | 0420201103 |  | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 552 | 12.05 | 11.93 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {A8BF5FBF-4D70-4EA7-BA40-1016DC47A715}
8204 | 2769 | {1FE69EA6-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | NAPA | Bank 1 | CB 1104 | PGE\C7CF | 2017-05-30 11:01:56.8059196 -07:00 | 042021104 |  | 8 | 3 | 3 | 2 | 1200 | 26.19 | 25.93 | 1200 | 26.19 | 25.93 | 1200 | 26.19 | 25.93 | 1200 | 26.19 | 25.93 | 1200 | 26.19 | 25.93 | 1200 | 26.19 | 25.93 | 1200 | 26.19 | 25.93 | 1200 | 26.19 | 25.93 | Normal Open CB |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {247A791A-A15A-4332-AB90-B60C3F466381}
8205 | 2771 | {1FE69EBB-78E6-11E5-8C7B-9CB70D532D7F} | NORTH BAY | NAPA | Bank 3 | CB 1109 | PGE\C7CF | 2017-05-30 11:10:30.3119776 -07:00 | 0420201109 |  | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {8BD7568F-07E2-4E84-AC31-4DC0B4E0BA2C}
8206 | 2771 | {B3281AB1-FDD3-11E5-9D37-D4BED91EFF1A} | NORTH BAY | NAPA | Bank 3 | CB 1110 | PGE\C7CF | 2017-05-30 11:10:06.5212151 -07:00 | 0420201110 |  | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {331F93C2-656B-4F84-9BF3-8FB58C7DC9E3}
8207 | 2771 | {4468181D-DE8B-11E6-8DDC-9CB70D532D7F} | NORTH BAY | NAPA | Bank 3 | CB 1111 | PGE\C7CF | 2017-05-30 11:11:08.2835946 -07:00 |  |  | 8 | 3 | 3 | 2 | 1200 | 26.19 | 25.93 | 1140 | 24.88 | 24.63 | 1200 | 26.19 | 25.93 | 1140 | 24.88 | 24.63 | 1200 | 26.19 | 25.93 | 1140 | 24.88 | 24.63 | 1200 | 26.19 | 25.93 | 1140 | 24.88 | 24.63 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {1E6E5B95-AFB2-4B11-8116-3A3B8571CD7F}
8208 | 2771 | {EAA5C269-E652-11E5-9614-9CB70D532D7F} | NORTH BAY | NAPA | Bank 3 | CB 1112 | PGE\C7CF | 2017-05-30 11:14:03.3992071 -07:00 | 0420201112 |  | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 552 | 12.05 | 11.93 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {27B511B3-DDC1-4658-A685-F00DB448E994}
8209 | 2771 | {4F91FA59-3F29-11E7-813B-005056AE4E7D} | NORTH BAY | NAPA | Bank 3 | CB 1750/2 (Under Construction) | PGE\C7CF | 2017-05-30 11:14:52.7279881 -07:00 |  |  | 8 | 4 | 4 | 2 | 1374 | 29.99 | 29.69 | 1374 | 29.99 | 29.69 | 1787 | 39 | 38.61 | 1787 | 39 | 38.61 | 1649 | 35.99 | 35.63 | 1649 | 35.99 | 35.63 | 2000 | 43.65 | 43.21 | 2000 | 43.65 | 43.21 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {6A64BB9B-403C-49E1-8079-14DDD74565C7}
8210 | 2771 | {63B96152-3F29-11E7-813B-005056AE4E7D} | NORTH BAY | NAPA | Bank 3 | CB 1850/2 (Under Construction) | PGE\C7CF | 2017-05-30 11:15:33.5232956 -07:00 |  |  | 8 | 4 | 4 | 2 | 1374 | 29.99 | 29.69 | 1374 | 29.99 | 29.69 | 1787 | 39 | 38.61 | 1787 | 39 | 38.61 | 1649 | 35.99 | 35.63 | 1649 | 35.99 | 35.63 | 2000 | 43.65 | 43.21 | 2000 | 43.65 | 43.21 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {A5FAF62F-7003-41F2-803C-813CDAC6BE0A}
8211 | 2771 | {76314380-3F29-11E7-813B-005056AE4E7D} | NORTH BAY | NAPA | Bank 3 | CB 1950/2 (Under Construction) | PGE\C7CF | 2017-05-30 11:16:03.0706426 -07:00 |  |  | 8 | 4 | 4 | 2 | 1374 | 29.99 | 29.69 | 1374 | 29.99 | 29.69 | 1787 | 39 | 38.61 | 1787 | 39 | 38.61 | 1649 | 35.99 | 35.63 | 1649 | 35.99 | 35.63 | 2000 | 43.65 | 43.21 | 2000 | 43.65 | 43.21 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {A68366AF-A0FD-4DD9-83C8-CE166D427927}
8212 | 2547 | {3ECC0B68-E7F9-11E6-BC23-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 2 | CB BK 2/12 | PGE\C7CF | 2017-05-30 15:56:40.4599338 -07:00 |  |  | 7 | 4 | 4 | 2 | 2083 | 44.99 | 44.54 | 2083 | 44.99 | 44.54 | 2708 | 58.49 | 57.91 | 2708 | 58.49 | 57.91 | 2500 | 54 | 53.46 | 2500 | 54 | 53.46 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {CC77A485-5B2E-4F76-8099-07D882872DC1}
8213 | 2547 | {500DEDA8-E7F9-11E6-BC23-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 2 | CB BK 2/2 | PGE\C7CF | 2017-05-30 15:57:01.6298123 -07:00 |  |  | 7 | 4 | 4 | 2 | 2083 | 44.99 | 44.54 | 2083 | 44.99 | 44.54 | 2708 | 58.49 | 57.91 | 2708 | 58.49 | 57.91 | 2500 | 54 | 53.46 | 2500 | 54 | 53.46 | 3000 | 64.8 | 64.15 | 3000 | 64.8 | 64.15 |  |  | FALSE | FALSE | 2083 | 2708 | 2500 | 3125 | {495BF778-AC39-41C7-A381-FD15B9DBA770}
8214 | 4762 | {665B4733-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 4 | CB 401 | PGE\C7CF | 2017-05-30 16:34:46.9472163 -07:00 | 012090401 |  | 4 | 3 | 3 | 2 | 356 | 2.69 | 2.66 | 356 | 2.69 | 2.66 | 392 | 2.97 | 2.94 | 392 | 2.97 | 2.94 | 367 | 2.78 | 2.75 | 367 | 2.78 | 2.75 | 403 | 3.05 | 3.02 | 403 | 3.05 | 3.02 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {97D36970-F9AA-44B7-B035-535F9F4C3468}
8215 | 4762 | {665B4736-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND J | Bank 4 | CB 408 | PGE\C7CF | 2017-05-30 16:46:54.9757498 -07:00 | 012090408 |  | 4 | 3 | 3 | 2 | 356 | 2.69 | 2.66 | 356 | 2.69 | 2.66 | 383 | 2.9 | 2.87 | 383 | 2.9 | 2.87 | 367 | 2.78 | 2.75 | 367 | 2.78 | 2.75 | 383 | 2.9 | 2.87 | 383 | 2.9 | 2.87 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {7ECBE1E7-1C37-4B21-8352-A0D943EE9F3E}
8216 | 4650 | {2DBE3BD6-5FE0-11E6-9BE4-80000BC6CD8D} | DE ANZA | LAWRENCE | Bank 2 | CB 1107 | PGE\IRB2 | 2017-06-02 09:13:07.0515213 -07:00 | 083421107 |  | 8 | 3 | 3 | 2 | 564 | 12.31 | 12.19 | 564 | 12.31 | 12.19 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3092 | {73487982-F751-4101-81A1-D8E56DE5736B}
8217 | 4774 | {AE9993FE-5FDF-11E6-9BE4-80000BC6CD8D} | EAST BAY | OAKLAND L | 12kv BUS 2 (BK 1, BK 3, BK 5) | CB 1103 | PGE\C7CF | 2017-06-05 17:07:31.5753327 -07:00 | 012111103 |  | 7 | 4 | 4 | 2 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {92818579-7581-4CD5-B83D-B7AA9C039974}
8218 | 4774 | {D1430C3D-334C-11E6-B38D-D4BED91EFF1A} | EAST BAY | OAKLAND L | 12kv BUS 2 (BK 1, BK 3, BK 5) | CB 1104 (Non-SCADA) | PGE\C7CF | 2017-06-05 17:16:22.9337449 -07:00 | 0121101104 |  | 7 | 3 | 3 | 2 | 446 | 9.63 | 9.53 | 446 | 9.63 | 9.53 | 549 | 11.86 | 11.74 | 549 | 11.86 | 11.74 | 459 | 9.91 | 9.81 | 459 | 9.91 | 9.81 | 556 | 12.01 | 11.89 | 556 | 12.01 | 11.89 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {6FB40FC7-D000-4315-9740-C2405CB6E754}
8219 | 4774 | {794386F2-78E5-11E5-8C7B-9CB70D532D7F} | EAST BAY | OAKLAND L | 12kv BUS 2 (BK 1, BK 3, BK 5) | CB 1106 | PGE\C7CF | 2017-06-05 17:22:48.5862891 -07:00 | 0121101106 |  | 7 | 3 | 3 | 2 | 545 | 11.77 | 11.65 | 545 | 11.77 | 11.65 | 633 | 13.67 | 13.53 | 633 | 13.67 | 13.53 | 556 | 12.01 | 11.89 | 556 | 12.01 | 11.89 | 646 | 13.95 | 13.81 | 646 | 13.95 | 13.81 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {4F56BAD9-0A85-443F-93E7-61E197644AC3}
8220 | 4774 | {D92B4BD9-5FDF-11E6-9BE4-80000BC6CD8D} | EAST BAY | OAKLAND L | 12kv BUS 2 (BK 1, BK 3, BK 5) | CB 1108 | PGE\C7CF | 2017-06-05 17:28:17.1421013 -07:00 | 012111108 |  | 7 | 3 | 3 | 2 | 517 | 11.17 | 11.06 | 517 | 11.17 | 11.06 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 | 527 | 11.38 | 11.27 | 527 | 11.38 | 11.27 | 600 | 12.96 | 12.83 | 600 | 12.96 | 12.83 |  |  | FALSE | FALSE | 2000 | 2000 | 2000 | 2000 | {27FBD3C3-25DB-4D59-9381-20D78609C4E0}
8221 | 4776 | {D9CA3885-EE39-11E6-BC23-9CB70D532D7F} | PENINSULA | LAS PULGAS | Bank 1 | CB 410 | PGE\C7CF | 2017-06-06 16:06:26.8029493 -07:00 |  |  | 4 | 4 | 4 | 2 | 924 | 6.99 | 6.92 | 924 | 6.99 | 6.92 | 1202 | 9.1 | 9.01 | 1202 | 9.1 | 9.01 | 1109 | 8.39 | 8.31 | 1109 | 8.39 | 8.31 | 1387 | 10.5 | 10.4 | 1387 | 10.5 | 10.4 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {5B435002-8F59-470B-8593-FA8812ECDF59}
8222 | 4776 | {25CD65E7-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | LAS PULGAS | Bank 1 | CB 401 | PGE\C7CF | 2017-06-06 16:13:47.9454049 -07:00 | 02412401 |  | 4 | 3 | 3 | 2 | 409 | 3.1 | 3.07 | 409 | 3.1 | 3.07 | 474 | 3.59 | 3.55 | 474 | 3.59 | 3.55 | 417 | 3.16 | 3.13 | 417 | 3.16 | 3.13 | 483 | 3.66 | 3.62 | 483 | 3.66 | 3.62 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {CD659795-9CDF-45A3-BFDD-712D06A711D2}
8223 | 4776 | {25CD65F0-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | LAS PULGAS | Bank 1 | CB 402 | PGE\C7CF | 2017-06-06 16:21:00.7105531 -07:00 | 02412402 |  | 4 | 3 | 3 | 2 | 462 | 3.5 | 3.47 | 462 | 3.5 | 3.47 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 471 | 3.57 | 3.53 | 471 | 3.57 | 3.53 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {21FB0335-46E6-4DFC-8BAF-5A1097B0394F}
8224 | 4776 | {27FAFBFD-EE3A-11E6-BC23-9CB70D532D7F} | PENINSULA | LAS PULGAS | Bank 1 | CB D-E TIE | PGE\C7CF | 2017-06-06 16:21:39.6486523 -07:00 |  |  | 4 | 4 | 4 | 2 | 924 | 6.99 | 6.92 | 924 | 6.99 | 6.92 | 1202 | 9.1 | 9.01 | 1202 | 9.1 | 9.01 | 1109 | 8.39 | 8.31 | 1109 | 8.39 | 8.31 | 1387 | 10.5 | 10.4 | 1387 | 10.5 | 10.4 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {F095C32C-0A97-43C5-8902-C5FCAB5159F3}
8225 | 4775 | {F57A6805-EE39-11E6-BC23-9CB70D532D7F} | PENINSULA | LAS PULGAS | Bank 2 | CB 420 | PGE\C7CF | 2017-06-06 16:22:06.0285905 -07:00 |  |  | 4 | 4 | 4 | 2 | 924 | 6.99 | 6.92 | 924 | 6.99 | 6.92 | 1202 | 9.1 | 9.01 | 1202 | 9.1 | 9.01 | 1109 | 8.39 | 8.31 | 1109 | 8.39 | 8.31 | 1387 | 10.5 | 10.4 | 1387 | 10.5 | 10.4 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {24DF4F9A-C5BA-491A-95CB-9484A372AA81}
8226 | 4775 | {25CD6603-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | LAS PULGAS | Bank 2 | CB 403 | PGE\C7CF | 2017-06-06 16:28:03.5695743 -07:00 | 02412403 |  | 4 | 3 | 3 | 2 | 462 | 3.5 | 3.47 | 462 | 3.5 | 3.47 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 471 | 3.57 | 3.53 | 471 | 3.57 | 3.53 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {0D7B385C-863E-4E6D-A868-5F0C47A1C68F}
8227 | 4775 | {25CD660C-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | LAS PULGAS | Bank 2 | CB 404 | PGE\C7CF | 2017-06-06 16:31:47.4948451 -07:00 | 02412404 |  | 4 | 3 | 3 | 2 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 | 500 | 3.78 | 3.74 |  |  | FALSE | FALSE | 924 | 1202 | 1109 | 1387 | {2055A302-9D00-44CE-B5FC-436D6F2FE7D8}
8228 | 4777 | {2C77C860-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | REDWOOD CITY | Bank 4 | CB 1103 | PGE\C7CF | 2017-06-06 17:36:36.3127011 -07:00 | 024161103 |  | 8 | 3 | 3 | 2 | 458 | 10 | 9.9 | 458 | 10 | 9.9 | 595 | 12.99 | 12.86 | 570 | 12.44 | 12.32 | 549 | 11.98 | 11.86 | 549 | 11.98 | 11.86 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 458 | 595 | 549 | 687 | {31927041-586F-496F-9A13-23C308200E06}
8231 | 4780 | {25CD6662-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MENLO | Bank 2 | CB 403 | PGE\C7CF | 2017-06-08 17:46:16.6752570 -07:00 | 024130403 |  | 4 | 3 | 3 | 2 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 |  |  | FALSE | FALSE | 660 | 858 | 792 | 990 | {5FAA3D33-6036-4510-A5B0-1A08FB5F664D}
8232 | 4780 | {25CD666B-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MENLO | Bank 2 | CB 404 | PGE\C7CF | 2017-06-08 17:48:56.6895855 -07:00 | 024130404 |  | 4 | 3 | 3 | 2 | 365 | 2.76 | 2.73 | 365 | 2.76 | 2.73 | 394 | 2.98 | 2.95 | 380 | 2.88 | 2.85 | 376 | 2.85 | 2.82 | 376 | 2.85 | 2.82 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 |  |  | FALSE | FALSE | 660 | 858 | 792 | 990 | {985FA04E-F4DC-41D4-9DF6-FBCB4A1651A3}
8233 | 4426 | {25CD6648-D1C5-11E5-8ECE-9CB70D532D7F} | PENINSULA | MENLO | Bank 1 | CB 402 | PGE\C7CF | 2017-06-08 17:53:32.2880185 -07:00 | 024130402 |  | 4 | 3 | 3 | 2 | 330 | 2.5 | 2.48 | 330 | 2.5 | 2.48 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 | 396 | 3 | 2.97 | 380 | 2.88 | 2.85 | 400 | 3.03 | 3 | 380 | 2.88 | 2.85 |  |  | FALSE | FALSE | 330 | 429 | 396 | 495 | {BCEFAF8A-AC12-4E7A-8A81-89217839BCC9}
8234 | 4736 | {B12487E3-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | STELLING | Bank 1 | CB 1102 | PGE\MTTA | 2017-06-09 15:23:06.7903588 -07:00 | 0834801102 |  | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1945 | 2380 | 2000 | 2400 | {18EDFC4E-159E-490E-8C78-F541F7028BDC}
8236 | 4736 | {B12487EC-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | STELLING | Bank 1 | CB 1103 | PGE\MTTA | 2017-06-09 15:29:35.8200273 -07:00 | 0834801103 |  | 8 | 3 | 3 | 2 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 527 | 11.5 | 11.39 | 527 | 11.5 | 11.39 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1945 | 2380 | 2000 | 2400 | {CB100744-6032-4DD8-9534-202B3D107931}
8238 | 4736 | {B12487FC-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | STELLING | Bank 1 | CB 1104 | PGE\MTTA | 2017-06-09 15:43:29.8071568 -07:00 | 0834801104 |  | 8 | 3 | 3 | 2 | 517 | 11.28 | 11.17 | 517 | 11.28 | 11.17 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 527 | 11.5 | 11.39 | 527 | 11.5 | 11.39 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1945 | 2380 | 2000 | 2400 | {DA97C6CE-5CF2-4FF3-BB6A-992C94E57283}
8239 | 4736 | {B1248805-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | STELLING | Bank 1 | CB 1105 | PGE\MTTA | 2017-06-09 15:46:48.5263258 -07:00 | 0834801105 |  | 8 | 3 | 3 | 2 | 542 | 11.83 | 11.71 | 542 | 11.83 | 11.71 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 558 | 12.18 | 12.06 | 558 | 12.18 | 12.06 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 1945 | 2380 | 2000 | 2400 | {F6AC1540-A7E1-40B1-BC38-0AFFB0EB5402}
8241 | 4738 | {B1248818-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | STELLING | Bank 2 | CB 1106 | PGE\MTTA | 2017-06-12 14:57:51.5591465 -07:00 | 0834801106 |  | 8 | 3 | 3 | 2 | 467 | 10.19 | 10.09 | 467 | 10.19 | 10.09 | 523 | 11.41 | 11.3 | 523 | 11.41 | 11.3 | 481 | 10.5 | 10.4 | 481 | 10.5 | 10.4 | 539 | 11.76 | 11.64 | 539 | 11.76 | 11.64 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {7B4B7535-02E1-48EC-948C-C23146638B4D}
8242 | 4738 | {B1248821-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | STELLING | Bank 2 | CB 1107 | PGE\MTTA | 2017-06-12 15:04:31.9226793 -07:00 | 0834801107 |  | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {07572A53-D92E-42EE-B1FF-D503E55A58BA}
8243 | 4738 | {B1248831-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | STELLING | Bank 2 | CB 1108 | PGE\MTTA | 2017-06-12 15:24:05.2293215 -07:00 | 0834801108 |  | 8 | 3 | 3 | 2 | 582 | 12.7 | 12.57 | 552 | 12.05 | 11.93 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {13F1065A-FB0B-4CD8-98EF-4CB476D2EFFA}
8244 | 4738 | {B124884F-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | STELLING | Bank 2 | CB 1109 | PGE\MTTA | 2017-06-12 15:47:58.6692987 -07:00 | 0834801109 |  | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 1374 | 1787 | 1649 | 2061 | {3D3668C7-B0CA-48F2-BD1B-D117CAA41171}
8245 | 4778 | {B1248869-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | STELLING | Bank 3 | CB 1110 | PGE\MTTA | 2017-06-12 15:58:37.6846911 -07:00 | 0834801110 |  | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 5533 | 5533 | 5533 | 5533 | {7C607C42-E57C-456B-8771-7561CA2AF92A}
8246 | 4778 | {B12488A4-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | STELLING | Bank 3 | CB 1111 | PGE\MTTA | 2017-06-12 16:05:05.9580689 -07:00 | 0834801111 |  | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 5533 | 5533 | 5533 | 5533 | {383370D0-A8C8-4A3B-B964-A656739C864A}
8247 | 4778 | {B12488C9-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | STELLING | Bank 3 | CB 1112 | PGE\MTTA | 2017-06-12 16:11:19.0368519 -07:00 | 0834801112 |  | 8 | 3 | 3 | 2 | 541 | 11.81 | 11.69 | 541 | 11.81 | 11.69 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 | 557 | 12.16 | 12.04 | 557 | 12.16 | 12.04 | 600 | 13.09 | 12.96 | 570 | 12.44 | 12.32 |  |  | FALSE | FALSE | 5533 | 5533 | 5533 | 5533 | {6B15D3F2-6DB1-4035-A208-24E834708BAB}
8248 | 4778 | {B12488D2-D1CA-11E5-8ECE-9CB70D532D7F} | DE ANZA | STELLING | Bank 3 | CB 1113 | PGE\MTTA | 2017-06-12 16:13:21.9196273 -07:00 | 0834801113 |  | 8 | 3 | 3 | 2 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 5533 | 5533 | 5533 | 5533 | {A60DBBE0-D220-41C9-A8B9-7C7C20FCB137}
8252 | 2298 | {58406D02-671D-11E5-80CA-005056A729E5} | YOSEMITE | MADERA | Bank 1 | CB 1116 | PGE\KRBk | 2017-06-13 10:43:30.5448588 -07:00 | 2527601116 |  | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 | 500 | 10.91 | 10.8 | 475 | 10.37 | 10.27 |  |  | FALSE | FALSE | 916 | 1125 | 1100 | 1200 | {FA3EB4C7-75AB-4B23-876C-63EF4D24DC6D}
8255 | 4034 | {3E1158F3-3CD2-11E7-813B-005056AE4E7D} | MISSION | GRANT | Bank 1 | CB 1101 | PGE\RDR1 | 2017-06-14 14:44:30.3675278 -07:00 |  |  | 7 | 4 | 4 | 2 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | 1200 | 25.92 | 25.66 | Only feeds station capacitor bank (6.0 MVAR) |  | FALSE | FALSE | 2083 | 2640 | 2200 | 2640 | {710BF243-2A5D-4DDC-BE83-CB38D03FB91E}
8257 | 2330 | {A4579886-EB07-11E5-9614-9CB70D532D7F} | CENTRAL COAST | FORT ORD | Bank 2 | CB 2107 | PGE\MTTA | 2017-06-29 10:05:47.5623304 -07:00 | 1824002107 |  | 22 | 3 | 3 | 2 | 201 | 7.23 | 7.16 | 190 | 6.84 | 6.77 | 227 | 8.17 | 8.09 | 215 | 7.74 | 7.66 | 266 | 9.57 | 9.47 | 252 | 9.07 | 8.98 | 284 | 10.22 | 10.12 | 269 | 9.68 | 9.58 |  |  | FALSE | FALSE | 1250 | 1625 | 1500 | 1806 | {73CB98D2-E4C9-449D-B63B-AE96D22F4010}
8258 | 2487 | {599ED463-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | MORRO BAY | Bank 11 | CB 1101 | PGE\MTDR | 2017-07-06 09:52:48.4654595 -07:00 | 183011101 |  | 8 | 4 | 4 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {AF179BF7-B117-4080-8477-95920A59D3C3}
8259 | 2487 | {5FF1BD0C-78EA-11E5-8C7B-9CB70D532D7F} | LOS PADRES | MORRO BAY | Bank 11 | CB 1102 | PGE\MTDR | 2017-07-06 08:46:11.4050709 -07:00 | 1830101102 |  | 8 | 4 | 4 | 2 | 572 | 12.48 | 12.36 | 572 | 12.48 | 12.36 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 |  |  | FALSE | FALSE | 733 | 953 | 879 | 1099 | {F1AD78D0-D59B-46AF-8B83-8776E3C440DC}
8264 | 2407 | {787136BC-9BB6-11E6-841B-D4BED91EFF1A} | CENTRAL COAST | GONZALES | Bank 3 | CB 1101 | PGE\MTDR | 2017-07-10 15:36:04.8589566 -07:00 | 1821301101 |  | 8 | 4 | 4 | 2 | 307 | 6.7 | 6.63 | 307 | 6.7 | 6.63 | 399 | 8.71 | 8.62 | 399 | 8.71 | 8.62 | 368 | 8.03 | 7.95 | 368 | 8.03 | 7.95 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 307 | 399 | 368 | 460 | {23320E1C-EC9D-45B7-8A8B-9158E9146E42}
8265 | 2407 | {A07819A5-9BB6-11E6-841B-D4BED91EFF1A} | CENTRAL COAST | GONZALES | Bank 3 | CB 1102 | PGE\MTDR | 2017-07-10 15:38:16.7898480 -07:00 | 1821301102 |  | 8 | 4 | 4 | 2 | 307 | 6.7 | 6.63 | 307 | 6.7 | 6.63 | 399 | 8.71 | 8.62 | 399 | 8.71 | 8.62 | 368 | 8.03 | 7.95 | 368 | 8.03 | 7.95 | 400 | 8.73 | 8.64 | 400 | 8.73 | 8.64 |  |  | FALSE | FALSE | 307 | 399 | 368 | 460 | {DD047713-4EFA-4176-A80B-52FBC5963406}
8269 | 2395 | {C32EC213-491D-11E6-AFF0-80000BC6CD8D} | YOSEMITE | WISHON | BANK 2 | CB 1101 (Non-SCADA) | PGE\KRBk | 2017-07-12 13:19:35.8104530 -07:00 | 251511101 |  | 8 | 4 | 4 | 2 | 38 | 0.83 | 0.82 | 38 | 0.83 | 0.82 | 38 | 0.83 | 0.82 | 38 | 0.83 | 0.82 | 38 | 0.83 | 0.82 | 38 | 0.83 | 0.82 | 38 | 0.83 | 0.82 | 38 | 0.83 | 0.82 |  |  | FALSE | FALSE | 38 | 38 | 38 | 38 | {DF78430E-AE99-43FC-8369-3F6EB64AD05F}
8270 | 3921 | {0C4778EF-78EA-11E5-8C7B-9CB70D532D7F} | CENTRAL COAST | VIEJO | Bank 2 | CB 2203 | PGE\MTDR | 2017-07-13 09:59:07.4761611 -07:00 | 1828502203 |  | 12 | 4 | 4 | 2 | 515 | 19.46 | 19.27 | 515 | 19.46 | 19.27 | 578 | 21.84 | 21.62 | 578 | 21.84 | 21.62 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 | 600 | 22.68 | 22.45 |  |  | FALSE | FALSE | 793 | 924 | 924 | 924 | {8E28500F-9FCB-451A-8E08-BE8439863713}
8272 | 4454 | {6EF5E075-374B-11E7-813A-005056AE4E7D} | PENINSULA | SF H MARTIN | BANK 4 | CB 1112 | PGE\DSMc | 2017-08-01 10:11:49.3591422 -07:00 | 022101112 |  | 8 | 3 | 3 | 2 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | 600 | 13.09 | 12.96 | UG Conductor 750 CU EPR is install from Martin H 1112 to 400 Paul. |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {3863EF80-6AAB-4FBD-8CEF-214BC6CF6D3E}
8273 | 2294 | {D86AD74E-2F7C-11E7-813A-005056AE4E7D} | YOSEMITE | LE GRAND | Bank 1 | CB 1112 | PGE\SJJ8 | 2017-08-07 15:11:08.6227527 -07:00 | 255361112 |  | 8 | 3 | 3 | 1 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 | 500 | 10.91 | 10.8 |  |  | FALSE | FALSE | 2061 | 2680 | 2474 | 3000 | {8A19C69B-9BAD-43F8-B2D5-D8A845DF6940}

## Sheet1
CedsaId | LENGTH |  |  | Corrected | Copied | LENGTH Corrected
182631104 | 9 |  |  | 182631104 | 182631104 | 9
2520401101 | 10 | 25204 | 1101 | 252041101 | 252041101 | 9
2520401102 | 10 | 25204 | 1102 | 252041102 | 252041102 | 9
2520401103 | 10 | 25204 | 1103 | 252041103 | 252041103 | 9
252041104 | 9 |  |  | 252041104 | 252041104 | 9
1823301101 | 10 | 18233 | 1101 | 182331101 | 182331101 | 9
2520401105 | 10 | 25204 | 1105 | 252041105 | 252041105 | 9
2520401106 | 10 | 25204 | 1106 | 252041106 | 252041106 | 9
252041107 | 9 |  |  | 252041107 | 252041107 | 9
2520401108 | 10 | 25204 | 1108 | 252041108 | 252041108 | 9
2540001103 | 10 | 25400 | 1103 | 254001103 | 254001103 | 9
2540001104 | 10 | 25400 | 1104 | 254001104 | 254001104 | 9
254001105 | 9 |  |  | 254001105 | 254001105 | 9
2540001106 | 10 | 25400 | 1106 | 254001106 | 254001106 | 9
2521501102 | 10 | 25215 | 1102 | 252151102 | 252151102 | 9
2521501103 | 10 | 25215 | 1103 | 252151103 | 252151103 | 9
2521501104 | 10 | 25215 | 1104 | 252151104 | 252151104 | 9
1823301102 | 10 | 18233 | 1102 | 182331102 | 182331102 | 9
2520501102 | 10 | 25205 | 1102 | 252051102 | 252051102 | 9
2520501107 | 10 | 25205 | 1107 | 252051107 | 252051107 | 9
2520501114 | 10 | 25205 | 1114 | 252051114 | 252051114 | 9
2520502105 | 10 | 25205 | 2105 | 252052105 | 252052105 | 9
2520502110 | 10 | 25205 | 2110 | 252052110 | 252052110 | 9
2520502119 | 10 | 25205 | 2119 | 252052119 | 252052119 | 9
2520501103 | 10 | 25205 | 1103 | 252051103 | 252051103 | 9
2520501109 | 10 | 25205 | 1109 | 252051109 | 252051109 | 9
2520501111 | 10 | 25205 | 1111 | 252051111 | 252051111 | 9
2520501112 | 10 | 25205 | 1112 | 252051112 | 252051112 | 9
2520501113 | 10 | 25205 | 1113 | 252051113 | 252051113 | 9
2520502115 | 10 | 25205 | 2115 | 252052115 | 252052115 | 9
2520502117 | 10 | 25205 | 2117 | 252052117 | 252052117 | 9
2520501104 | 10 | 25205 | 1104 | 252051104 | 252051104 | 9
2520501106 | 10 | 25205 | 1106 | 252051106 | 252051106 | 9
2520501108 | 10 | 25205 | 1108 | 252051108 | 252051108 | 9
2520501116 | 10 | 25205 | 1116 | 252051116 | 252051116 | 9
2520502101 | 10 | 25205 | 2101 | 252052101 | 252052101 | 9
2520502118 | 10 | 25205 | 2118 | 252052118 | 252052118 | 9
2541501102 | 10 | 25415 | 1102 | 254151102 | 254151102 | 9
2541501101 | 10 | 25415 | 1101 | 254151101 | 254151101 | 9
2550002101 | 10 | 25500 | 2101 | 255002101 | 255002101 | 9
2525001101 | 10 | 25250 | 1101 | 252501101 | 252501101 | 9
2535701101 | 10 | 25357 | 1101 | 253571101 | 253571101 | 9
2535701102 | 10 | 25357 | 1102 | 253571102 | 253571102 | 9
2535701104 | 10 | 25357 | 1104 | 253571104 | 253571104 | 9
2535701105 | 10 | 25357 | 1105 | 253571105 | 253571105 | 9
2535701106 | 10 | 25357 | 1106 | 253571106 | 253571106 | 9
2535701108 | 10 | 25357 | 1108 | 253571108 | 253571108 | 9
2535701109 | 10 | 25357 | 1109 | 253571109 | 253571109 | 9
2535701110 | 10 | 25357 | 1110 | 253571110 | 253571110 | 9
2535701111 | 10 | 25357 | 1111 | 253571111 | 253571111 | 9
2535701112 | 10 | 25357 | 1112 | 253571112 | 253571112 | 9
2535701114 | 10 | 25357 | 1114 | 253571114 | 253571114 | 9
2535701115 | 10 | 25357 | 1115 | 253571115 | 253571115 | 9
2535701116 | 10 | 25357 | 1116 | 253571116 | 253571116 | 9
2522101101 | 10 | 25221 | 1101 | 252211101 | 252211101 | 9
2522101102 | 10 | 25221 | 1102 | 252211102 | 252211102 | 9
2522101103 | 10 | 25221 | 1103 | 252211103 | 252211103 | 9
2522101104 | 10 | 25221 | 1104 | 252211104 | 252211104 | 9
253961101 | 9 |  |  | 253961101 | 253961101 | 9
2535301101 | 10 | 25353 | 1101 | 253531101 | 253531101 | 9
2535301102 | 10 | 25353 | 1102 | 253531102 | 253531102 | 9
2535301103 | 10 | 25353 | 1103 | 253531103 | 253531103 | 9
2535301104 | 10 | 25353 | 1104 | 253531104 | 253531104 | 9
2539602111 | 10 | 25396 | 2111 | 253962111 | 253962111 | 9
2539602112 | 10 | 25396 | 2112 | 253962112 | 253962112 | 9
2539602114 | 10 | 25396 | 2114 | 253962114 | 253962114 | 9
2539601105 | 10 | 25396 | 1105 | 253961105 | 253961105 | 9
2539601106 | 10 | 25396 | 1106 | 253961106 | 253961106 | 9
2539601107 | 10 | 25396 | 1107 | 253961107 | 253961107 | 9
2539601108 | 10 | 25396 | 1108 | 253961108 | 253961108 | 9
2539601109 | 10 | 25396 | 1109 | 253961109 | 253961109 | 9
2539601110 | 10 | 25396 | 1110 | 253961110 | 253961110 | 9
2539601101 | 10 | 25396 | 1101 | 253961101 | 253961101 | 9
2539601102 | 10 | 25396 | 1102 | 253961102 | 253961102 | 9
2539601103 | 10 | 25396 | 1103 | 253961103 | 253961103 | 9
2539601104 | 10 | 25396 | 1104 | 253961104 | 253961104 | 9
2539601113 | 10 | 25396 | 1113 | 253961113 | 253961113 | 9
2534401101 | 10 | 25344 | 1101 | 253441101 | 253441101 | 9
2534401102 | 10 | 25344 | 1102 | 253441102 | 253441102 | 9
2534401103 | 10 | 25344 | 1103 | 253441103 | 253441103 | 9
2534401104 | 10 | 25344 | 1104 | 253441104 | 253441104 | 9
1826101108 | 10 | 18261 | 1108 | 182611108 | 182611108 | 9
1823801101 | 10 | 18238 | 1101 | 182381101 | 182381101 | 9
1823801103 | 10 | 18238 | 1103 | 182381103 | 182381103 | 9
1920201106 | 10 | 19202 | 1106 | 192021106 | 192021106 | 9
2535901101 | 10 | 25359 | 1101 | 253591101 | 253591101 | 9
1824001101 | 10 | 18240 | 1101 | 182401101 | 182401101 | 9
1824001102 | 10 | 18240 | 1102 | 182401102 | 182401102 | 9
2535901102 | 10 | 25359 | 1102 | 253591102 | 253591102 | 9
1920201123 | 10 | 19202 | 1123 | 192021123 | 192021123 | 9
2535901103 | 10 | 25359 | 1103 | 253591103 | 253591103 | 9
2535901104 | 10 | 25359 | 1104 | 253591104 | 253591104 | 9
2535901105 | 10 | 25359 | 1105 | 253591105 | 253591105 | 9
1525601105 | 10 | 15256 | 1105 | 152561105 | 152561105 | 9
1525601106 | 10 | 15256 | 1106 | 152561106 | 152561106 | 9
1525601107 | 10 | 15256 | 1107 | 152561107 | 152561107 | 9
1524402103 | 10 | 15244 | 2103 | 152442103 | 152442103 | 9
1524402104 | 10 | 15244 | 2104 | 152442104 | 152442104 | 9
2521902101 | 10 | 25219 | 2101 | 252192101 | 252192101 | 9
2521902105 | 10 | 25219 | 2105 | 252192105 | 252192105 | 9
2553901101 | 10 | 25539 | 1101 | 255391101 | 255391101 | 9
2553901102 | 10 | 25539 | 1102 | 255391102 | 255391102 | 9
2553901103 | 10 | 25539 | 1103 | 255391103 | 255391103 | 9
2551201101 | 10 | 25512 | 1101 | 255121101 | 255121101 | 9
2551201102 | 10 | 25512 | 1102 | 255121102 | 255121102 | 9
2551201103 | 10 | 25512 | 1103 | 255121103 | 255121103 | 9
2520901101 | 10 | 25209 | 1101 | 252091101 | 252091101 | 9
2520901104 | 10 | 25209 | 1104 | 252091104 | 252091104 | 9
2520901106 | 10 | 25209 | 1106 | 252091106 | 252091106 | 9
2520901102 | 10 | 25209 | 1102 | 252091102 | 252091102 | 9
2520901103 | 10 | 25209 | 1103 | 252091103 | 252091103 | 9
2520901105 | 10 | 25209 | 1105 | 252091105 | 252091105 | 9
2542702107 | 10 | 25427 | 2107 | 254272107 | 254272107 | 9
2542702108 | 10 | 25427 | 2108 | 254272108 | 254272108 | 9
2541001101 | 10 | 25410 | 1101 | 254101101 | 254101101 | 9
2541001102 | 10 | 25410 | 1102 | 254101102 | 254101102 | 9
2541001103 | 10 | 25410 | 1103 | 254101103 | 254101103 | 9
2541001104 | 10 | 25410 | 1104 | 254101104 | 254101104 | 9
2541001105 | 10 | 25410 | 1105 | 254101105 | 254101105 | 9
2541001106 | 10 | 25410 | 1106 | 254101106 | 254101106 | 9
2544302103 | 10 | 25443 | 2103 | 254432103 | 254432103 | 9
2544302104 | 10 | 25443 | 2104 | 254432104 | 254432104 | 9
1633501701 | 10 | 16335 | 1701 | 163351701 | 163351701 | 9
1633501702 | 10 | 16335 | 1702 | 163351702 | 163351702 | 9
1633501703 | 10 | 16335 | 1703 | 163351703 | 163351703 | 9
1633501704 | 10 | 16335 | 1704 | 163351704 | 163351704 | 9
1633501705 | 10 | 16335 | 1705 | 163351705 | 163351705 | 9
2524201102 | 10 | 25242 | 1102 | 252421102 | 252421102 | 9
2524201105 | 10 | 25242 | 1105 | 252421105 | 252421105 | 9
2524201109 | 10 | 25242 | 1109 | 252421109 | 252421109 | 9
252421111 | 9 |  |  | 252421111 | 252421111 | 9
2524201112 | 10 | 25242 | 1112 | 252421112 | 252421112 | 9
2524201113 | 10 | 25242 | 1113 | 252421113 | 252421113 | 9
1521801101 | 10 | 15218 | 1101 | 152181101 | 152181101 | 9
1521801102 | 10 | 15218 | 1102 | 152181102 | 152181102 | 9
1525701101 | 10 | 15257 | 1101 | 152571101 | 152571101 | 9
1525701102 | 10 | 15257 | 1102 | 152571102 | 152571102 | 9
1525701103 | 10 | 15257 | 1103 | 152571103 | 152571103 | 9
1525701104 | 10 | 15257 | 1104 | 152571104 | 152571104 | 9
1525701105 | 10 | 15257 | 1105 | 152571105 | 152571105 | 9
1525701106 | 10 | 15257 | 1106 | 152571106 | 152571106 | 9
0833302101 | 10 | 08333 | 2101 | 083332101 | 083332101 | 9
1537001101 | 10 | 15370 | 1101 | 153701101 | 153701101 | 9
1537001102 | 10 | 15370 | 1102 | 153701102 | 153701102 | 9
1537002108 | 10 | 15370 | 2108 | 153702108 | 153702108 | 9
1537001104 | 10 | 15370 | 1104 | 153701104 | 153701104 | 9
1537001105 | 10 | 15370 | 1105 | 153701105 | 153701105 | 9
083010401 | 9 |  |  | 083010401 | 083010401 | 9
083010402 | 9 |  |  | 083010402 | 083010402 | 9
083040401 | 9 |  |  | 083040401 | 083040401 | 9
083041101 | 9 |  |  | 083041101 | 083041101 | 9
0143701105 | 10 | 01437 | 1105 | 014371105 | 014371105 | 9
0143701106 | 10 | 01437 | 1106 | 014371106 | 014371106 | 9
1525801103 | 10 | 15258 | 1103 | 152581103 | 152581103 | 9
1525801104 | 10 | 15258 | 1104 | 152581104 | 152581104 | 9
0142601101 | 10 | 01426 | 1101 | 014261101 | 014261101 | 9
0142601102 | 10 | 01426 | 1102 | 014261102 | 014261102 | 9
0142601103 | 10 | 01426 | 1103 | 014261103 | 014261103 | 9
1525802105 | 10 | 15258 | 2105 | 152582105 | 152582105 | 9
1525802106 | 10 | 15258 | 2106 | 152582106 | 152582106 | 9
0143401103 | 10 | 01434 | 1103 | 014341103 | 014341103 | 9
0143401105 | 10 | 01434 | 1105 | 014341105 | 014341105 | 9
0143401106 | 10 | 01434 | 1106 | 014341106 | 014341106 | 9
1525802109 | 10 | 15258 | 2109 | 152582109 | 152582109 | 9
0139201101 | 10 | 01392 | 1101 | 013921101 | 013921101 | 9
0139201102 | 10 | 01392 | 1102 | 013921102 | 013921102 | 9
0139201103 | 10 | 01392 | 1103 | 013921103 | 013921103 | 9
0139201104 | 10 | 01392 | 1104 | 013921104 | 013921104 | 9
1525802110 | 10 | 15258 | 2110 | 152582110 | 152582110 | 9
0125001103 | 10 | 01250 | 1103 | 012501103 | 012501103 | 9
0125001108 | 10 | 01250 | 1108 | 012501108 | 012501108 | 9
0125001109 | 10 | 01250 | 1109 | 012501109 | 012501109 | 9
0125001112 | 10 | 01250 | 1112 | 012501112 | 012501112 | 9
0828401101 | 10 | 08284 | 1101 | 082841101 | 082841101 | 9
0828401102 | 10 | 08284 | 1102 | 082841102 | 082841102 | 9
083050402 | 9 |  |  | 083050402 | 083050402 | 9
1824601101 | 10 | 18246 | 1101 | 182461101 | 182461101 | 9
1824601102 | 10 | 18246 | 1102 | 182461102 | 182461102 | 9
1822601101 | 10 | 18226 | 1101 | 182261101 | 182261101 | 9
1822601102 | 10 | 18226 | 1102 | 182261102 | 182261102 | 9
1822601106 | 10 | 18226 | 1106 | 182261106 | 182261106 | 9
1822601103 | 10 | 18226 | 1103 | 182261103 | 182261103 | 9
1822601104 | 10 | 18226 | 1104 | 182261104 | 182261104 | 9
1835802101 | 10 | 18358 | 2101 | 183582101 | 183582101 | 9
0836202103 | 10 | 08362 | 2103 | 083622103 | 083622103 | 9
0836202104 | 10 | 08362 | 2104 | 083622104 | 083622104 | 9
2522801110 | 10 | 25228 | 1110 | 252281110 | 252281110 | 9
0836202105 | 10 | 08362 | 2105 | 083622105 | 083622105 | 9
2522801113 | 10 | 25228 | 1113 | 252281113 | 252281113 | 9
2522801114 | 10 | 25228 | 1114 | 252281114 | 252281114 | 9
2522801117 | 10 | 25228 | 1117 | 252281117 | 252281117 | 9
2522801106 | 10 | 25228 | 1106 | 252281106 | 252281106 | 9
2522801111 | 10 | 25228 | 1111 | 252281111 | 252281111 | 9
2522801112 | 10 | 25228 | 1112 | 252281112 | 252281112 | 9
2522801116 | 10 | 25228 | 1116 | 252281116 | 252281116 | 9
2522801102 | 10 | 25228 | 1102 | 252281102 | 252281102 | 9
0836202106 | 10 | 08362 | 2106 | 083622106 | 083622106 | 9
2522801103 | 10 | 25228 | 1103 | 252281103 | 252281103 | 9
2522801104 | 10 | 25228 | 1104 | 252281104 | 252281104 | 9
2522801108 | 10 | 25228 | 1108 | 252281108 | 252281108 | 9
2523001103 | 10 | 25230 | 1103 | 252301103 | 252301103 | 9
2523001104 | 10 | 25230 | 1104 | 252301104 | 252301104 | 9
2523001105 | 10 | 25230 | 1105 | 252301105 | 252301105 | 9
2523001102 | 10 | 25230 | 1102 | 252301102 | 252301102 | 9
2523701101 | 10 | 25237 | 1101 | 252371101 | 252371101 | 9
2523701102 | 10 | 25237 | 1102 | 252371102 | 252371102 | 9
1820701101 | 10 | 18207 | 1101 | 182071101 | 182071101 | 9
2523701104 | 10 | 25237 | 1104 | 252371104 | 252371104 | 9
2523701105 | 10 | 25237 | 1105 | 252371105 | 252371105 | 9
182040401 | 9 |  |  | 182040401 | 182040401 | 9
182040402 | 9 |  |  | 182040402 | 182040402 | 9
182040403 | 9 |  |  | 182040403 | 182040403 | 9
2540801101 | 10 | 25408 | 1101 | 254081101 | 254081101 | 9
2540801102 | 10 | 25408 | 1102 | 254081102 | 254081102 | 9
182040405 | 9 |  |  | 182040405 | 182040405 | 9
2540801103 | 10 | 25408 | 1103 | 254081103 | 254081103 | 9
2540801104 | 10 | 25408 | 1104 | 254081104 | 254081104 | 9
083110401 | 9 |  |  | 083110401 | 083110401 | 9
2540801105 | 10 | 25408 | 1105 | 254081105 | 254081105 | 9
1823502103 | 10 | 18235 | 2103 | 182352103 | 182352103 | 9
1823502104 | 10 | 18235 | 2104 | 182352104 | 182352104 | 9
083230401 | 9 |  |  | 083230401 | 083230401 | 9
2540801106 | 10 | 25408 | 1106 | 254081106 | 254081106 | 9
1525601103 | 10 | 15256 | 1103 | 152561103 | 152561103 | 9
083230402 | 9 |  |  | 083230402 | 083230402 | 9
083230403 | 9 |  |  | 083230403 | 083230403 | 9
088820401 | 9 |  |  | 088820401 | 088820401 | 9
2540801107 | 10 | 25408 | 1107 | 254081107 | 254081107 | 9
1822202102 | 10 | 18222 | 2102 | 182222102 | 182222102 | 9
0428601101 | 10 | 04286 | 1101 | 042861101 | 042861101 | 9
1822202103 | 10 | 18222 | 2103 | 182222103 | 182222103 | 9
2540801108 | 10 | 25408 | 1108 | 254081108 | 254081108 | 9
2540802109 | 10 | 25408 | 2109 | 254082109 | 254082109 | 9
1822202104 | 10 | 18222 | 2104 | 182222104 | 182222104 | 9
1822202105 | 10 | 18222 | 2105 | 182222105 | 182222105 | 9
2540802110 | 10 | 25408 | 2110 | 254082110 | 254082110 | 9
182221101 | 9 |  |  | 182221101 | 182221101 | 9
2540802111 | 10 | 25408 | 2111 | 254082111 | 254082111 | 9
1823801104 | 10 | 18238 | 1104 | 182381104 | 182381104 | 9
2521601108 | 10 | 25216 | 1108 | 252161108 | 252161108 | 9
2521601109 | 10 | 25216 | 1109 | 252161109 | 252161109 | 9
083510403 | 9 |  |  | 083510403 | 083510403 | 9
083510404 | 9 |  |  | 083510404 | 083510404 | 9
083140401 | 9 |  |  | 083140401 | 083140401 | 9
192020122 | 9 |  |  | 192020122 | 192020122 | 9
1920201121 | 10 | 19202 | 1121 | 192021121 | 192021121 | 9
1524402107 | 10 | 15244 | 2107 | 152442107 | 152442107 | 9
1524402108 | 10 | 15244 | 2108 | 152442108 | 152442108 | 9
1920201122 | 10 | 19202 | 1122 | 192021122 | 192021122 | 9
2535901106 | 10 | 25359 | 1106 | 253591106 | 253591106 | 9
1524402109 | 10 | 15244 | 2109 | 152442109 | 152442109 | 9
1524402110 | 10 | 15244 | 2110 | 152442110 | 152442110 | 9
1520601101 | 10 | 15206 | 1101 | 152061101 | 152061101 | 9
1520601102 | 10 | 15206 | 1102 | 152061102 | 152061102 | 9
2521601106 | 10 | 25216 | 1106 | 252161106 | 252161106 | 9
2521601107 | 10 | 25216 | 1107 | 252161107 | 252161107 | 9
1520601103 | 10 | 15206 | 1103 | 152061103 | 152061103 | 9
1520601104 | 10 | 15206 | 1104 | 152061104 | 152061104 | 9
022390401 | 9 |  |  | 022390401 | 022390401 | 9
022390402 | 9 |  |  | 022390402 | 022390402 | 9
022670401 | 9 |  |  | 022670401 | 022670401 | 9
2521701112 | 10 | 25217 | 1112 | 252171112 | 252171112 | 9
2521701116 | 10 | 25217 | 1116 | 252171116 | 252171116 | 9
2521701118 | 10 | 25217 | 1118 | 252171118 | 252171118 | 9
2521701104 | 10 | 25217 | 1104 | 252171104 | 252171104 | 9
2521701106 | 10 | 25217 | 1106 | 252171106 | 252171106 | 9
2521701108 | 10 | 25217 | 1108 | 252171108 | 252171108 | 9
2534501101 | 10 | 25345 | 1101 | 253451101 | 253451101 | 9
2534501102 | 10 | 25345 | 1102 | 253451102 | 253451102 | 9
2540901102 | 10 | 25409 | 1102 | 254091102 | 254091102 | 9
2540901104 | 10 | 25409 | 1104 | 254091104 | 254091104 | 9
2540901105 | 10 | 25409 | 1105 | 254091105 | 254091105 | 9
2540901106 | 10 | 25409 | 1106 | 254091106 | 254091106 | 9
2540601102 | 10 | 25406 | 1102 | 254061102 | 254061102 | 9
2540601103 | 10 | 25406 | 1103 | 254061103 | 254061103 | 9
2545502102 | 10 | 25455 | 2102 | 254552102 | 254552102 | 9
2545502103 | 10 | 25455 | 2103 | 254552103 | 254552103 | 9
2545502104 | 10 | 25455 | 2104 | 254552104 | 254552104 | 9
2545502105 | 10 | 25455 | 2105 | 254552105 | 254552105 | 9
0828301104 | 10 | 08283 | 1104 | 082831104 | 082831104 | 9
2545502107 | 10 | 25455 | 2107 | 254552107 | 254552107 | 9
2545502108 | 10 | 25455 | 2108 | 254552108 | 254552108 | 9
2545502109 | 10 | 25455 | 2109 | 254552109 | 254552109 | 9
2545502110 | 10 | 25455 | 2110 | 254552110 | 254552110 | 9
2545502111 | 10 | 25455 | 2111 | 254552111 | 254552111 | 9
2545502112 | 10 | 25455 | 2112 | 254552112 | 254552112 | 9
2545502113 | 10 | 25455 | 2113 | 254552113 | 254552113 | 9
2526601102 | 10 | 25266 | 1102 | 252661102 | 252661102 | 9
2526601104 | 10 | 25266 | 1104 | 252661104 | 252661104 | 9
2526601106 | 10 | 25266 | 1106 | 252661106 | 252661106 | 9
2526601108 | 10 | 25266 | 1108 | 252661108 | 252661108 | 9
0828301106 | 10 | 08283 | 1106 | 082831106 | 082831106 | 9
2526601101 | 10 | 25266 | 1101 | 252661101 | 252661101 | 9
2526601103 | 10 | 25266 | 1103 | 252661103 | 252661103 | 9
2537101101 | 10 | 25371 | 1101 | 253711101 | 253711101 | 9
2537101102 | 10 | 25371 | 1102 | 253711102 | 253711102 | 9
0620801101 | 10 | 06208 | 1101 | 062081101 | 062081101 | 9
0620801102 | 10 | 06208 | 1102 | 062081102 | 062081102 | 9
0620801103 | 10 | 06208 | 1103 | 062081103 | 062081103 | 9
0620801104 | 10 | 06208 | 1104 | 062081104 | 062081104 | 9
2526801106 | 10 | 25268 | 1106 | 252681106 | 252681106 | 9
2526801110 | 10 | 25268 | 1110 | 252681110 | 252681110 | 9
0631201101 | 10 | 06312 | 1101 | 063121101 | 063121101 | 9
2547701101 | 10 | 25477 | 1101 | 254771101 | 254771101 | 9
2547701102 | 10 | 25477 | 1102 | 254771102 | 254771102 | 9
2527001113 | 10 | 25270 | 1113 | 252701113 | 252701113 | 9
2527001114 | 10 | 25270 | 1114 | 252701114 | 252701114 | 9
2527101104 | 10 | 25271 | 1104 | 252711104 | 252711104 | 9
2527101106 | 10 | 25271 | 1106 | 252711106 | 252711106 | 9
2527101108 | 10 | 25271 | 1108 | 252711108 | 252711108 | 9
2527101101 | 10 | 25271 | 1101 | 252711101 | 252711101 | 9
2527101102 | 10 | 25271 | 1102 | 252711102 | 252711102 | 9
2527101103 | 10 | 25271 | 1103 | 252711103 | 252711103 | 9
2527301101 | 10 | 25273 | 1101 | 252731101 | 252731101 | 9
2527302104 | 10 | 25273 | 2104 | 252732104 | 252732104 | 9
2522401102 | 10 | 25224 | 1102 | 252241102 | 252241102 | 9
2522401108 | 10 | 25224 | 1108 | 252241108 | 252241108 | 9
2522401110 | 10 | 25224 | 1110 | 252241110 | 252241110 | 9
2522401116 | 10 | 25224 | 1116 | 252241116 | 252241116 | 9
2522401111 | 10 | 25224 | 1111 | 252241111 | 252241111 | 9
2522401112 | 10 | 25224 | 1112 | 252241112 | 252241112 | 9
2522401113 | 10 | 25224 | 1113 | 252241113 | 252241113 | 9
2522401114 | 10 | 25224 | 1114 | 252241114 | 252241114 | 9
2536001101 | 10 | 25360 | 1101 | 253601101 | 253601101 | 9
2536001103 | 10 | 25360 | 1103 | 253601103 | 253601103 | 9
2536001102 | 10 | 25360 | 1102 | 253601102 | 253601102 | 9
2536001104 | 10 | 25360 | 1104 | 253601104 | 253601104 | 9
2536001105 | 10 | 25360 | 1105 | 253601105 | 253601105 | 9
2542501109 | 10 | 25425 | 1109 | 254251109 | 254251109 | 9
2542501110 | 10 | 25425 | 1110 | 254251110 | 254251110 | 9
2542501111 | 10 | 25425 | 1111 | 254251111 | 254251111 | 9
2542501105 | 10 | 25425 | 1105 | 254251105 | 254251105 | 9
2542501106 | 10 | 25425 | 1106 | 254251106 | 254251106 | 9
2542501107 | 10 | 25425 | 1107 | 254251107 | 254251107 | 9
2542501108 | 10 | 25425 | 1108 | 254251108 | 254251108 | 9
2542501101 | 10 | 25425 | 1101 | 254251101 | 254251101 | 9
2542501102 | 10 | 25425 | 1102 | 254251102 | 254251102 | 9
2542501103 | 10 | 25425 | 1103 | 254251103 | 254251103 | 9
2542501104 | 10 | 25425 | 1104 | 254251104 | 254251104 | 9
2539201101 | 10 | 25392 | 1101 | 253921101 | 253921101 | 9
2539201103 | 10 | 25392 | 1103 | 253921103 | 253921103 | 9
2539201104 | 10 | 25392 | 1104 | 253921104 | 253921104 | 9
2539201107 | 10 | 25392 | 1107 | 253921107 | 253921107 | 9
2539201102 | 10 | 25392 | 1102 | 253921102 | 253921102 | 9
2539201105 | 10 | 25392 | 1105 | 253921105 | 253921105 | 9
2539201106 | 10 | 25392 | 1106 | 253921106 | 253921106 | 9
2539201108 | 10 | 25392 | 1108 | 253921108 | 253921108 | 9
2539201109 | 10 | 25392 | 1109 | 253921109 | 253921109 | 9
2539201110 | 10 | 25392 | 1110 | 253921110 | 253921110 | 9
2539201111 | 10 | 25392 | 1111 | 253921111 | 253921111 | 9
2539201112 | 10 | 25392 | 1112 | 253921112 | 253921112 | 9
2541201101 | 10 | 25412 | 1101 | 254121101 | 254121101 | 9
2541201103 | 10 | 25412 | 1103 | 254121103 | 254121103 | 9
2541201105 | 10 | 25412 | 1105 | 254121105 | 254121105 | 9
2541201107 | 10 | 25412 | 1107 | 254121107 | 254121107 | 9
2541201102 | 10 | 25412 | 1102 | 254121102 | 254121102 | 9
2541201104 | 10 | 25412 | 1104 | 254121104 | 254121104 | 9
2541201106 | 10 | 25412 | 1106 | 254121106 | 254121106 | 9
2544101104 | 10 | 25441 | 1104 | 254411104 | 254411104 | 9
2544101105 | 10 | 25441 | 1105 | 254411105 | 254411105 | 9
2544101106 | 10 | 25441 | 1106 | 254411106 | 254411106 | 9
2528401101 | 10 | 25284 | 1101 | 252841101 | 252841101 | 9
2528401103 | 10 | 25284 | 1103 | 252841103 | 252841103 | 9
2528401102 | 10 | 25284 | 1102 | 252841102 | 252841102 | 9
2528401104 | 10 | 25284 | 1104 | 252841104 | 252841104 | 9
2522901102 | 10 | 25229 | 1102 | 252291102 | 252291102 | 9
2522901103 | 10 | 25229 | 1103 | 252291103 | 252291103 | 9
2522901104 | 10 | 25229 | 1104 | 252291104 | 252291104 | 9
2528502101 | 10 | 25285 | 2101 | 252852101 | 252852101 | 9
2528502102 | 10 | 25285 | 2102 | 252852102 | 252852102 | 9
2528502103 | 10 | 25285 | 2103 | 252852103 | 252852103 | 9
2528502105 | 10 | 25285 | 2105 | 252852105 | 252852105 | 9
2528502106 | 10 | 25285 | 2106 | 252852106 | 252852106 | 9
2528502107 | 10 | 25285 | 2107 | 252852107 | 252852107 | 9
2528502109 | 10 | 25285 | 2109 | 252852109 | 252852109 | 9
2528502110 | 10 | 25285 | 2110 | 252852110 | 252852110 | 9
2528502111 | 10 | 25285 | 2111 | 252852111 | 252852111 | 9
2544401105 | 10 | 25444 | 1105 | 254441105 | 254441105 | 9
2544401106 | 10 | 25444 | 1106 | 254441106 | 254441106 | 9
2523401106 | 10 | 25234 | 1106 | 252341106 | 252341106 | 9
2523401112 | 10 | 25234 | 1112 | 252341112 | 252341112 | 9
2523401101 | 10 | 25234 | 1101 | 252341101 | 252341101 | 9
2523401104 | 10 | 25234 | 1104 | 252341104 | 252341104 | 9
2523401110 | 10 | 25234 | 1110 | 252341110 | 252341110 | 9
254181101 | 9 |  |  | 254181101 | 254181101 | 9
255251101 | 9 |  |  | 255251101 | 255251101 | 9
2523601106 | 10 | 25236 | 1106 | 252361106 | 252361106 | 9
2523601108 | 10 | 25236 | 1108 | 252361108 | 252361108 | 9
2523601112 | 10 | 25236 | 1112 | 252361112 | 252361112 | 9
2523501108 | 10 | 25235 | 1108 | 252351108 | 252351108 | 9
2523501112 | 10 | 25235 | 1112 | 252351112 | 252351112 | 9
2523501114 | 10 | 25235 | 1114 | 252351114 | 252351114 | 9
2523501116 | 10 | 25235 | 1116 | 252351116 | 252351116 | 9
2523501118 | 10 | 25235 | 1118 | 252351118 | 252351118 | 9
2523501104 | 10 | 25235 | 1104 | 252351104 | 252351104 | 9
2523501106 | 10 | 25235 | 1106 | 252351106 | 252351106 | 9
2523501110 | 10 | 25235 | 1110 | 252351110 | 252351110 | 9
2528901104 | 10 | 25289 | 1104 | 252891104 | 252891104 | 9
2528901105 | 10 | 25289 | 1105 | 252891105 | 252891105 | 9
2528901107 | 10 | 25289 | 1107 | 252891107 | 252891107 | 9
2528901108 | 10 | 25289 | 1108 | 252891108 | 252891108 | 9
2528901109 | 10 | 25289 | 1109 | 252891109 | 252891109 | 9
2528901114 | 10 | 25289 | 1114 | 252891114 | 252891114 | 9
2528901116 | 10 | 25289 | 1116 | 252891116 | 252891116 | 9
2528901110 | 10 | 25289 | 1110 | 252891110 | 252891110 | 9
2520602110 | 10 | 25206 | 2110 | 252062110 | 252062110 | 9
2520602111 | 10 | 25206 | 2111 | 252062111 | 252062111 | 9
2520602112 | 10 | 25206 | 2112 | 252062112 | 252062112 | 9
2529201108 | 10 | 25292 | 1108 | 252921108 | 252921108 | 9
2529201109 | 10 | 25292 | 1109 | 252921109 | 252921109 | 9
2529201110 | 10 | 25292 | 1110 | 252921110 | 252921110 | 9
2529501104 | 10 | 25295 | 1104 | 252951104 | 252951104 | 9
2529501106 | 10 | 25295 | 1106 | 252951106 | 252951106 | 9
2545301109 | 10 | 25453 | 1109 | 254531109 | 254531109 | 9
2545301110 | 10 | 25453 | 1110 | 254531110 | 254531110 | 9
2545301111 | 10 | 25453 | 1111 | 254531111 | 254531111 | 9
0431801102 | 10 | 04318 | 1102 | 043181102 | 043181102 | 9
0431801104 | 10 | 04318 | 1104 | 043181104 | 043181104 | 9
2537301101 | 10 | 25373 | 1101 | 253731101 | 253731101 | 9
2537301102 | 10 | 25373 | 1102 | 253731102 | 253731102 | 9
2537301103 | 10 | 25373 | 1103 | 253731103 | 253731103 | 9
2537301104 | 10 | 25373 | 1104 | 253731104 | 253731104 | 9
2537301109 | 10 | 25373 | 1109 | 253731109 | 253731109 | 9
2537301105 | 10 | 25373 | 1105 | 253731105 | 253731105 | 9
2537301106 | 10 | 25373 | 1106 | 253731106 | 253731106 | 9
2537301107 | 10 | 25373 | 1107 | 253731107 | 253731107 | 9
2537301108 | 10 | 25373 | 1108 | 253731108 | 253731108 | 9
2537301110 | 10 | 25373 | 1110 | 253731110 | 253731110 | 9
0431802101 | 10 | 04318 | 2101 | 043182101 | 043182101 | 9
2537301111 | 10 | 25373 | 1111 | 253731111 | 253731111 | 9
2537301112 | 10 | 25373 | 1112 | 253731112 | 253731112 | 9
0431802105 | 10 | 04318 | 2105 | 043182105 | 043182105 | 9
0434901101 | 10 | 04349 | 1101 | 043491101 | 043491101 | 9
0434901102 | 10 | 04349 | 1102 | 043491102 | 043491102 | 9
0434901103 | 10 | 04349 | 1103 | 043491103 | 043491103 | 9
254801101 | 9 |  |  | 254801101 | 254801101 | 9
254912101 | 9 |  |  | 254912101 | 254912101 | 9
2552902101 | 10 | 25529 | 2101 | 255292101 | 255292101 | 9
192361101 | 9 |  |  | 192361101 | 192361101 | 9
2552902102 | 10 | 25529 | 2102 | 255292102 | 255292102 | 9
2552902103 | 10 | 25529 | 2103 | 255292103 | 255292103 | 9
2552902104 | 10 | 25529 | 2104 | 255292104 | 255292104 | 9
1825401101 | 10 | 18254 | 1101 | 182541101 | 182541101 | 9
1825401102 | 10 | 18254 | 1102 | 182541102 | 182541102 | 9
2536101105 | 10 | 25361 | 1105 | 253611105 | 253611105 | 9
2536101106 | 10 | 25361 | 1106 | 253611106 | 253611106 | 9
1825401103 | 10 | 18254 | 1103 | 182541103 | 182541103 | 9
2536101107 | 10 | 25361 | 1107 | 253611107 | 253611107 | 9
2536101108 | 10 | 25361 | 1108 | 253611108 | 253611108 | 9
182801101 | 9 |  |  | 182801101 | 182801101 | 9
1830401101 | 10 | 18304 | 1101 | 183041101 | 183041101 | 9
1830401102 | 10 | 18304 | 1102 | 183041102 | 183041102 | 9
2536101102 | 10 | 25361 | 1102 | 253611102 | 253611102 | 9
2536101103 | 10 | 25361 | 1103 | 253611103 | 253611103 | 9
2536101104 | 10 | 25361 | 1104 | 253611104 | 253611104 | 9
2540401101 | 10 | 25404 | 1101 | 254041101 | 254041101 | 9
2540401102 | 10 | 25404 | 1102 | 254041102 | 254041102 | 9
2538801103 | 10 | 25388 | 1103 | 253881103 | 253881103 | 9
2538801104 | 10 | 25388 | 1104 | 253881104 | 253881104 | 9
2538801102 | 10 | 25388 | 1102 | 253881102 | 253881102 | 9
2538801105 | 10 | 25388 | 1105 | 253881105 | 253881105 | 9
2538801106 | 10 | 25388 | 1106 | 253881106 | 253881106 | 9
2538802109 | 10 | 25388 | 2109 | 253882109 | 253882109 | 9
2538802110 | 10 | 25388 | 2110 | 253882110 | 253882110 | 9
2524501102 | 10 | 25245 | 1102 | 252451102 | 252451102 | 9
2524501104 | 10 | 25245 | 1104 | 252451104 | 252451104 | 9
2524501101 | 10 | 25245 | 1101 | 252451101 | 252451101 | 9
1924601101 | 10 | 19246 | 1101 | 192461101 | 192461101 | 9
2524501103 | 10 | 25245 | 1103 | 252451103 | 252451103 | 9
1924601102 | 10 | 19246 | 1102 | 192461102 | 192461102 | 9
1921801101 | 10 | 19218 | 1101 | 192181101 | 192181101 | 9
1921801102 | 10 | 19218 | 1102 | 192181102 | 192181102 | 9
2539801102 | 10 | 25398 | 1102 | 253981102 | 253981102 | 9
2539801105 | 10 | 25398 | 1105 | 253981105 | 253981105 | 9
2539801106 | 10 | 25398 | 1106 | 253981106 | 253981106 | 9
2534701101 | 10 | 25347 | 1101 | 253471101 | 253471101 | 9
2534701102 | 10 | 25347 | 1102 | 253471102 | 253471102 | 9
1831001103 | 10 | 18310 | 1103 | 183101103 | 183101103 | 9
1831001104 | 10 | 18310 | 1104 | 183101104 | 183101104 | 9
1827701101 | 10 | 18277 | 1101 | 182771101 | 182771101 | 9
1827701102 | 10 | 18277 | 1102 | 182771102 | 182771102 | 9
1825501101 | 10 | 18255 | 1101 | 182551101 | 182551101 | 9
1825501102 | 10 | 18255 | 1102 | 182551102 | 182551102 | 9
2534701103 | 10 | 25347 | 1103 | 253471103 | 253471103 | 9
1631101101 | 10 | 16311 | 1101 | 163111101 | 163111101 | 9
1631101102 | 10 | 16311 | 1102 | 163111102 | 163111102 | 9
2534001101 | 10 | 25340 | 1101 | 253401101 | 253401101 | 9
2534001102 | 10 | 25340 | 1102 | 253401102 | 253401102 | 9
2534001104 | 10 | 25340 | 1104 | 253401104 | 253401104 | 9
2553601104 | 10 | 25536 | 1104 | 255361104 | 255361104 | 9
2553601106 | 10 | 25536 | 1106 | 255361106 | 255361106 | 9
2553601110 | 10 | 25536 | 1110 | 255361110 | 255361110 | 9
0837701101 | 10 | 08377 | 1101 | 083771101 | 083771101 | 9
2522601106 | 10 | 25226 | 1106 | 252261106 | 252261106 | 9
2522601101 | 10 | 25226 | 1101 | 252261101 | 252261101 | 9
0837701102 | 10 | 08377 | 1102 | 083771102 | 083771102 | 9
0837701103 | 10 | 08377 | 1103 | 083771103 | 083771103 | 9
2522601102 | 10 | 25226 | 1102 | 252261102 | 252261102 | 9
0837701104 | 10 | 08377 | 1104 | 083771104 | 083771104 | 9
2527601112 | 10 | 25276 | 1112 | 252761112 | 252761112 | 9
2527601114 | 10 | 25276 | 1114 | 252761114 | 252761114 | 9
2527601102 | 10 | 25276 | 1102 | 252761102 | 252761102 | 9
0837701105 | 10 | 08377 | 1105 | 083771105 | 083771105 | 9
2527601104 | 10 | 25276 | 1104 | 252761104 | 252761104 | 9
2527601106 | 10 | 25276 | 1106 | 252761106 | 252761106 | 9
2527601118 | 10 | 25276 | 1118 | 252761118 | 252761118 | 9
2527601119 | 10 | 25276 | 1119 | 252761119 | 252761119 | 9
2544502101 | 10 | 25445 | 2101 | 254452101 | 254452101 | 9
2544502102 | 10 | 25445 | 2102 | 254452102 | 254452102 | 9
0837701108 | 10 | 08377 | 1108 | 083771108 | 083771108 | 9
2523101101 | 10 | 25231 | 1101 | 252311101 | 252311101 | 9
2523101102 | 10 | 25231 | 1102 | 252311102 | 252311102 | 9
2523101103 | 10 | 25231 | 1103 | 252311103 | 252311103 | 9
2523101104 | 10 | 25231 | 1104 | 252311104 | 252311104 | 9
2528002101 | 10 | 25280 | 2101 | 252802101 | 252802101 | 9
2528002102 | 10 | 25280 | 2102 | 252802102 | 252802102 | 9
2528001108 | 10 | 25280 | 1108 | 252801108 | 252801108 | 9
2528001114 | 10 | 25280 | 1114 | 252801114 | 252801114 | 9
2528001116 | 10 | 25280 | 1116 | 252801116 | 252801116 | 9
012670401 | 9 |  |  | 012670401 | 012670401 | 9
1636601701 | 10 | 16366 | 1701 | 163661701 | 163661701 | 9
1636601702 | 10 | 16366 | 1702 | 163661702 | 163661702 | 9
2544601111 | 10 | 25446 | 1111 | 254461111 | 254461111 | 9
013030401 | 9 |  |  | 013030401 | 013030401 | 9
2544601109 | 10 | 25446 | 1109 | 254461109 | 254461109 | 9
013030402 | 9 |  |  | 013030402 | 013030402 | 9
1627401105 | 10 | 16274 | 1105 | 162741105 | 162741105 | 9
1627401106 | 10 | 16274 | 1106 | 162741106 | 162741106 | 9
013020401 | 9 |  |  | 013020401 | 013020401 | 9
2544201101 | 10 | 25442 | 1101 | 254421101 | 254421101 | 9
013020402 | 9 |  |  | 013020402 | 013020402 | 9
2544201102 | 10 | 25442 | 1102 | 254421102 | 254421102 | 9
1825601101 | 10 | 18256 | 1101 | 182561101 | 182561101 | 9
2544201103 | 10 | 25442 | 1103 | 254421103 | 254421103 | 9
255371106 | 9 |  |  | 255371106 | 255371106 | 9
255371108 | 9 |  |  | 255371108 | 255371108 | 9
012640401 | 9 |  |  | 012640401 | 012640401 | 9
255371110 | 9 |  |  | 255371110 | 255371110 | 9
255371112 | 9 |  |  | 255371112 | 255371112 | 9
1825602102 | 10 | 18256 | 2102 | 182562102 | 182562102 | 9
1631301101 | 10 | 16313 | 1101 | 163131101 | 163131101 | 9
1631301102 | 10 | 16313 | 1102 | 163131102 | 163131102 | 9
2553701115 | 10 | 25537 | 1115 | 255371115 | 255371115 | 9
2553701116 | 10 | 25537 | 1116 | 255371116 | 255371116 | 9
2553701117 | 10 | 25537 | 1117 | 255371117 | 255371117 | 9
1831101101 | 10 | 18311 | 1101 | 183111101 | 183111101 | 9
012650402 | 9 |  |  | 012650402 | 012650402 | 9
1824002105 | 10 | 18240 | 2105 | 182402105 | 182402105 | 9
012690401 | 9 |  |  | 012690401 | 012690401 | 9
013170401 | 9 |  |  | 013170401 | 013170401 | 9
1824002106 | 10 | 18240 | 2106 | 182402106 | 182402106 | 9
013520401 | 9 |  |  | 013520401 | 013520401 | 9
1824002108 | 10 | 18240 | 2108 | 182402108 | 182402108 | 9
012330401 | 9 |  |  | 012330401 | 012330401 | 9
012330403 | 9 |  |  | 012330403 | 012330403 | 9
012600401 | 9 |  |  | 012600401 | 012600401 | 9
0120101109 | 10 | 01201 | 1109 | 012011109 | 012011109 | 9
0120101113 | 10 | 01201 | 1113 | 012011113 | 012011113 | 9
0120101114 | 10 | 01201 | 1114 | 012011114 | 012011114 | 9
0120101115 | 10 | 01201 | 1115 | 012011115 | 012011115 | 9
0120101117 | 10 | 01201 | 1117 | 012011117 | 012011117 | 9
1635601101 | 10 | 16356 | 1101 | 163561101 | 163561101 | 9
1635601102 | 10 | 16356 | 1102 | 163561102 | 163561102 | 9
0426301105 | 10 | 04263 | 1105 | 042631105 | 042631105 | 9
0426301106 | 10 | 04263 | 1106 | 042631106 | 042631106 | 9
0426301108 | 10 | 04263 | 1108 | 042631108 | 042631108 | 9
012011119 | 9 |  |  | 012011119 | 012011119 | 9
2553701118 | 10 | 25537 | 1118 | 255371118 | 255371118 | 9
1831101102 | 10 | 18311 | 1102 | 183111102 | 183111102 | 9
2543101105 | 10 | 25431 | 1105 | 254311105 | 254311105 | 9
2543101106 | 10 | 25431 | 1106 | 254311106 | 254311106 | 9
163130401 | 9 |  |  | 163130401 | 163130401 | 9
1637801701 | 10 | 16378 | 1701 | 163781701 | 163781701 | 9
163130402 | 9 |  |  | 163130402 | 163130402 | 9
1637801704 | 10 | 16378 | 1704 | 163781704 | 163781704 | 9
1637801705 | 10 | 16378 | 1705 | 163781705 | 163781705 | 9
1637601703 | 10 | 16376 | 1703 | 163761703 | 163761703 | 9
1637601704 | 10 | 16376 | 1704 | 163761704 | 163761704 | 9
0139101101 | 10 | 01391 | 1101 | 013911101 | 013911101 | 9
0139101102 | 10 | 01391 | 1102 | 013911102 | 013911102 | 9
1631901713 | 10 | 16319 | 1713 | 163191713 | 163191713 | 9
1631901715 | 10 | 16319 | 1715 | 163191715 | 163191715 | 9
1631901716 | 10 | 16319 | 1716 | 163191716 | 163191716 | 9
2525301101 | 10 | 25253 | 1101 | 252531101 | 252531101 | 9
2525301102 | 10 | 25253 | 1102 | 252531102 | 252531102 | 9
2525301103 | 10 | 25253 | 1103 | 252531103 | 252531103 | 9
2540501101 | 10 | 25405 | 1101 | 254051101 | 254051101 | 9
2540501104 | 10 | 25405 | 1104 | 254051104 | 254051104 | 9
2535401102 | 10 | 25354 | 1102 | 253541102 | 253541102 | 9
2535401105 | 10 | 25354 | 1105 | 253541105 | 253541105 | 9
1630701101 | 10 | 16307 | 1101 | 163071101 | 163071101 | 9
1630701102 | 10 | 16307 | 1102 | 163071102 | 163071102 | 9
1636501101 | 10 | 16365 | 1101 | 163651101 | 163651101 | 9
1636501102 | 10 | 16365 | 1102 | 163651102 | 163651102 | 9
0430801101 | 10 | 04308 | 1101 | 043081101 | 043081101 | 9
1622301101 | 10 | 16223 | 1101 | 162231101 | 162231101 | 9
0422701102 | 10 | 04227 | 1102 | 042271102 | 042271102 | 9
1622301102 | 10 | 16223 | 1102 | 162231102 | 162231102 | 9
0422701103 | 10 | 04227 | 1103 | 042271103 | 042271103 | 9
1629901101 | 10 | 16299 | 1101 | 162991101 | 162991101 | 9
1633001104 | 10 | 16330 | 1104 | 163301104 | 163301104 | 9
1629901103 | 10 | 16299 | 1103 | 162991103 | 162991103 | 9
0422701104 | 10 | 04227 | 1104 | 042271104 | 042271104 | 9
0422701105 | 10 | 04227 | 1105 | 042271105 | 042271105 | 9
1629901102 | 10 | 16299 | 1102 | 162991102 | 162991102 | 9
0434101101 | 10 | 04341 | 1101 | 043411101 | 043411101 | 9
0434101102 | 10 | 04341 | 1102 | 043411102 | 043411102 | 9
1628301701 | 10 | 16283 | 1701 | 162831701 | 162831701 | 9
2546101104 | 10 | 25461 | 1104 | 254611104 | 254611104 | 9
2546101105 | 10 | 25461 | 1105 | 254611105 | 254611105 | 9
2546101106 | 10 | 25461 | 1106 | 254611106 | 254611106 | 9
2546101107 | 10 | 25461 | 1107 | 254611107 | 254611107 | 9
2546101108 | 10 | 25461 | 1108 | 254611108 | 254611108 | 9
2546101109 | 10 | 25461 | 1109 | 254611109 | 254611109 | 9
2546101111 | 10 | 25461 | 1111 | 254611111 | 254611111 | 9
1629801702 | 10 | 16298 | 1702 | 162981702 | 162981702 | 9
1629801703 | 10 | 16298 | 1703 | 162981703 | 162981703 | 9
1629801704 | 10 | 16298 | 1704 | 162981704 | 162981704 | 9
1626701101 | 10 | 16267 | 1101 | 162671101 | 162671101 | 9
162671102 | 9 |  |  | 162671102 | 162671102 | 9
1626701103 | 10 | 16267 | 1103 | 162671103 | 162671103 | 9
1922901121 | 10 | 19229 | 1121 | 192291121 | 192291121 | 9
0421401101 | 10 | 04214 | 1101 | 042141101 | 042141101 | 9
0421401102 | 10 | 04214 | 1102 | 042141102 | 042141102 | 9
0428201101 | 10 | 04282 | 1101 | 042821101 | 042821101 | 9
2543001101 | 10 | 25430 | 1101 | 254301101 | 254301101 | 9
0428201102 | 10 | 04282 | 1102 | 042821102 | 042821102 | 9
2543001102 | 10 | 25430 | 1102 | 254301102 | 254301102 | 9
2543001103 | 10 | 25430 | 1103 | 254301103 | 254301103 | 9
012660401 | 9 |  |  | 012660401 | 012660401 | 9
012660404 | 9 |  |  | 012660404 | 012660404 | 9
012660402 | 9 |  |  | 012660402 | 012660402 | 9
1633001105 | 10 | 16330 | 1105 | 163301105 | 163301105 | 9
1633001106 | 10 | 16330 | 1106 | 163301106 | 163301106 | 9
012660403 | 9 |  |  | 012660403 | 012660403 | 9
2535601101 | 10 | 25356 | 1101 | 253561101 | 253561101 | 9
2535601102 | 10 | 25356 | 1102 | 253561102 | 253561102 | 9
2535601103 | 10 | 25356 | 1103 | 253561103 | 253561103 | 9
013210401 | 9 |  |  | 013210401 | 013210401 | 9
0430701102 | 10 | 04307 | 1102 | 043071102 | 043071102 | 9
0430701103 | 10 | 04307 | 1103 | 043071103 | 043071103 | 9
0430701101 | 10 | 04307 | 1101 | 043071101 | 043071101 | 9
0136801101 | 10 | 01368 | 1101 | 013681101 | 013681101 | 9
0136801103 | 10 | 01368 | 1103 | 013681103 | 013681103 | 9
0136801104 | 10 | 01368 | 1104 | 013681104 | 013681104 | 9
0136801105 | 10 | 01368 | 1105 | 013681105 | 013681105 | 9
1923801102 | 10 | 19238 | 1102 | 192381102 | 192381102 | 9
0136801110 | 10 | 01368 | 1110 | 013681110 | 013681110 | 9
1923801103 | 10 | 19238 | 1103 | 192381103 | 192381103 | 9
0136801111 | 10 | 01368 | 1111 | 013681111 | 013681111 | 9
0136801112 | 10 | 01368 | 1112 | 013681112 | 013681112 | 9
0136801113 | 10 | 01368 | 1113 | 013681113 | 013681113 | 9
0136801114 | 10 | 01368 | 1114 | 013681114 | 013681114 | 9
0136801115 | 10 | 01368 | 1115 | 013681115 | 013681115 | 9
1921701101 | 10 | 19217 | 1101 | 192171101 | 192171101 | 9
1921701102 | 10 | 19217 | 1102 | 192171102 | 192171102 | 9
2525201103 | 10 | 25252 | 1103 | 252521103 | 252521103 | 9
1921701103 | 10 | 19217 | 1103 | 192171103 | 192171103 | 9
0426601102 | 10 | 04266 | 1102 | 042661102 | 042661102 | 9
0426601103 | 10 | 04266 | 1103 | 042661103 | 042661103 | 9
0426601104 | 10 | 04266 | 1104 | 042661104 | 042661104 | 9
0426301101 | 10 | 04263 | 1101 | 042631101 | 042631101 | 9
0426301102 | 10 | 04263 | 1102 | 042631102 | 042631102 | 9
2524101104 | 10 | 25241 | 1104 | 252411104 | 252411104 | 9
2524101106 | 10 | 25241 | 1106 | 252411106 | 252411106 | 9
252411110 | 9 |  |  | 252411110 | 252411110 | 9
2524101112 | 10 | 25241 | 1112 | 252411112 | 252411112 | 9
2523801104 | 10 | 25238 | 1104 | 252381104 | 252381104 | 9
2523801105 | 10 | 25238 | 1105 | 252381105 | 252381105 | 9
2523801106 | 10 | 25238 | 1106 | 252381106 | 252381106 | 9
2523801107 | 10 | 25238 | 1107 | 252381107 | 252381107 | 9
012650401 | 9 |  |  | 012650401 | 012650401 | 9
1821301101 | 10 | 18213 | 1101 | 182131101 | 182131101 | 9
1821301102 | 10 | 18213 | 1102 | 182131102 | 182131102 | 9
1821301103 | 10 | 18213 | 1103 | 182131103 | 182131103 | 9
1821301104 | 10 | 18213 | 1104 | 182131104 | 182131104 | 9
0831902102 | 10 | 08319 | 2102 | 083192102 | 083192102 | 9
0831902103 | 10 | 08319 | 2103 | 083192103 | 083192103 | 9
0131101101 | 10 | 01311 | 1101 | 013111101 | 013111101 | 9
0831902101 | 10 | 08319 | 2101 | 083192101 | 083192101 | 9
0831902104 | 10 | 08319 | 2104 | 083192104 | 083192104 | 9
0120101134 | 10 | 01201 | 1134 | 012011134 | 012011134 | 9
0120101108 | 10 | 01201 | 1108 | 012011108 | 012011108 | 9
012011111 | 9 |  |  | 012011111 | 012011111 | 9
0426301109 | 10 | 04263 | 1109 | 042631109 | 042631109 | 9
0426301110 | 10 | 04263 | 1110 | 042631110 | 042631110 | 9
1822901101 | 10 | 18229 | 1101 | 182291101 | 182291101 | 9
1822901102 | 10 | 18229 | 1102 | 182291102 | 182291102 | 9
1824902101 | 10 | 18249 | 2101 | 182492101 | 182492101 | 9
1824902102 | 10 | 18249 | 2102 | 182492102 | 182492102 | 9
012011118 | 9 |  |  | 012011118 | 012011118 | 9
0421501101 | 10 | 04215 | 1101 | 042151101 | 042151101 | 9
0421501102 | 10 | 04215 | 1102 | 042151102 | 042151102 | 9
0421501103 | 10 | 04215 | 1103 | 042151103 | 042151103 | 9
0421501104 | 10 | 04215 | 1104 | 042151104 | 042151104 | 9
0421501105 | 10 | 04215 | 1105 | 042151105 | 042151105 | 9
0421501106 | 10 | 04215 | 1106 | 042151106 | 042151106 | 9
0421501107 | 10 | 04215 | 1107 | 042151107 | 042151107 | 9
0421501108 | 10 | 04215 | 1108 | 042151108 | 042151108 | 9
0421501109 | 10 | 04215 | 1109 | 042151109 | 042151109 | 9
0421501110 | 10 | 04215 | 1110 | 042151110 | 042151110 | 9
0421501111 | 10 | 04215 | 1111 | 042151111 | 042151111 | 9
2546001103 | 10 | 25460 | 1103 | 254601103 | 254601103 | 9
0421501112 | 10 | 04215 | 1112 | 042151112 | 042151112 | 9
1631901711 | 10 | 16319 | 1711 | 163191711 | 163191711 | 9
1631901712 | 10 | 16319 | 1712 | 163191712 | 163191712 | 9
1631901714 | 10 | 16319 | 1714 | 163191714 | 163191714 | 9
1820601103 | 10 | 18206 | 1103 | 182061103 | 182061103 | 9
1820601104 | 10 | 18206 | 1104 | 182061104 | 182061104 | 9
1820601106 | 10 | 18206 | 1106 | 182061106 | 182061106 | 9
1820601107 | 10 | 18206 | 1107 | 182061107 | 182061107 | 9
1820601108 | 10 | 18206 | 1108 | 182061108 | 182061108 | 9
2526901104 | 10 | 25269 | 1104 | 252691104 | 252691104 | 9
1829501101 | 10 | 18295 | 1101 | 182951101 | 182951101 | 9
1632501101 | 10 | 16325 | 1101 | 163251101 | 163251101 | 9
1632501102 | 10 | 16325 | 1102 | 163251102 | 163251102 | 9
1829501102 | 10 | 18295 | 1102 | 182951102 | 182951102 | 9
2544302102 | 10 | 25443 | 2102 | 254432102 | 254432102 | 9
2547002103 | 10 | 25470 | 2103 | 254702103 | 254702103 | 9
0143501103 | 10 | 01435 | 1103 | 014351103 | 014351103 | 9
2547002104 | 10 | 25470 | 2104 | 254702104 | 254702104 | 9
0143501104 | 10 | 01435 | 1104 | 014351104 | 014351104 | 9
0143501105 | 10 | 01435 | 1105 | 014351105 | 014351105 | 9
0627201101 | 10 | 06272 | 1101 | 062721101 | 062721101 | 9
0627201102 | 10 | 06272 | 1102 | 062721102 | 062721102 | 9
0433002102 | 10 | 04330 | 2102 | 043302102 | 043302102 | 9
0433002103 | 10 | 04330 | 2103 | 043302103 | 043302103 | 9
0433001104 | 10 | 04330 | 1104 | 043301104 | 043301104 | 9
0433001105 | 10 | 04330 | 1105 | 043301105 | 043301105 | 9
0433001106 | 10 | 04330 | 1106 | 043301106 | 043301106 | 9
0433002107 | 10 | 04330 | 2107 | 043302107 | 043302107 | 9
0433601101 | 10 | 04336 | 1101 | 043361101 | 043361101 | 9
0433601102 | 10 | 04336 | 1102 | 043361102 | 043361102 | 9
0433601103 | 10 | 04336 | 1103 | 043361103 | 043361103 | 9
0433601104 | 10 | 04336 | 1104 | 043361104 | 043361104 | 9
0631701103 | 10 | 06317 | 1103 | 063171103 | 063171103 | 9
0631701105 | 10 | 06317 | 1105 | 063171105 | 063171105 | 9
0427601101 | 10 | 04276 | 1101 | 042761101 | 042761101 | 9
0427601102 | 10 | 04276 | 1102 | 042761102 | 042761102 | 9
0631702101 | 10 | 06317 | 2101 | 063172101 | 063172101 | 9
0427601103 | 10 | 04276 | 1103 | 042761103 | 042761103 | 9
0427601104 | 10 | 04276 | 1104 | 042761104 | 042761104 | 9
0638001101 | 10 | 06380 | 1101 | 063801101 | 063801101 | 9
0638001102 | 10 | 06380 | 1102 | 063801102 | 063801102 | 9
0638001103 | 10 | 06380 | 1103 | 063801103 | 063801103 | 9
0433701101 | 10 | 04337 | 1101 | 043371101 | 043371101 | 9
0433701102 | 10 | 04337 | 1102 | 043371102 | 043371102 | 9
0638001104 | 10 | 06380 | 1104 | 063801104 | 063801104 | 9
0638001105 | 10 | 06380 | 1105 | 063801105 | 063801105 | 9
0425601101 | 10 | 04256 | 1101 | 042561101 | 042561101 | 9
0425601102 | 10 | 04256 | 1102 | 042561102 | 042561102 | 9
0425601103 | 10 | 04256 | 1103 | 042561103 | 042561103 | 9
0425601104 | 10 | 04256 | 1104 | 042561104 | 042561104 | 9
0425601105 | 10 | 04256 | 1105 | 042561105 | 042561105 | 9
0425601106 | 10 | 04256 | 1106 | 042561106 | 042561106 | 9
0425601107 | 10 | 04256 | 1107 | 042561107 | 042561107 | 9
0625401101 | 10 | 06254 | 1101 | 062541101 | 062541101 | 9
0620201101 | 10 | 06202 | 1101 | 062021101 | 062021101 | 9
0620201103 | 10 | 06202 | 1103 | 062021103 | 062021103 | 9
0620201104 | 10 | 06202 | 1104 | 062021104 | 062021104 | 9
0620201105 | 10 | 06202 | 1105 | 062021105 | 062021105 | 9
0627001101 | 10 | 06270 | 1101 | 062701101 | 062701101 | 9
0627001102 | 10 | 06270 | 1102 | 062701102 | 062701102 | 9
0620701101 | 10 | 06207 | 1101 | 062071101 | 062071101 | 9
0638101101 | 10 | 06381 | 1101 | 063811101 | 063811101 | 9
0631901107 | 10 | 06319 | 1107 | 063191107 | 063191107 | 9
0631901105 | 10 | 06319 | 1105 | 063191105 | 063191105 | 9
0631901106 | 10 | 06319 | 1106 | 063191106 | 063191106 | 9
0625401102 | 10 | 06254 | 1102 | 062541102 | 062541102 | 9
2549001101 | 10 | 25490 | 1101 | 254901101 | 254901101 | 9
2549001102 | 10 | 25490 | 1102 | 254901102 | 254901102 | 9
1633001101 | 10 | 16330 | 1101 | 163301101 | 163301101 | 9
1824902103 | 10 | 18249 | 2103 | 182492103 | 182492103 | 9
1633001102 | 10 | 16330 | 1102 | 163301102 | 163301102 | 9
1633001103 | 10 | 16330 | 1103 | 163301103 | 163301103 | 9
1824902104 | 10 | 18249 | 2104 | 182492104 | 182492104 | 9
1824902105 | 10 | 18249 | 2105 | 182492105 | 182492105 | 9
1633001108 | 10 | 16330 | 1108 | 163301108 | 163301108 | 9
1824902106 | 10 | 18249 | 2106 | 182492106 | 182492106 | 9
1633001109 | 10 | 16330 | 1109 | 163301109 | 163301109 | 9
0429801101 | 10 | 04298 | 1101 | 042981101 | 042981101 | 9
182300411 | 9 |  |  | 182300411 | 182300411 | 9
0621301101 | 10 | 06213 | 1101 | 062131101 | 062131101 | 9
0621301102 | 10 | 06213 | 1102 | 062131102 | 062131102 | 9
1921201103 | 10 | 19212 | 1103 | 192121103 | 192121103 | 9
182300412 | 9 |  |  | 182300412 | 182300412 | 9
0621301103 | 10 | 06213 | 1103 | 062131103 | 062131103 | 9
182300413 | 9 |  |  | 182300413 | 182300413 | 9
182300415 | 9 |  |  | 182300415 | 182300415 | 9
1825801105 | 10 | 18258 | 1105 | 182581105 | 182581105 | 9
182581107 | 9 |  |  | 182581107 | 182581107 | 9
0621301104 | 10 | 06213 | 1104 | 062131104 | 062131104 | 9
182581108 | 9 |  |  | 182581108 | 182581108 | 9
0621301105 | 10 | 06213 | 1105 | 062131105 | 062131105 | 9
0621301106 | 10 | 06213 | 1106 | 062131106 | 062131106 | 9
0621301107 | 10 | 06213 | 1107 | 062131107 | 062131107 | 9
1828201101 | 10 | 18282 | 1101 | 182821101 | 182821101 | 9
1828201102 | 10 | 18282 | 1102 | 182821102 | 182821102 | 9
1828201103 | 10 | 18282 | 1103 | 182821103 | 182821103 | 9
0621301108 | 10 | 06213 | 1108 | 062131108 | 062131108 | 9
1826001104 | 10 | 18260 | 1104 | 182601104 | 182601104 | 9
1826001106 | 10 | 18260 | 1106 | 182601106 | 182601106 | 9
1637202104 | 10 | 16372 | 2104 | 163722104 | 163722104 | 9
0621301109 | 10 | 06213 | 1109 | 062131109 | 062131109 | 9
1826001108 | 10 | 18260 | 1108 | 182601108 | 182601108 | 9
1637202105 | 10 | 16372 | 2105 | 163722105 | 163722105 | 9
0621301110 | 10 | 06213 | 1110 | 062131110 | 062131110 | 9
1829801102 | 10 | 18298 | 1102 | 182981102 | 182981102 | 9
012011120 | 9 |  |  | 012011120 | 012011120 | 9
0120101132 | 10 | 01201 | 1132 | 012011132 | 012011132 | 9
0621301112 | 10 | 06213 | 1112 | 062131112 | 062131112 | 9
0621301111 | 10 | 06213 | 1111 | 062131111 | 062131111 | 9
1826001101 | 10 | 18260 | 1101 | 182601101 | 182601101 | 9
0120101133 | 10 | 01201 | 1133 | 012011133 | 012011133 | 9
1826001102 | 10 | 18260 | 1102 | 182601102 | 182601102 | 9
1826001103 | 10 | 18260 | 1103 | 182601103 | 182601103 | 9
1826001105 | 10 | 18260 | 1105 | 182601105 | 182601105 | 9
013180401 | 9 |  |  | 013180401 | 013180401 | 9
1820301105 | 10 | 18203 | 1105 | 182031105 | 182031105 | 9
1820301106 | 10 | 18203 | 1106 | 182031106 | 182031106 | 9
012520401 | 9 |  |  | 012520401 | 012520401 | 9
012520402 | 9 |  |  | 012520402 | 012520402 | 9
012840401 | 9 |  |  | 012840401 | 012840401 | 9
012840402 | 9 |  |  | 012840402 | 012840402 | 9
013310401 | 9 |  |  | 013310401 | 013310401 | 9
013310402 | 9 |  |  | 013310402 | 013310402 | 9
013140402 | 9 |  |  | 013140402 | 013140402 | 9
013840401 | 9 |  |  | 013840401 | 013840401 | 9
013840402 | 9 |  |  | 013840402 | 013840402 | 9
013840403 | 9 |  |  | 013840403 | 013840403 | 9
013840404 | 9 |  |  | 013840404 | 013840404 | 9
013840405 | 9 |  |  | 013840405 | 013840405 | 9
013840406 | 9 |  |  | 013840406 | 013840406 | 9
0146701101 | 10 | 01467 | 1101 | 014671101 | 014671101 | 9
0146701102 | 10 | 01467 | 1102 | 014671102 | 014671102 | 9
0146701103 | 10 | 01467 | 1103 | 014671103 | 014671103 | 9
43182103 | 8 |  |  | 043182103 | 043182103 | 9
1637202107 | 10 | 16372 | 2107 | 163722107 | 163722107 | 9
1637202108 | 10 | 16372 | 2108 | 163722108 | 163722108 | 9
42751111 | 8 |  |  | 042751111 | 042751111 | 9
42751112 | 8 |  |  | 042751112 | 042751112 | 9
42751113 | 8 |  |  | 042751113 | 042751113 | 9
0428901101 | 10 | 04289 | 1101 | 042891101 | 042891101 | 9
0428901102 | 10 | 04289 | 1102 | 042891102 | 042891102 | 9
013780401 | 9 |  |  | 013780401 | 013780401 | 9
0420901101 | 10 | 04209 | 1101 | 042091101 | 042091101 | 9
1637202110 | 10 | 16372 | 2110 | 163722110 | 163722110 | 9
1637202111 | 10 | 16372 | 2111 | 163722111 | 163722111 | 9
013350401 | 9 |  |  | 013350401 | 013350401 | 9
0420901102 | 10 | 04209 | 1102 | 042091102 | 042091102 | 9
013350402 | 9 |  |  | 013350402 | 013350402 | 9
013740401 | 9 |  |  | 013740401 | 013740401 | 9
0425701101 | 10 | 04257 | 1101 | 042571101 | 042571101 | 9
013380401 | 9 |  |  | 013380401 | 013380401 | 9
0829501101 | 10 | 08295 | 1101 | 082951101 | 082951101 | 9
0425701102 | 10 | 04257 | 1102 | 042571102 | 042571102 | 9
0425701103 | 10 | 04257 | 1103 | 042571103 | 042571103 | 9
0425701104 | 10 | 04257 | 1104 | 042571104 | 042571104 | 9
0428101111 | 10 | 04281 | 1111 | 042811111 | 042811111 | 9
0428101112 | 10 | 04281 | 1112 | 042811112 | 042811112 | 9
0428101113 | 10 | 04281 | 1113 | 042811113 | 042811113 | 9
0120401103 | 10 | 01204 | 1103 | 012041103 | 012041103 | 9
0829501102 | 10 | 08295 | 1102 | 082951102 | 082951102 | 9
0120401117 | 10 | 01204 | 1117 | 012041117 | 012041117 | 9
0120401104 | 10 | 01204 | 1104 | 012041104 | 012041104 | 9
0120401105 | 10 | 01204 | 1105 | 012041105 | 012041105 | 9
43471101 | 8 |  |  | 043471101 | 043471101 | 9
0120401106 | 10 | 01204 | 1106 | 012041106 | 012041106 | 9
0120401107 | 10 | 01204 | 1107 | 012041107 | 012041107 | 9
0120401110 | 10 | 01204 | 1110 | 012041110 | 012041110 | 9
1923901101 | 10 | 19239 | 1101 | 192391101 | 192391101 | 9
1923901102 | 10 | 19239 | 1102 | 192391102 | 192391102 | 9
0120401115 | 10 | 01204 | 1115 | 012041115 | 012041115 | 9
0120401101 | 10 | 01204 | 1101 | 012041101 | 012041101 | 9
0427201102 | 10 | 04272 | 1102 | 042721102 | 042721102 | 9
0120401102 | 10 | 01204 | 1102 | 012041102 | 012041102 | 9
0120401111 | 10 | 01204 | 1111 | 012041111 | 012041111 | 9
0120401112 | 10 | 01204 | 1112 | 012041112 | 012041112 | 9
0120401116 | 10 | 01204 | 1116 | 012041116 | 012041116 | 9
0427201103 | 10 | 04272 | 1103 | 042721103 | 042721103 | 9
0120401130 | 10 | 01204 | 1130 | 012041130 | 012041130 | 9
0120401131 | 10 | 01204 | 1131 | 012041131 | 012041131 | 9
0120401132 | 10 | 01204 | 1132 | 012041132 | 012041132 | 9
0829501103 | 10 | 08295 | 1103 | 082951103 | 082951103 | 9
0120401133 | 10 | 01204 | 1133 | 012041133 | 012041133 | 9
1624201103 | 10 | 16242 | 1103 | 162421103 | 162421103 | 9
2545802101 | 10 | 25458 | 2101 | 254582101 | 254582101 | 9
1624201105 | 10 | 16242 | 1105 | 162421105 | 162421105 | 9
2545802102 | 10 | 25458 | 2102 | 254582102 | 254582102 | 9
0427201104 | 10 | 04272 | 1104 | 042721104 | 042721104 | 9
2545802103 | 10 | 25458 | 2103 | 254582103 | 254582103 | 9
0427201105 | 10 | 04272 | 1105 | 042721105 | 042721105 | 9
012080401 | 9 |  |  | 012080401 | 012080401 | 9
2520201101 | 10 | 25202 | 1101 | 252021101 | 252021101 | 9
0427201106 | 10 | 04272 | 1106 | 042721106 | 042721106 | 9
2520201102 | 10 | 25202 | 1102 | 252021102 | 252021102 | 9
012080402 | 9 |  |  | 012080402 | 012080402 | 9
0427201107 | 10 | 04272 | 1107 | 042721107 | 042721107 | 9
062701104 | 9 |  |  | 062701104 | 062701104 | 9
2538001101 | 10 | 25380 | 1101 | 253801101 | 253801101 | 9
2538001102 | 10 | 25380 | 1102 | 253801102 | 253801102 | 9
2538001103 | 10 | 25380 | 1103 | 253801103 | 253801103 | 9
062701110 | 9 |  |  | 062701110 | 062701110 | 9
0433201101 | 10 | 04332 | 1101 | 043321101 | 043321101 | 9
0433201102 | 10 | 04332 | 1102 | 043321102 | 043321102 | 9
0829502106 | 10 | 08295 | 2106 | 082952106 | 082952106 | 9
0433201103 | 10 | 04332 | 1103 | 043321103 | 043321103 | 9
0433201104 | 10 | 04332 | 1104 | 043321104 | 043321104 | 9
2533702104 | 10 | 25337 | 2104 | 253372104 | 253372104 | 9
2533702106 | 10 | 25337 | 2106 | 253372106 | 253372106 | 9
2533702107 | 10 | 25337 | 2107 | 253372107 | 253372107 | 9
0121101101 | 10 | 01211 | 1101 | 012111101 | 012111101 | 9
2533702108 | 10 | 25337 | 2108 | 253372108 | 253372108 | 9
1923901103 | 10 | 19239 | 1103 | 192391103 | 192391103 | 9
0121101102 | 10 | 01211 | 1102 | 012111102 | 012111102 | 9
0431601101 | 10 | 04316 | 1101 | 043161101 | 043161101 | 9
0121101107 | 10 | 01211 | 1107 | 012111107 | 012111107 | 9
0428701101 | 10 | 04287 | 1101 | 042871101 | 042871101 | 9
2533702109 | 10 | 25337 | 2109 | 253372109 | 253372109 | 9
0121101111 | 10 | 01211 | 1111 | 012111111 | 012111111 | 9
1923901104 | 10 | 19239 | 1104 | 192391104 | 192391104 | 9
0427701113 | 10 | 04277 | 1113 | 042771113 | 042771113 | 9
0427701114 | 10 | 04277 | 1114 | 042771114 | 042771114 | 9
0427701115 | 10 | 04277 | 1115 | 042771115 | 042771115 | 9
0427701111 | 10 | 04277 | 1111 | 042771111 | 042771111 | 9
0121101112 | 10 | 01211 | 1112 | 012111112 | 012111112 | 9
0121101113 | 10 | 01211 | 1113 | 012111113 | 012111113 | 9
192231101 | 9 |  |  | 192231101 | 192231101 | 9
192231102 | 9 |  |  | 192231102 | 192231102 | 9
1923201121 | 10 | 19232 | 1121 | 192321121 | 192321121 | 9
1923201122 | 10 | 19232 | 1122 | 192321122 | 192321122 | 9
1921201106 | 10 | 19212 | 1106 | 192121106 | 192121106 | 9
1921201107 | 10 | 19212 | 1107 | 192121107 | 192121107 | 9
0428501121 | 10 | 04285 | 1121 | 042851121 | 042851121 | 9
1923301101 | 10 | 19233 | 1101 | 192331101 | 192331101 | 9
1923301104 | 10 | 19233 | 1104 | 192331104 | 192331104 | 9
1923301105 | 10 | 19233 | 1105 | 192331105 | 192331105 | 9
0829502107 | 10 | 08295 | 2107 | 082952107 | 082952107 | 9
0628801102 | 10 | 06288 | 1102 | 062881102 | 062881102 | 9
2533701101 | 10 | 25337 | 1101 | 253371101 | 253371101 | 9
2533701105 | 10 | 25337 | 1105 | 253371105 | 253371105 | 9
2533701107 | 10 | 25337 | 1107 | 253371107 | 253371107 | 9
2533701115 | 10 | 25337 | 1115 | 253371115 | 253371115 | 9
2533701114 | 10 | 25337 | 1114 | 253371114 | 253371114 | 9
0426801101 | 10 | 04268 | 1101 | 042681101 | 042681101 | 9
1827301101 | 10 | 18273 | 1101 | 182731101 | 182731101 | 9
2527201116 | 10 | 25272 | 1116 | 252721116 | 252721116 | 9
1827301102 | 10 | 18273 | 1102 | 182731102 | 182731102 | 9
1624202106 | 10 | 16242 | 2106 | 162422106 | 162422106 | 9
1624202107 | 10 | 16242 | 2107 | 162422107 | 162422107 | 9
1624202108 | 10 | 16242 | 2108 | 162422108 | 162422108 | 9
022590402 | 9 |  |  | 022590402 | 022590402 | 9
1820301101 | 10 | 18203 | 1101 | 182031101 | 182031101 | 9
0426801102 | 10 | 04268 | 1102 | 042681102 | 042681102 | 9
192411101 | 9 |  |  | 192411101 | 192411101 | 9
0433501103 | 10 | 04335 | 1103 | 043351103 | 043351103 | 9
1524801102 | 10 | 15248 | 1102 | 152481102 | 152481102 | 9
1524801103 | 10 | 15248 | 1103 | 152481103 | 152481103 | 9
0433501106 | 10 | 04335 | 1106 | 043351106 | 043351106 | 9
1524801104 | 10 | 15248 | 1104 | 152481104 | 152481104 | 9
1921001101 | 10 | 19210 | 1101 | 192101101 | 192101101 | 9
0429501101 | 10 | 04295 | 1101 | 042951101 | 042951101 | 9
0429501102 | 10 | 04295 | 1102 | 042951102 | 042951102 | 9
1830301101 | 10 | 18303 | 1101 | 183031101 | 183031101 | 9
1820301102 | 10 | 18203 | 1102 | 182031102 | 182031102 | 9
042120411 | 9 |  |  | 042120411 | 042120411 | 9
1820301103 | 10 | 18203 | 1103 | 182031103 | 182031103 | 9
042120413 | 9 |  |  | 042120413 | 042120413 | 9
1820301104 | 10 | 18203 | 1104 | 182031104 | 182031104 | 9
1922501101 | 10 | 19225 | 1101 | 192251101 | 192251101 | 9
1922501102 | 10 | 19225 | 1102 | 192251102 | 192251102 | 9
1826101101 | 10 | 18261 | 1101 | 182611101 | 182611101 | 9
43061101 | 8 |  |  | 043061101 | 043061101 | 9
1524801105 | 10 | 15248 | 1105 | 152481105 | 152481105 | 9
1524801106 | 10 | 15248 | 1106 | 152481106 | 152481106 | 9
1924501103 | 10 | 19245 | 1103 | 192451103 | 192451103 | 9
1924501104 | 10 | 19245 | 1104 | 192451104 | 192451104 | 9
1524801107 | 10 | 15248 | 1107 | 152481107 | 152481107 | 9
1524801110 | 10 | 15248 | 1110 | 152481110 | 152481110 | 9
1923101141 | 10 | 19231 | 1141 | 192311141 | 192311141 | 9
1923101142 | 10 | 19231 | 1142 | 192311142 | 192311142 | 9
1536602102 | 10 | 15366 | 2102 | 153662102 | 153662102 | 9
1524701101 | 10 | 15247 | 1101 | 152471101 | 152471101 | 9
1820301107 | 10 | 18203 | 1107 | 182031107 | 182031107 | 9
1820301108 | 10 | 18203 | 1108 | 182031108 | 182031108 | 9
1536601103 | 10 | 15366 | 1103 | 153661103 | 153661103 | 9
1536601104 | 10 | 15366 | 1104 | 153661104 | 153661104 | 9
0139102107 | 10 | 01391 | 2107 | 013912107 | 013912107 | 9
0139102108 | 10 | 01391 | 2108 | 013912108 | 013912108 | 9
1823701111 | 10 | 18237 | 1111 | 182371111 | 182371111 | 9
1823701112 | 10 | 18237 | 1112 | 182371112 | 182371112 | 9
2539501109 | 10 | 25395 | 1109 | 253951109 | 253951109 | 9
2539501103 | 10 | 25395 | 1103 | 253951103 | 253951103 | 9
1821501101 | 10 | 18215 | 1101 | 182151101 | 182151101 | 9
2539501110 | 10 | 25395 | 1110 | 253951110 | 253951110 | 9
2539501104 | 10 | 25395 | 1104 | 253951104 | 253951104 | 9
1821501102 | 10 | 18215 | 1102 | 182151102 | 182151102 | 9
2539501105 | 10 | 25395 | 1105 | 253951105 | 253951105 | 9
2539501106 | 10 | 25395 | 1106 | 253951106 | 253951106 | 9
0839001101 | 10 | 08390 | 1101 | 083901101 | 083901101 | 9
2546802101 | 10 | 25468 | 2101 | 254682101 | 254682101 | 9
0839001102 | 10 | 08390 | 1102 | 083901102 | 083901102 | 9
2546801102 | 10 | 25468 | 1102 | 254681102 | 254681102 | 9
2533701116 | 10 | 25337 | 1116 | 253371116 | 253371116 | 9
2533701118 | 10 | 25337 | 1118 | 253371118 | 253371118 | 9
1820802101 | 10 | 18208 | 2101 | 182082101 | 182082101 | 9
0820201106 | 10 | 08202 | 1106 | 082021106 | 082021106 | 9
2533701102 | 10 | 25337 | 1102 | 253371102 | 253371102 | 9
2533701106 | 10 | 25337 | 1106 | 253371106 | 253371106 | 9
2533701110 | 10 | 25337 | 1110 | 253371110 | 253371110 | 9
1820802102 | 10 | 18208 | 2102 | 182082102 | 182082102 | 9
1820802103 | 10 | 18208 | 2103 | 182082103 | 182082103 | 9
1924301109 | 10 | 19243 | 1109 | 192431109 | 192431109 | 9
1924301108 | 10 | 19243 | 1108 | 192431108 | 192431108 | 9
1523001101 | 10 | 15230 | 1101 | 152301101 | 152301101 | 9
1523001102 | 10 | 15230 | 1102 | 152301102 | 152301102 | 9
0432101101 | 10 | 04321 | 1101 | 043211101 | 043211101 | 9
183150404 | 9 |  |  | 183150404 | 183150404 | 9
0432101102 | 10 | 04321 | 1102 | 043211102 | 043211102 | 9
0635901101 | 10 | 06359 | 1101 | 063591101 | 063591101 | 9
0431401101 | 10 | 04314 | 1101 | 043141101 | 043141101 | 9
0431401103 | 10 | 04314 | 1103 | 043141103 | 043141103 | 9
0635901109 | 10 | 06359 | 1109 | 063591109 | 063591109 | 9
0431401102 | 10 | 04314 | 1102 | 043141102 | 043141102 | 9
0635901102 | 10 | 06359 | 1102 | 063591102 | 063591102 | 9
0242601102 | 10 | 02426 | 1102 | 024261102 | 024261102 | 9
0242601103 | 10 | 02426 | 1103 | 024261103 | 024261103 | 9
0431901101 | 10 | 04319 | 1101 | 043191101 | 043191101 | 9
0820201107 | 10 | 08202 | 1107 | 082021107 | 082021107 | 9
182090401 | 9 |  |  | 182090401 | 182090401 | 9
0242601104 | 10 | 02426 | 1104 | 024261104 | 024261104 | 9
0431901102 | 10 | 04319 | 1102 | 043191102 | 043191102 | 9
0635901103 | 10 | 06359 | 1103 | 063591103 | 063591103 | 9
2524401104 | 10 | 25244 | 1104 | 252441104 | 252441104 | 9
2524401106 | 10 | 25244 | 1106 | 252441106 | 252441106 | 9
0426001101 | 10 | 04260 | 1101 | 042601101 | 042601101 | 9
0426001102 | 10 | 04260 | 1102 | 042601102 | 042601102 | 9
0635901104 | 10 | 06359 | 1104 | 063591104 | 063591104 | 9
1922201101 | 10 | 19222 | 1101 | 192221101 | 192221101 | 9
0433801101 | 10 | 04338 | 1101 | 043381101 | 043381101 | 9
0635901105 | 10 | 06359 | 1105 | 063591105 | 063591105 | 9
0433101102 | 10 | 04331 | 1102 | 043311102 | 043311102 | 9
0433101108 | 10 | 04331 | 1108 | 043311108 | 043311108 | 9
0635901106 | 10 | 06359 | 1106 | 063591106 | 063591106 | 9
192221102 | 9 |  |  | 192221102 | 192221102 | 9
1921501132 | 10 | 19215 | 1132 | 192151132 | 192151132 | 9
2539301101 | 10 | 25393 | 1101 | 253931101 | 253931101 | 9
1921501131 | 10 | 19215 | 1131 | 192151131 | 192151131 | 9
1921501133 | 10 | 19215 | 1133 | 192151133 | 192151133 | 9
0635901107 | 10 | 06359 | 1107 | 063591107 | 063591107 | 9
192221103 | 9 |  |  | 192221103 | 192221103 | 9
2539301102 | 10 | 25393 | 1102 | 253931102 | 253931102 | 9
1922601101 | 10 | 19226 | 1101 | 192261101 | 192261101 | 9
1922601102 | 10 | 19226 | 1102 | 192261102 | 192261102 | 9
0428401111 | 10 | 04284 | 1111 | 042841111 | 042841111 | 9
0428401112 | 10 | 04284 | 1112 | 042841112 | 042841112 | 9
192401101 | 9 |  |  | 192401101 | 192401101 | 9
0422501101 | 10 | 04225 | 1101 | 042251101 | 042251101 | 9
192341101 | 9 |  |  | 192341101 | 192341101 | 9
192341102 | 9 |  |  | 192341102 | 192341102 | 9
2539301104 | 10 | 25393 | 1104 | 253931104 | 253931104 | 9
2539301105 | 10 | 25393 | 1105 | 253931105 | 253931105 | 9
0820201108 | 10 | 08202 | 1108 | 082021108 | 082021108 | 9
2539301106 | 10 | 25393 | 1106 | 253931106 | 253931106 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
2539301107 | 10 | 25393 | 1107 | 253931107 | 253931107 | 9
| 0 |  |  |  |  | 0
2539301108 | 10 | 25393 | 1108 | 253931108 | 253931108 | 9
2539301109 | 10 | 25393 | 1109 | 253931109 | 253931109 | 9
2538701102 | 10 | 25387 | 1102 | 253871102 | 253871102 | 9
2538701103 | 10 | 25387 | 1103 | 253871103 | 253871103 | 9
1020401101 | 10 | 10204 | 1101 | 102041101 | 102041101 | 9
1020401102 | 10 | 10204 | 1102 | 102041102 | 102041102 | 9
1020401103 | 10 | 10204 | 1103 | 102041103 | 102041103 | 9
1020401104 | 10 | 10204 | 1104 | 102041104 | 102041104 | 9
1033801101 | 10 | 10338 | 1101 | 103381101 | 103381101 | 9
1033801102 | 10 | 10338 | 1102 | 103381102 | 103381102 | 9
1028501101 | 10 | 10285 | 1101 | 102851101 | 102851101 | 9
1028501102 | 10 | 10285 | 1102 | 102851102 | 102851102 | 9
1031402101 | 10 | 10314 | 2101 | 103142101 | 103142101 | 9
1031402102 | 10 | 10314 | 2102 | 103142102 | 103142102 | 9
1027401101 | 10 | 10274 | 1101 | 102741101 | 102741101 | 9
1027401103 | 10 | 10274 | 1103 | 102741103 | 102741103 | 9
1027401104 | 10 | 10274 | 1104 | 102741104 | 102741104 | 9
1037302101 | 10 | 10373 | 2101 | 103732101 | 103732101 | 9
1035701103 | 10 | 10357 | 1103 | 103571103 | 103571103 | 9
1035701104 | 10 | 10357 | 1104 | 103571104 | 103571104 | 9
0143501110 | 10 | 01435 | 1110 | 014351110 | 014351110 | 9
0143501111 | 10 | 01435 | 1111 | 014351111 | 014351111 | 9
182090402 | 9 |  |  | 182090402 | 182090402 | 9
0143501112 | 10 | 01435 | 1112 | 014351112 | 014351112 | 9
182090403 | 9 |  |  | 182090403 | 182090403 | 9
182090404 | 9 |  |  | 182090404 | 182090404 | 9
1826101102 | 10 | 18261 | 1102 | 182611102 | 182611102 | 9
1826101103 | 10 | 18261 | 1103 | 182611103 | 182611103 | 9
182090405 | 9 |  |  | 182090405 | 182090405 | 9
1823901102 | 10 | 18239 | 1102 | 182391102 | 182391102 | 9
1632901101 | 10 | 16329 | 1101 | 163291101 | 163291101 | 9
1632901102 | 10 | 16329 | 1102 | 163291102 | 163291102 | 9
1632901103 | 10 | 16329 | 1103 | 163291103 | 163291103 | 9
1632901104 | 10 | 16329 | 1104 | 163291104 | 163291104 | 9
1823901103 | 10 | 18239 | 1103 | 182391103 | 182391103 | 9
1823901104 | 10 | 18239 | 1104 | 182391104 | 182391104 | 9
083450401 | 9 |  |  | 083450401 | 083450401 | 9
083450402 | 9 |  |  | 083450402 | 083450402 | 9
1520301101 | 10 | 15203 | 1101 | 152031101 | 152031101 | 9
1520301102 | 10 | 15203 | 1102 | 152031102 | 152031102 | 9
1520301103 | 10 | 15203 | 1103 | 152031103 | 152031103 | 9
1829401101 | 10 | 18294 | 1101 | 182941101 | 182941101 | 9
1829401102 | 10 | 18294 | 1102 | 182941102 | 182941102 | 9
102050401 | 9 |  |  | 102050401 | 102050401 | 9
102050402 | 9 |  |  | 102050402 | 102050402 | 9
0125001102 | 10 | 01250 | 1102 | 012501102 | 012501102 | 9
0125001105 | 10 | 01250 | 1105 | 012501105 | 012501105 | 9
0125001111 | 10 | 01250 | 1111 | 012501111 | 012501111 | 9
0125001113 | 10 | 01250 | 1113 | 012501113 | 012501113 | 9
0125001114 | 10 | 01250 | 1114 | 012501114 | 012501114 | 9
0125001101 | 10 | 01250 | 1101 | 012501101 | 012501101 | 9
0125001104 | 10 | 01250 | 1104 | 012501104 | 012501104 | 9
0125001106 | 10 | 01250 | 1106 | 012501106 | 012501106 | 9
2534801101 | 10 | 25348 | 1101 | 253481101 | 253481101 | 9
2534801102 | 10 | 25348 | 1102 | 253481102 | 253481102 | 9
2534801103 | 10 | 25348 | 1103 | 253481103 | 253481103 | 9
1025401101 | 10 | 10254 | 1101 | 102541101 | 102541101 | 9
1025401102 | 10 | 10254 | 1102 | 102541102 | 102541102 | 9
2537001101 | 10 | 25370 | 1101 | 253701101 | 253701101 | 9
2537001102 | 10 | 25370 | 1102 | 253701102 | 253701102 | 9
2537001103 | 10 | 25370 | 1103 | 253701103 | 253701103 | 9
2537001104 | 10 | 25370 | 1104 | 253701104 | 253701104 | 9
2537001105 | 10 | 25370 | 1105 | 253701105 | 253701105 | 9
2537001106 | 10 | 25370 | 1106 | 253701106 | 253701106 | 9
1036001101 | 10 | 10360 | 1101 | 103601101 | 103601101 | 9
2537001107 | 10 | 25370 | 1107 | 253701107 | 253701107 | 9
2537001108 | 10 | 25370 | 1108 | 253701108 | 253701108 | 9
2537001109 | 10 | 25370 | 1109 | 253701109 | 253701109 | 9
103611101 | 9 |  |  | 103611101 | 103611101 | 9
2537001110 | 10 | 25370 | 1110 | 253701110 | 253701110 | 9
2537001111 | 10 | 25370 | 1111 | 253701111 | 253701111 | 9
2537001112 | 10 | 25370 | 1112 | 253701112 | 253701112 | 9
1035501101 | 10 | 10355 | 1101 | 103551101 | 103551101 | 9
2542901103 | 10 | 25429 | 1103 | 254291103 | 254291103 | 9
2542901104 | 10 | 25429 | 1104 | 254291104 | 254291104 | 9
2542901102 | 10 | 25429 | 1102 | 254291102 | 254291102 | 9
1826101104 | 10 | 18261 | 1104 | 182611104 | 182611104 | 9
2529701101 | 10 | 25297 | 1101 | 252971101 | 252971101 | 9
2529701102 | 10 | 25297 | 1102 | 252971102 | 252971102 | 9
2529701103 | 10 | 25297 | 1103 | 252971103 | 252971103 | 9
1826101106 | 10 | 18261 | 1106 | 182611106 | 182611106 | 9
2529701105 | 10 | 25297 | 1105 | 252971105 | 252971105 | 9
0125001107 | 10 | 01250 | 1107 | 012501107 | 012501107 | 9
0125001110 | 10 | 01250 | 1110 | 012501110 | 012501110 | 9
012501201 | 9 |  |  | 012501201 | 012501201 | 9
012501202 | 9 |  |  | 012501202 | 012501202 | 9
012501203 | 9 |  |  | 012501203 | 012501203 | 9
012501204 | 9 |  |  | 012501204 | 012501204 | 9
1826101107 | 10 | 18261 | 1107 | 182611107 | 182611107 | 9
1020501101 | 10 | 10205 | 1101 | 102051101 | 102051101 | 9
2529701106 | 10 | 25297 | 1106 | 252971106 | 252971106 | 9
1020501102 | 10 | 10205 | 1102 | 102051102 | 102051102 | 9
1020501103 | 10 | 10205 | 1103 | 102051103 | 102051103 | 9
2529601101 | 10 | 25296 | 1101 | 252961101 | 252961101 | 9
2529601102 | 10 | 25296 | 1102 | 252961102 | 252961102 | 9
2529601104 | 10 | 25296 | 1104 | 252961104 | 252961104 | 9
1830701101 | 10 | 18307 | 1101 | 183071101 | 183071101 | 9
2544001102 | 10 | 25440 | 1102 | 254401102 | 254401102 | 9
2544002105 | 10 | 25440 | 2105 | 254402105 | 254402105 | 9
2545601103 | 10 | 25456 | 1103 | 254561103 | 254561103 | 9
2545601104 | 10 | 25456 | 1104 | 254561104 | 254561104 | 9
2545601105 | 10 | 25456 | 1105 | 254561105 | 254561105 | 9
2545601106 | 10 | 25456 | 1106 | 254561106 | 254561106 | 9
2553202101 | 10 | 25532 | 2101 | 255322101 | 255322101 | 9
2553202102 | 10 | 25532 | 2102 | 255322102 | 255322102 | 9
2553202103 | 10 | 25532 | 2103 | 255322103 | 255322103 | 9
2553202104 | 10 | 25532 | 2104 | 255322104 | 255322104 | 9
2553202105 | 10 | 25532 | 2105 | 255322105 | 255322105 | 9
2525501104 | 10 | 25255 | 1104 | 252551104 | 252551104 | 9
2525502103 | 10 | 25255 | 2103 | 252552103 | 252552103 | 9
2529301102 | 10 | 25293 | 1102 | 252931102 | 252931102 | 9
2529301103 | 10 | 25293 | 1103 | 252931103 | 252931103 | 9
2529301105 | 10 | 25293 | 1105 | 252931105 | 252931105 | 9
2529301106 | 10 | 25293 | 1106 | 252931106 | 252931106 | 9
1624201101 | 10 | 16242 | 1101 | 162421101 | 162421101 | 9
1624201106 | 10 | 16242 | 1106 | 162421106 | 162421106 | 9
1624202103 | 10 | 16242 | 2103 | 162422103 | 162422103 | 9
1624202104 | 10 | 16242 | 2104 | 162422104 | 162422104 | 9
1624202105 | 10 | 16242 | 2105 | 162422105 | 162422105 | 9
1627001701 | 10 | 16270 | 1701 | 162701701 | 162701701 | 9
1627001702 | 10 | 16270 | 1702 | 162701702 | 162701702 | 9
1627001703 | 10 | 16270 | 1703 | 162701703 | 162701703 | 9
182440421 | 9 |  |  | 182440421 | 182440421 | 9
182440423 | 9 |  |  | 182440423 | 182440423 | 9
1635701701 | 10 | 16357 | 1701 | 163571701 | 163571701 | 9
1635701702 | 10 | 16357 | 1702 | 163571702 | 163571702 | 9
0420301122 | 10 | 04203 | 1122 | 042031122 | 042031122 | 9
0420301123 | 10 | 04203 | 1123 | 042031123 | 042031123 | 9
2520801101 | 10 | 25208 | 1101 | 252081101 | 252081101 | 9
2520801103 | 10 | 25208 | 1103 | 252081103 | 252081103 | 9
2520801104 | 10 | 25208 | 1104 | 252081104 | 252081104 | 9
0420301124 | 10 | 04203 | 1124 | 042031124 | 042031124 | 9
2520801106 | 10 | 25208 | 1106 | 252081106 | 252081106 | 9
2520801108 | 10 | 25208 | 1108 | 252081108 | 252081108 | 9
0420301120 | 10 | 04203 | 1120 | 042031120 | 042031120 | 9
2540701109 | 10 | 25407 | 1109 | 254071109 | 254071109 | 9
0420301121 | 10 | 04203 | 1121 | 042031121 | 042031121 | 9
2540701110 | 10 | 25407 | 1110 | 254071110 | 254071110 | 9
2540701111 | 10 | 25407 | 1111 | 254071111 | 254071111 | 9
0420301125 | 10 | 04203 | 1125 | 042031125 | 042031125 | 9
1627001706 | 10 | 16270 | 1706 | 162701706 | 162701706 | 9
1627001707 | 10 | 16270 | 1707 | 162701707 | 162701707 | 9
0424601101 | 10 | 04246 | 1101 | 042461101 | 042461101 | 9
0424601104 | 10 | 04246 | 1104 | 042461104 | 042461104 | 9
0424601105 | 10 | 04246 | 1105 | 042461105 | 042461105 | 9
0424601106 | 10 | 04246 | 1106 | 042461106 | 042461106 | 9
0422601101 | 10 | 04226 | 1101 | 042261101 | 042261101 | 9
0427101101 | 10 | 04271 | 1101 | 042711101 | 042711101 | 9
0427101102 | 10 | 04271 | 1102 | 042711102 | 042711102 | 9
0432801103 | 10 | 04328 | 1103 | 043281103 | 043281103 | 9
0432801104 | 10 | 04328 | 1104 | 043281104 | 043281104 | 9
0432801105 | 10 | 04328 | 1105 | 043281105 | 043281105 | 9
0430901101 | 10 | 04309 | 1101 | 043091101 | 043091101 | 9
0430901102 | 10 | 04309 | 1102 | 043091102 | 043091102 | 9
0627001112 | 10 | 06270 | 1112 | 062701112 | 062701112 | 9
2540702108 | 10 | 25407 | 2108 | 254072108 | 254072108 | 9
2540702109 | 10 | 25407 | 2109 | 254072109 | 254072109 | 9
2540702110 | 10 | 25407 | 2110 | 254072110 | 254072110 | 9
2540702111 | 10 | 25407 | 2111 | 254072111 | 254072111 | 9
0430901103 | 10 | 04309 | 1103 | 043091103 | 043091103 | 9
2540702112 | 10 | 25407 | 2112 | 254072112 | 254072112 | 9
2540702113 | 10 | 25407 | 2113 | 254072113 | 254072113 | 9
62881103 | 8 |  |  | 062881103 | 062881103 | 9
2540702114 | 10 | 25407 | 2114 | 254072114 | 254072114 | 9
2540702115 | 10 | 25407 | 2115 | 254072115 | 254072115 | 9
0430901104 | 10 | 04309 | 1104 | 043091104 | 043091104 | 9
2540701105 | 10 | 25407 | 1105 | 254071105 | 254071105 | 9
2540701106 | 10 | 25407 | 1106 | 254071106 | 254071106 | 9
182440422 | 9 |  |  | 182440422 | 182440422 | 9
2540702105 | 10 | 25407 | 2105 | 254072105 | 254072105 | 9
182440424 | 9 |  |  | 182440424 | 182440424 | 9
2540702106 | 10 | 25407 | 2106 | 254072106 | 254072106 | 9
2540702107 | 10 | 25407 | 2107 | 254072107 | 254072107 | 9
0832502101 | 10 | 08325 | 2101 | 083252101 | 083252101 | 9
0832502102 | 10 | 08325 | 2102 | 083252102 | 083252102 | 9
0636001102 | 10 | 06360 | 1102 | 063601102 | 063601102 | 9
0832502103 | 10 | 08325 | 2103 | 083252103 | 083252103 | 9
0636001103 | 10 | 06360 | 1103 | 063601103 | 063601103 | 9
0832502104 | 10 | 08325 | 2104 | 083252104 | 083252104 | 9
0636001104 | 10 | 06360 | 1104 | 063601104 | 063601104 | 9
2535501101 | 10 | 25355 | 1101 | 253551101 | 253551101 | 9
2535501102 | 10 | 25355 | 1102 | 253551102 | 253551102 | 9
2535501103 | 10 | 25355 | 1103 | 253551103 | 253551103 | 9
2535501104 | 10 | 25355 | 1104 | 253551104 | 253551104 | 9
2535501105 | 10 | 25355 | 1105 | 253551105 | 253551105 | 9
2536501101 | 10 | 25365 | 1101 | 253651101 | 253651101 | 9
0426501102 | 10 | 04265 | 1102 | 042651102 | 042651102 | 9
0426501104 | 10 | 04265 | 1104 | 042651104 | 042651104 | 9
0426501106 | 10 | 04265 | 1106 | 042651106 | 042651106 | 9
0426501101 | 10 | 04265 | 1101 | 042651101 | 042651101 | 9
0426501103 | 10 | 04265 | 1103 | 042651103 | 042651103 | 9
0426501105 | 10 | 04265 | 1105 | 042651105 | 042651105 | 9
0832502105 | 10 | 08325 | 2105 | 083252105 | 083252105 | 9
0832502106 | 10 | 08325 | 2106 | 083252106 | 083252106 | 9
2536501102 | 10 | 25365 | 1102 | 253651102 | 253651102 | 9
2536501103 | 10 | 25365 | 1103 | 253651103 | 253651103 | 9
2536501104 | 10 | 25365 | 1104 | 253651104 | 253651104 | 9
1638001702 | 10 | 16380 | 1702 | 163801702 | 163801702 | 9
1638001704 | 10 | 16380 | 1704 | 163801704 | 163801704 | 9
1829701101 | 10 | 18297 | 1101 | 182971101 | 182971101 | 9
2531901101 | 10 | 25319 | 1101 | 253191101 | 253191101 | 9
2531901102 | 10 | 25319 | 1102 | 253191102 | 253191102 | 9
2531901104 | 10 | 25319 | 1104 | 253191104 | 253191104 | 9
2547601101 | 10 | 25476 | 1101 | 254761101 | 254761101 | 9
254761102 | 9 |  |  | 254761102 | 254761102 | 9
2528601102 | 10 | 25286 | 1102 | 252861102 | 252861102 | 9
2528601106 | 10 | 25286 | 1106 | 252861106 | 252861106 | 9
2528601101 | 10 | 25286 | 1101 | 252861101 | 252861101 | 9
2528601103 | 10 | 25286 | 1103 | 252861103 | 252861103 | 9
0424801103 | 10 | 04248 | 1103 | 042481103 | 042481103 | 9
0424801104 | 10 | 04248 | 1104 | 042481104 | 042481104 | 9
2545702101 | 10 | 25457 | 2101 | 254572101 | 254572101 | 9
2545702102 | 10 | 25457 | 2102 | 254572102 | 254572102 | 9
2545702103 | 10 | 25457 | 2103 | 254572103 | 254572103 | 9
2545702105 | 10 | 25457 | 2105 | 254572105 | 254572105 | 9
2545702107 | 10 | 25457 | 2107 | 254572107 | 254572107 | 9
0832502107 | 10 | 08325 | 2107 | 083252107 | 083252107 | 9
0429901103 | 10 | 04299 | 1103 | 042991103 | 042991103 | 9
0429901104 | 10 | 04299 | 1104 | 042991104 | 042991104 | 9
0832502108 | 10 | 08325 | 2108 | 083252108 | 083252108 | 9
0429901105 | 10 | 04299 | 1105 | 042991105 | 042991105 | 9
0832502109 | 10 | 08325 | 2109 | 083252109 | 083252109 | 9
0429901106 | 10 | 04299 | 1106 | 042991106 | 042991106 | 9
0429901107 | 10 | 04299 | 1107 | 042991107 | 042991107 | 9
253642101 | 9 |  |  | 253642101 | 253642101 | 9
082931101 | 9 |  |  | 082931101 | 082931101 | 9
1829601107 | 10 | 18296 | 1107 | 182961107 | 182961107 | 9
0420201105 | 10 | 04202 | 1105 | 042021105 | 042021105 | 9
1829601110 | 10 | 18296 | 1110 | 182961110 | 182961110 | 9
2534202101 | 10 | 25342 | 2101 | 253422101 | 253422101 | 9
2534202102 | 10 | 25342 | 2102 | 253422102 | 253422102 | 9
022590401 | 9 |  |  | 022590401 | 022590401 | 9
0420201106 | 10 | 04202 | 1106 | 042021106 | 042021106 | 9
1826301101 | 10 | 18263 | 1101 | 182631101 | 182631101 | 9
2528201103 | 10 | 25282 | 1103 | 252821103 | 252821103 | 9
2528201104 | 10 | 25282 | 1104 | 252821104 | 252821104 | 9
1826301102 | 10 | 18263 | 1102 | 182631102 | 182631102 | 9
2528201101 | 10 | 25282 | 1101 | 252821101 | 252821101 | 9
1826301103 | 10 | 18263 | 1103 | 182631103 | 182631103 | 9
2528201102 | 10 | 25282 | 1102 | 252821102 | 252821102 | 9
0420401102 | 10 | 04204 | 1102 | 042041102 | 042041102 | 9
0420401103 | 10 | 04204 | 1103 | 042041103 | 042041103 | 9
0420401104 | 10 | 04204 | 1104 | 042041104 | 042041104 | 9
0420401108 | 10 | 04204 | 1108 | 042041108 | 042041108 | 9
0422101101 | 10 | 04221 | 1101 | 042211101 | 042211101 | 9
0422101102 | 10 | 04221 | 1102 | 042211102 | 042211102 | 9
0422101103 | 10 | 04221 | 1103 | 042211103 | 042211103 | 9
0422101104 | 10 | 04221 | 1104 | 042211104 | 042211104 | 9
0422901101 | 10 | 04229 | 1101 | 042291101 | 042291101 | 9
0420501101 | 10 | 04205 | 1101 | 042051101 | 042051101 | 9
0420501102 | 10 | 04205 | 1102 | 042051102 | 042051102 | 9
0420501103 | 10 | 04205 | 1103 | 042051103 | 042051103 | 9
0432902101 | 10 | 04329 | 2101 | 043292101 | 043292101 | 9
2527201110 | 10 | 25272 | 1110 | 252721110 | 252721110 | 9
0432902102 | 10 | 04329 | 2102 | 043292102 | 043292102 | 9
2527201112 | 10 | 25272 | 1112 | 252721112 | 252721112 | 9
0432902103 | 10 | 04329 | 2103 | 043292103 | 043292103 | 9
0432901102 | 10 | 04329 | 1102 | 043291102 | 043291102 | 9
2527201114 | 10 | 25272 | 1114 | 252721114 | 252721114 | 9
0432901103 | 10 | 04329 | 1103 | 043291103 | 043291103 | 9
0432901104 | 10 | 04329 | 1104 | 043291104 | 043291104 | 9
0432901105 | 10 | 04329 | 1105 | 043291105 | 043291105 | 9
2527201104 | 10 | 25272 | 1104 | 252721104 | 252721104 | 9
2527201106 | 10 | 25272 | 1106 | 252721106 | 252721106 | 9
2527201108 | 10 | 25272 | 1108 | 252721108 | 252721108 | 9
022590403 | 9 |  |  | 022590403 | 022590403 | 9
0420101103 | 10 | 04201 | 1103 | 042011103 | 042011103 | 9
0420101104 | 10 | 04201 | 1104 | 042011104 | 042011104 | 9
0420101106 | 10 | 04201 | 1106 | 042011106 | 042011106 | 9
0420101101 | 10 | 04201 | 1101 | 042011101 | 042011101 | 9
0420101102 | 10 | 04201 | 1102 | 042011102 | 042011102 | 9
0144202109 | 10 | 01442 | 2109 | 014422109 | 014422109 | 9
0144202111 | 10 | 01442 | 2111 | 014422111 | 014422111 | 9
0144002103 | 10 | 01440 | 2103 | 014402103 | 014402103 | 9
0144002104 | 10 | 01440 | 2104 | 014402104 | 014402104 | 9
0420101107 | 10 | 04201 | 1107 | 042011107 | 042011107 | 9
0420101108 | 10 | 04201 | 1108 | 042011108 | 042011108 | 9
0144002105 | 10 | 01440 | 2105 | 014402105 | 014402105 | 9
0144002106 | 10 | 01440 | 2106 | 014402106 | 014402106 | 9
0420101105 | 10 | 04201 | 1105 | 042011105 | 042011105 | 9
0144002107 | 10 | 01440 | 2107 | 014402107 | 014402107 | 9
0144002108 | 10 | 01440 | 2108 | 014402108 | 014402108 | 9
0144002109 | 10 | 01440 | 2109 | 014402109 | 014402109 | 9
0144002110 | 10 | 01440 | 2110 | 014402110 | 014402110 | 9
0420101109 | 10 | 04201 | 1109 | 042011109 | 042011109 | 9
0420101110 | 10 | 04201 | 1110 | 042011110 | 042011110 | 9
0121401101 | 10 | 01214 | 1101 | 012141101 | 012141101 | 9
0121401103 | 10 | 01214 | 1103 | 012141103 | 012141103 | 9
0121401102 | 10 | 01214 | 1102 | 012141102 | 012141102 | 9
0144502103 | 10 | 01445 | 2103 | 014452103 | 014452103 | 9
0144502104 | 10 | 01445 | 2104 | 014452104 | 014452104 | 9
0121401104 | 10 | 01214 | 1104 | 012141104 | 012141104 | 9
042490401 | 9 |  |  | 042490401 | 042490401 | 9
042490402 | 9 |  |  | 042490402 | 042490402 | 9
0424901101 | 10 | 04249 | 1101 | 042491101 | 042491101 | 9
0424901102 | 10 | 04249 | 1102 | 042491102 | 042491102 | 9
0434302102 | 10 | 04343 | 2102 | 043432102 | 043432102 | 9
0434302103 | 10 | 04343 | 2103 | 043432103 | 043432103 | 9
0434302104 | 10 | 04343 | 2104 | 043432104 | 043432104 | 9
0434302105 | 10 | 04343 | 2105 | 043432105 | 043432105 | 9
2546901101 | 10 | 25469 | 1101 | 254691101 | 254691101 | 9
2546901102 | 10 | 25469 | 1102 | 254691102 | 254691102 | 9
2526101101 | 10 | 25261 | 1101 | 252611101 | 252611101 | 9
2526101103 | 10 | 25261 | 1103 | 252611103 | 252611103 | 9
0432001101 | 10 | 04320 | 1101 | 043201101 | 043201101 | 9
0432001102 | 10 | 04320 | 1102 | 043201102 | 043201102 | 9
2526101102 | 10 | 25261 | 1102 | 252611102 | 252611102 | 9
2526101104 | 10 | 25261 | 1104 | 252611104 | 252611104 | 9
0423001101 | 10 | 04230 | 1101 | 042301101 | 042301101 | 9
0131501101 | 10 | 01315 | 1101 | 013151101 | 013151101 | 9
0131501102 | 10 | 01315 | 1102 | 013151102 | 013151102 | 9
0131501105 | 10 | 01315 | 1105 | 013151105 | 013151105 | 9
0142401101 | 10 | 01424 | 1101 | 014241101 | 014241101 | 9
0137501102 | 10 | 01375 | 1102 | 013751102 | 013751102 | 9
0137501101 | 10 | 01375 | 1101 | 013751101 | 013751101 | 9
0137501103 | 10 | 01375 | 1103 | 013751103 | 013751103 | 9
0820201101 | 10 | 08202 | 1101 | 082021101 | 082021101 | 9
1624701101 | 10 | 16247 | 1101 | 162471101 | 162471101 | 9
1624701102 | 10 | 16247 | 1102 | 162471102 | 162471102 | 9
083260401 | 9 |  |  | 083260401 | 083260401 | 9
083260402 | 9 |  |  | 083260402 | 083260402 | 9
022680401 | 9 |  |  | 022680401 | 022680401 | 9
1624701103 | 10 | 16247 | 1103 | 162471103 | 162471103 | 9
0820201102 | 10 | 08202 | 1102 | 082021102 | 082021102 | 9
0836902104 | 10 | 08369 | 2104 | 083692104 | 083692104 | 9
1637401102 | 10 | 16374 | 1102 | 163741102 | 163741102 | 9
1637401103 | 10 | 16374 | 1103 | 163741103 | 163741103 | 9
163220401 | 9 |  |  | 163220401 | 163220401 | 9
163220402 | 9 |  |  | 163220402 | 163220402 | 9
1630801102 | 10 | 16308 | 1102 | 163081102 | 163081102 | 9
0131101102 | 10 | 01311 | 1102 | 013111102 | 013111102 | 9
0131101103 | 10 | 01311 | 1103 | 013111103 | 013111103 | 9
0131101104 | 10 | 01311 | 1104 | 013111104 | 013111104 | 9
162370406 | 9 |  |  | 162370406 | 162370406 | 9
162370407 | 9 |  |  | 162370407 | 162370407 | 9
162370409 | 9 |  |  | 162370409 | 162370409 | 9
0131101110 | 10 | 01311 | 1110 | 013111110 | 013111110 | 9
162370410 | 9 |  |  | 162370410 | 162370410 | 9
1637001109 | 10 | 16370 | 1109 | 163701109 | 163701109 | 9
162370411 | 9 |  |  | 162370411 | 162370411 | 9
1637001110 | 10 | 16370 | 1110 | 163701110 | 163701110 | 9
1630201102 | 10 | 16302 | 1102 | 163021102 | 163021102 | 9
1630201103 | 10 | 16302 | 1103 | 163021103 | 163021103 | 9
0131101105 | 10 | 01311 | 1105 | 013111105 | 013111105 | 9
0131101106 | 10 | 01311 | 1106 | 013111106 | 013111106 | 9
0131101107 | 10 | 01311 | 1107 | 013111107 | 013111107 | 9
0227201101 | 10 | 02272 | 1101 | 022721101 | 022721101 | 9
0227201102 | 10 | 02272 | 1102 | 022721102 | 022721102 | 9
0227201106 | 10 | 02272 | 1106 | 022721106 | 022721106 | 9
0631301105 | 10 | 06313 | 1105 | 063131105 | 063131105 | 9
022580401 | 9 |  |  | 022580401 | 022580401 | 9
2534101101 | 10 | 25341 | 1101 | 253411101 | 253411101 | 9
2534101102 | 10 | 25341 | 1102 | 253411102 | 253411102 | 9
2534101103 | 10 | 25341 | 1103 | 253411103 | 253411103 | 9
0631301106 | 10 | 06313 | 1106 | 063131106 | 063131106 | 9
0631301107 | 10 | 06313 | 1107 | 063131107 | 063131107 | 9
022580402 | 9 |  |  | 022580402 | 022580402 | 9
2552602101 | 10 | 25526 | 2101 | 255262101 | 255262101 | 9
2552602103 | 10 | 25526 | 2103 | 255262103 | 255262103 | 9
2552602104 | 10 | 25526 | 2104 | 255262104 | 255262104 | 9
2552602105 | 10 | 25526 | 2105 | 255262105 | 255262105 | 9
0227201107 | 10 | 02272 | 1107 | 022721107 | 022721107 | 9
0631301108 | 10 | 06313 | 1108 | 063131108 | 063131108 | 9
0228601103 | 10 | 02286 | 1103 | 022861103 | 022861103 | 9
0228601104 | 10 | 02286 | 1104 | 022861104 | 022861104 | 9
0631301109 | 10 | 06313 | 1109 | 063131109 | 063131109 | 9
1827402104 | 10 | 18274 | 2104 | 182742104 | 182742104 | 9
083500401 | 9 |  |  | 083500401 | 083500401 | 9
024190404 | 9 |  |  | 024190404 | 024190404 | 9
024190407 | 9 |  |  | 024190407 | 024190407 | 9
024190408 | 9 |  |  | 024190408 | 024190408 | 9
2545001102 | 10 | 25450 | 1102 | 254501102 | 254501102 | 9
0631301110 | 10 | 06313 | 1110 | 063131110 | 063131110 | 9
0631301111 | 10 | 06313 | 1111 | 063131111 | 063131111 | 9
1620801101 | 10 | 16208 | 1101 | 162081101 | 162081101 | 9
0131101109 | 10 | 01311 | 1109 | 013111109 | 013111109 | 9
0131101111 | 10 | 01311 | 1111 | 013111111 | 013111111 | 9
1620801102 | 10 | 16208 | 1102 | 162081102 | 162081102 | 9
0131101112 | 10 | 01311 | 1112 | 013111112 | 013111112 | 9
0131101113 | 10 | 01311 | 1113 | 013111113 | 013111113 | 9
1035301103 | 10 | 10353 | 1103 | 103531103 | 103531103 | 9
0836902105 | 10 | 08369 | 2105 | 083692105 | 083692105 | 9
083750401 | 9 |  |  | 083750401 | 083750401 | 9
083750402 | 9 |  |  | 083750402 | 083750402 | 9
1826301105 | 10 | 18263 | 1105 | 182631105 | 182631105 | 9
1826301107 | 10 | 18263 | 1107 | 182631107 | 182631107 | 9
1826301108 | 10 | 18263 | 1108 | 182631108 | 182631108 | 9
1826601104 | 10 | 18266 | 1104 | 182661104 | 182661104 | 9
1826601105 | 10 | 18266 | 1105 | 182661105 | 182661105 | 9
1826601106 | 10 | 18266 | 1106 | 182661106 | 182661106 | 9
1826601107 | 10 | 18266 | 1107 | 182661107 | 182661107 | 9
1826701105 | 10 | 18267 | 1105 | 182671105 | 182671105 | 9
1826701106 | 10 | 18267 | 1106 | 182671106 | 182671106 | 9
1826701107 | 10 | 18267 | 1107 | 182671107 | 182671107 | 9
1826701108 | 10 | 18267 | 1108 | 182671108 | 182671108 | 9
1826701109 | 10 | 18267 | 1109 | 182671109 | 182671109 | 9
1820101101 | 10 | 18201 | 1101 | 182011101 | 182011101 | 9
0636001105 | 10 | 06360 | 1105 | 063601105 | 063601105 | 9
1820101102 | 10 | 18201 | 1102 | 182011102 | 182011102 | 9
0636001106 | 10 | 06360 | 1106 | 063601106 | 063601106 | 9
1820101106 | 10 | 18201 | 1106 | 182011106 | 182011106 | 9
1820101107 | 10 | 18201 | 1107 | 182011107 | 182011107 | 9
0636001107 | 10 | 06360 | 1107 | 063601107 | 063601107 | 9
0636001108 | 10 | 06360 | 1108 | 063601108 | 063601108 | 9
0636001109 | 10 | 06360 | 1109 | 063601109 | 063601109 | 9
0636001110 | 10 | 06360 | 1110 | 063601110 | 063601110 | 9
0636001111 | 10 | 06360 | 1111 | 063601111 | 063601111 | 9
1820101103 | 10 | 18201 | 1103 | 182011103 | 182011103 | 9
1820101104 | 10 | 18201 | 1104 | 182011104 | 182011104 | 9
1820101105 | 10 | 18201 | 1105 | 182011105 | 182011105 | 9
0636001112 | 10 | 06360 | 1112 | 063601112 | 063601112 | 9
1820101108 | 10 | 18201 | 1108 | 182011108 | 182011108 | 9
1820101109 | 10 | 18201 | 1109 | 182011109 | 182011109 | 9
1821901101 | 10 | 18219 | 1101 | 182191101 | 182191101 | 9
04255401 | 8 | 04255 | 401 | 042550401 | 042550401 | 9
1821901102 | 10 | 18219 | 1102 | 182191102 | 182191102 | 9
0430201101 | 10 | 04302 | 1101 | 043021101 | 043021101 | 9
1827402101 | 10 | 18274 | 2101 | 182742101 | 182742101 | 9
0430201102 | 10 | 04302 | 1102 | 043021102 | 043021102 | 9
0620401102 | 10 | 06204 | 1102 | 062041102 | 062041102 | 9
0620401103 | 10 | 06204 | 1103 | 062041103 | 062041103 | 9
1827402102 | 10 | 18274 | 2102 | 182742102 | 182742102 | 9
1827402103 | 10 | 18274 | 2103 | 182742103 | 182742103 | 9
0620401104 | 10 | 06204 | 1104 | 062041104 | 062041104 | 9
0620401105 | 10 | 06204 | 1105 | 062041105 | 062041105 | 9
0620401106 | 10 | 06204 | 1106 | 062041106 | 062041106 | 9
0620401107 | 10 | 06204 | 1107 | 062041107 | 062041107 | 9
0620401108 | 10 | 06204 | 1108 | 062041108 | 062041108 | 9
013700401 | 9 |  |  | 013700401 | 013700401 | 9
0620401109 | 10 | 06204 | 1109 | 062041109 | 062041109 | 9
1028401101 | 10 | 10284 | 1101 | 102841101 | 102841101 | 9
0620401110 | 10 | 06204 | 1110 | 062041110 | 062041110 | 9
1028401102 | 10 | 10284 | 1102 | 102841102 | 102841102 | 9
012540401 | 9 |  |  | 012540401 | 012540401 | 9
012540402 | 9 |  |  | 012540402 | 012540402 | 9
0620401111 | 10 | 06204 | 1111 | 062041111 | 062041111 | 9
1028401105 | 10 | 10284 | 1105 | 102841105 | 102841105 | 9
1028401106 | 10 | 10284 | 1106 | 102841106 | 102841106 | 9
2527801101 | 10 | 25278 | 1101 | 252781101 | 252781101 | 9
0121101105 | 10 | 01211 | 1105 | 012111105 | 012111105 | 9
0121101115 | 10 | 01211 | 1115 | 012111115 | 012111115 | 9
0121101116 | 10 | 01211 | 1116 | 012111116 | 012111116 | 9
0121101114 | 10 | 01211 | 1114 | 012111114 | 012111114 | 9
0620401112 | 10 | 06204 | 1112 | 062041112 | 062041112 | 9
2531801104 | 10 | 25318 | 1104 | 253181104 | 253181104 | 9
2531801105 | 10 | 25318 | 1105 | 253181105 | 253181105 | 9
2542101101 | 10 | 25421 | 1101 | 254211101 | 254211101 | 9
2542101102 | 10 | 25421 | 1102 | 254211102 | 254211102 | 9
2527701101 | 10 | 25277 | 1101 | 252771101 | 252771101 | 9
2527701104 | 10 | 25277 | 1104 | 252771104 | 252771104 | 9
2527701105 | 10 | 25277 | 1105 | 252771105 | 252771105 | 9
2527701106 | 10 | 25277 | 1106 | 252771106 | 252771106 | 9
2527701108 | 10 | 25277 | 1108 | 252771108 | 252771108 | 9
1032701101 | 10 | 10327 | 1101 | 103271101 | 103271101 | 9
2527702108 | 10 | 25277 | 2108 | 252772108 | 252772108 | 9
2527702109 | 10 | 25277 | 2109 | 252772109 | 252772109 | 9
1920201124 | 10 | 19202 | 1124 | 192021124 | 192021124 | 9
1022101101 | 10 | 10221 | 1101 | 102211101 | 102211101 | 9
| 0 |  |  |  |  | 0
1022101102 | 10 | 10221 | 1102 | 102211102 | 102211102 | 9
2534901103 | 10 | 25349 | 1103 | 253491103 | 253491103 | 9
2534901104 | 10 | 25349 | 1104 | 253491104 | 253491104 | 9
2534901105 | 10 | 25349 | 1105 | 253491105 | 253491105 | 9
1022101103 | 10 | 10221 | 1103 | 102211103 | 102211103 | 9
0242501101 | 10 | 02425 | 1101 | 024251101 | 024251101 | 9
0242501102 | 10 | 02425 | 1102 | 024251102 | 024251102 | 9
024251104 | 9 |  |  | 024251104 | 024251104 | 9
2534901106 | 10 | 25349 | 1106 | 253491106 | 253491106 | 9
2534901107 | 10 | 25349 | 1107 | 253491107 | 253491107 | 9
2534901108 | 10 | 25349 | 1108 | 253491108 | 253491108 | 9
2534901109 | 10 | 25349 | 1109 | 253491109 | 253491109 | 9
0620401101 | 10 | 06204 | 1101 | 062041101 | 062041101 | 9
2539101102 | 10 | 25391 | 1102 | 253911102 | 253911102 | 9
2539101103 | 10 | 25391 | 1103 | 253911103 | 253911103 | 9
02285402 | 8 | 02285 | 402 | 022850402 | 022850402 | 9
2539101104 | 10 | 25391 | 1104 | 253911104 | 253911104 | 9
2539101105 | 10 | 25391 | 1105 | 253911105 | 253911105 | 9
2539101106 | 10 | 25391 | 1106 | 253911106 | 253911106 | 9
0631301104 | 10 | 06313 | 1104 | 063131104 | 063131104 | 9
2542001103 | 10 | 25420 | 1103 | 254201103 | 254201103 | 9
2542002104 | 10 | 25420 | 2104 | 254202104 | 254202104 | 9
0620301113 | 10 | 06203 | 1113 | 062031113 | 062031113 | 9
0620301101 | 10 | 06203 | 1101 | 062031101 | 062031101 | 9
0620301102 | 10 | 06203 | 1102 | 062031102 | 062031102 | 9
0620301103 | 10 | 06203 | 1103 | 062031103 | 062031103 | 9
0620301104 | 10 | 06203 | 1104 | 062031104 | 062031104 | 9
0620301105 | 10 | 06203 | 1105 | 062031105 | 062031105 | 9
0620301106 | 10 | 06203 | 1106 | 062031106 | 062031106 | 9
0620301107 | 10 | 06203 | 1107 | 062031107 | 062031107 | 9
0620301108 | 10 | 06203 | 1108 | 062031108 | 062031108 | 9
0620301109 | 10 | 06203 | 1109 | 062031109 | 062031109 | 9
0620301110 | 10 | 06203 | 1110 | 062031110 | 062031110 | 9
0620301111 | 10 | 06203 | 1111 | 062031111 | 062031111 | 9
0620301112 | 10 | 06203 | 1112 | 062031112 | 062031112 | 9
022470401 | 9 |  |  | 022470401 | 022470401 | 9
022470402 | 9 |  |  | 022470402 | 022470402 | 9
022510401 | 9 |  |  | 022510401 | 022510401 | 9
022510402 | 9 |  |  | 022510402 | 022510402 | 9
2545001103 | 10 | 25450 | 1103 | 254501103 | 254501103 | 9
162370402 | 9 |  |  | 162370402 | 162370402 | 9
162370403 | 9 |  |  | 162370403 | 162370403 | 9
162370412 | 9 |  |  | 162370412 | 162370412 | 9
013090401 | 9 |  |  | 013090401 | 013090401 | 9
013090402 | 9 |  |  | 013090402 | 013090402 | 9
083500402 | 9 |  |  | 083500402 | 083500402 | 9
1520101102 | 10 | 15201 | 1102 | 152011102 | 152011102 | 9
1520101103 | 10 | 15201 | 1103 | 152011103 | 152011103 | 9
1520101104 | 10 | 15201 | 1104 | 152011104 | 152011104 | 9
1520101105 | 10 | 15201 | 1105 | 152011105 | 152011105 | 9
1520101106 | 10 | 15201 | 1106 | 152011106 | 152011106 | 9
1520101107 | 10 | 15201 | 1107 | 152011107 | 152011107 | 9
1520101108 | 10 | 15201 | 1108 | 152011108 | 152011108 | 9
02419409 | 8 | 02419 | 409 | 024190409 | 024190409 | 9
024190410 | 9 |  |  | 024190410 | 024190410 | 9
1820501114 | 10 | 18205 | 1114 | 182051114 | 182051114 | 9
1820502101 | 10 | 18205 | 2101 | 182052101 | 182052101 | 9
1820502102 | 10 | 18205 | 2102 | 182052102 | 182052102 | 9
2545001106 | 10 | 25450 | 1106 | 254501106 | 254501106 | 9
0636402102 | 10 | 06364 | 2102 | 063642102 | 063642102 | 9
024180401 | 9 |  |  | 024180401 | 024180401 | 9
0636402104 | 10 | 06364 | 2104 | 063642104 | 063642104 | 9
0636402105 | 10 | 06364 | 2105 | 063642105 | 063642105 | 9
0636402106 | 10 | 06364 | 2106 | 063642106 | 063642106 | 9
0636402107 | 10 | 06364 | 2107 | 063642107 | 063642107 | 9
024180402 | 9 |  |  | 024180402 | 024180402 | 9
024180403 | 9 |  |  | 024180403 | 024180403 | 9
0636402108 | 10 | 06364 | 2108 | 063642108 | 063642108 | 9
024180404 | 9 |  |  | 024180404 | 024180404 | 9
0636402109 | 10 | 06364 | 2109 | 063642109 | 063642109 | 9
024180405 | 9 |  |  | 024180405 | 024180405 | 9
024180406 | 9 |  |  | 024180406 | 024180406 | 9
0241801102 | 10 | 02418 | 1102 | 024181102 | 024181102 | 9
0241801104 | 10 | 02418 | 1104 | 024181104 | 024181104 | 9
0241801101 | 10 | 02418 | 1101 | 024181101 | 024181101 | 9
0636402112 | 10 | 06364 | 2112 | 063642112 | 063642112 | 9
0241801103 | 10 | 02418 | 1103 | 024181103 | 024181103 | 9
0636402113 | 10 | 06364 | 2113 | 063642113 | 063642113 | 9
022700401 | 9 |  |  | 022700401 | 022700401 | 9
083300402 | 9 |  |  | 083300402 | 083300402 | 9
022700402 | 9 |  |  | 022700402 | 022700402 | 9
022700403 | 9 |  |  | 022700403 | 022700403 | 9
1822001121 | 10 | 18220 | 1121 | 182201121 | 182201121 | 9
1822001122 | 10 | 18220 | 1122 | 182201122 | 182201122 | 9
1822001123 | 10 | 18220 | 1123 | 182201123 | 182201123 | 9
1828502201 | 10 | 18285 | 2201 | 182852201 | 182852201 | 9
1828502202 | 10 | 18285 | 2202 | 182852202 | 182852202 | 9
162370404 | 9 |  |  | 162370404 | 162370404 | 9
083330411 | 9 |  |  | 083330411 | 083330411 | 9
083330413 | 9 |  |  | 083330413 | 083330413 | 9
083330414 | 9 |  |  | 083330414 | 083330414 | 9
162370405 | 9 |  |  | 162370405 | 162370405 | 9
1623701101 | 10 | 16237 | 1101 | 162371101 | 162371101 | 9
1826801101 | 10 | 18268 | 1101 | 182681101 | 182681101 | 9
1826801102 | 10 | 18268 | 1102 | 182681102 | 182681102 | 9
1623701102 | 10 | 16237 | 1102 | 162371102 | 162371102 | 9
1623701103 | 10 | 16237 | 1103 | 162371103 | 162371103 | 9
1623701104 | 10 | 16237 | 1104 | 162371104 | 162371104 | 9
1623701105 | 10 | 16237 | 1105 | 162371105 | 162371105 | 9
1830502108 | 10 | 18305 | 2108 | 183052108 | 183052108 | 9
0135001101 | 10 | 01350 | 1101 | 013501101 | 013501101 | 9
0135001103 | 10 | 01350 | 1103 | 013501103 | 013501103 | 9
1830502109 | 10 | 18305 | 2109 | 183052109 | 183052109 | 9
0135001104 | 10 | 01350 | 1104 | 013501104 | 013501104 | 9
1830502110 | 10 | 18305 | 2110 | 183052110 | 183052110 | 9
0137601101 | 10 | 01376 | 1101 | 013761101 | 013761101 | 9
0135001105 | 10 | 01350 | 1105 | 013501105 | 013501105 | 9
0135001106 | 10 | 01350 | 1106 | 013501106 | 013501106 | 9
0135001108 | 10 | 01350 | 1108 | 013501108 | 013501108 | 9
1830502111 | 10 | 18305 | 2111 | 183052111 | 183052111 | 9
1830502112 | 10 | 18305 | 2112 | 183052112 | 183052112 | 9
1830502113 | 10 | 18305 | 2113 | 183052113 | 183052113 | 9
0131101114 | 10 | 01311 | 1114 | 013111114 | 013111114 | 9
0137601103 | 10 | 01376 | 1103 | 013761103 | 013761103 | 9
0131101115 | 10 | 01311 | 1115 | 013111115 | 013111115 | 9
0135001109 | 10 | 01350 | 1109 | 013501109 | 013501109 | 9
0137601105 | 10 | 01376 | 1105 | 013761105 | 013761105 | 9
0131101116 | 10 | 01311 | 1116 | 013111116 | 013111116 | 9
0137601109 | 10 | 01376 | 1109 | 013761109 | 013761109 | 9
0135001110 | 10 | 01350 | 1110 | 013501110 | 013501110 | 9
0137601114 | 10 | 01376 | 1114 | 013761114 | 013761114 | 9
0135001111 | 10 | 01350 | 1111 | 013501111 | 013501111 | 9
013460401 | 9 |  |  | 013460401 | 013460401 | 9
013460402 | 9 |  |  | 013460402 | 013460402 | 9
0135001112 | 10 | 01350 | 1112 | 013501112 | 013501112 | 9
013260401 | 9 |  |  | 013260401 | 013260401 | 9
013260402 | 9 |  |  | 013260402 | 013260402 | 9
0824602106 | 10 | 08246 | 2106 | 082462106 | 082462106 | 9
0824602107 | 10 | 08246 | 2107 | 082462107 | 082462107 | 9
0824602109 | 10 | 08246 | 2109 | 082462109 | 082462109 | 9
0824602110 | 10 | 08246 | 2110 | 082462110 | 082462110 | 9
0824602111 | 10 | 08246 | 2111 | 082462111 | 082462111 | 9
0122201101 | 10 | 01222 | 1101 | 012221101 | 012221101 | 9
0122201102 | 10 | 01222 | 1102 | 012221102 | 012221102 | 9
0122201103 | 10 | 01222 | 1103 | 012221103 | 012221103 | 9
0122201104 | 10 | 01222 | 1104 | 012221104 | 012221104 | 9
0122201105 | 10 | 01222 | 1105 | 012221105 | 012221105 | 9
0122201106 | 10 | 01222 | 1106 | 012221106 | 012221106 | 9
0122201107 | 10 | 01222 | 1107 | 012221107 | 012221107 | 9
0122201108 | 10 | 01222 | 1108 | 012221108 | 012221108 | 9
0122202107 | 10 | 01222 | 2107 | 012222107 | 012222107 | 9
0122202108 | 10 | 01222 | 2108 | 012222108 | 012222108 | 9
0122202109 | 10 | 01222 | 2109 | 012222109 | 012222109 | 9
0122202110 | 10 | 01222 | 2110 | 012222110 | 012222110 | 9
1828101101 | 10 | 18281 | 1101 | 182811101 | 182811101 | 9
1828101102 | 10 | 18281 | 1102 | 182811102 | 182811102 | 9
1828101103 | 10 | 18281 | 1103 | 182811103 | 182811103 | 9
1828101104 | 10 | 18281 | 1104 | 182811104 | 182811104 | 9
1827201101 | 10 | 18272 | 1101 | 182721101 | 182721101 | 9
1827201102 | 10 | 18272 | 1102 | 182721102 | 182721102 | 9
1827201104 | 10 | 18272 | 1104 | 182721104 | 182721104 | 9
1623701106 | 10 | 16237 | 1106 | 162371106 | 162371106 | 9
1623701107 | 10 | 16237 | 1107 | 162371107 | 162371107 | 9
1623701108 | 10 | 16237 | 1108 | 162371108 | 162371108 | 9
1622101101 | 10 | 16221 | 1101 | 162211101 | 162211101 | 9
1623701109 | 10 | 16237 | 1109 | 162371109 | 162371109 | 9
1630901101 | 10 | 16309 | 1101 | 163091101 | 163091101 | 9
1623701110 | 10 | 16237 | 1110 | 162371110 | 162371110 | 9
1623701111 | 10 | 16237 | 1111 | 162371111 | 162371111 | 9
1630901103 | 10 | 16309 | 1103 | 163091103 | 163091103 | 9
0228101103 | 10 | 02281 | 1103 | 022811103 | 022811103 | 9
0636201108 | 10 | 06362 | 1108 | 063621108 | 063621108 | 9
0228101104 | 10 | 02281 | 1104 | 022811104 | 022811104 | 9
0636201109 | 10 | 06362 | 1109 | 063621109 | 063621109 | 9
0131101108 | 10 | 01311 | 1108 | 013111108 | 013111108 | 9
1631201105 | 10 | 16312 | 1105 | 163121105 | 163121105 | 9
1631201106 | 10 | 16312 | 1106 | 163121106 | 163121106 | 9
022690401 | 9 |  |  | 022690401 | 022690401 | 9
022690403 | 9 |  |  | 022690403 | 022690403 | 9
1639102104 | 10 | 16391 | 2104 | 163912104 | 163912104 | 9
2542001106 | 10 | 25420 | 1106 | 254201106 | 254201106 | 9
022690404 | 9 |  |  | 022690404 | 022690404 | 9
1639102105 | 10 | 16391 | 2105 | 163912105 | 163912105 | 9
1639102106 | 10 | 16391 | 2106 | 163912106 | 163912106 | 9
0140901101 | 10 | 01409 | 1101 | 014091101 | 014091101 | 9
1639102101 | 10 | 16391 | 2101 | 163912101 | 163912101 | 9
1639102102 | 10 | 16391 | 2102 | 163912102 | 163912102 | 9
1639102103 | 10 | 16391 | 2103 | 163912103 | 163912103 | 9
1634801101 | 10 | 16348 | 1101 | 163481101 | 163481101 | 9
0140901102 | 10 | 01409 | 1102 | 014091102 | 014091102 | 9
1634801105 | 10 | 16348 | 1105 | 163481105 | 163481105 | 9
2527201103 | 10 | 25272 | 1103 | 252721103 | 252721103 | 9
1634801112 | 10 | 16348 | 1112 | 163481112 | 163481112 | 9
1621601101 | 10 | 16216 | 1101 | 162161101 | 162161101 | 9
2527201107 | 10 | 25272 | 1107 | 252721107 | 252721107 | 9
0140901103 | 10 | 01409 | 1103 | 014091103 | 014091103 | 9
1634801113 | 10 | 16348 | 1113 | 163481113 | 163481113 | 9
0140901104 | 10 | 01409 | 1104 | 014091104 | 014091104 | 9
1630901104 | 10 | 16309 | 1104 | 163091104 | 163091104 | 9
012240401 | 9 |  |  | 012240401 | 012240401 | 9
012240402 | 9 |  |  | 012240402 | 012240402 | 9
1630901102 | 10 | 16309 | 1102 | 163091102 | 163091102 | 9
012980401 | 9 |  |  | 012980401 | 012980401 | 9
1633401101 | 10 | 16334 | 1101 | 163341101 | 163341101 | 9
0137601102 | 10 | 01376 | 1102 | 013761102 | 013761102 | 9
0137601104 | 10 | 01376 | 1104 | 013761104 | 013761104 | 9
0137601106 | 10 | 01376 | 1106 | 013761106 | 013761106 | 9
1633401102 | 10 | 16334 | 1102 | 163341102 | 163341102 | 9
0137601107 | 10 | 01376 | 1107 | 013761107 | 013761107 | 9
0137601108 | 10 | 01376 | 1108 | 013761108 | 013761108 | 9
1633401103 | 10 | 16334 | 1103 | 163341103 | 163341103 | 9
0137601110 | 10 | 01376 | 1110 | 013761110 | 013761110 | 9
0241601101 | 10 | 02416 | 1101 | 024161101 | 024161101 | 9
0241601102 | 10 | 02416 | 1102 | 024161102 | 024161102 | 9
024160402 | 9 |  |  | 024160402 | 024160402 | 9
163120401 | 9 |  |  | 163120401 | 163120401 | 9
1636201101 | 10 | 16362 | 1101 | 163621101 | 163621101 | 9
1636201102 | 10 | 16362 | 1102 | 163621102 | 163621102 | 9
0137601111 | 10 | 01376 | 1111 | 013761111 | 013761111 | 9
1636201103 | 10 | 16362 | 1103 | 163621103 | 163621103 | 9
1631501101 | 10 | 16315 | 1101 | 163151101 | 163151101 | 9
1631501102 | 10 | 16315 | 1102 | 163151102 | 163151102 | 9
0137601112 | 10 | 01376 | 1112 | 013761112 | 013761112 | 9
0137601113 | 10 | 01376 | 1113 | 013761113 | 013761113 | 9
163120402 | 9 |  |  | 163120402 | 163120402 | 9
163120403 | 9 |  |  | 163120403 | 163120403 | 9
1631201101 | 10 | 16312 | 1101 | 163121101 | 163121101 | 9
024160403 | 9 |  |  | 024160403 | 024160403 | 9
1631201102 | 10 | 16312 | 1102 | 163121102 | 163121102 | 9
024160405 | 9 |  |  | 024160405 | 024160405 | 9
024160404 | 9 |  |  | 024160404 | 024160404 | 9
024160406 | 9 |  |  | 024160406 | 024160406 | 9
024160408 | 9 |  |  | 024160408 | 024160408 | 9
02416409 | 8 | 02416 | 409 | 024160409 | 024160409 | 9
024160410 | 9 |  |  | 024160410 | 024160410 | 9
0241601104 | 10 | 02416 | 1104 | 024161104 | 024161104 | 9
1631201103 | 10 | 16312 | 1103 | 163121103 | 163121103 | 9
0241601105 | 10 | 02416 | 1105 | 024161105 | 024161105 | 9
1631201104 | 10 | 16312 | 1104 | 163121104 | 163121104 | 9
0241601106 | 10 | 02416 | 1106 | 024161106 | 024161106 | 9
0636201105 | 10 | 06362 | 1105 | 063621105 | 063621105 | 9
0241401101 | 10 | 02414 | 1101 | 024141101 | 024141101 | 9
0241401102 | 10 | 02414 | 1102 | 024141102 | 024141102 | 9
0636201106 | 10 | 06362 | 1106 | 063621106 | 063621106 | 9
0228101101 | 10 | 02281 | 1101 | 022811101 | 022811101 | 9
0228101102 | 10 | 02281 | 1102 | 022811102 | 022811102 | 9
0636201107 | 10 | 06362 | 1107 | 063621107 | 063621107 | 9
2527201109 | 10 | 25272 | 1109 | 252721109 | 252721109 | 9
1634801114 | 10 | 16348 | 1114 | 163481114 | 163481114 | 9
0140901105 | 10 | 01409 | 1105 | 014091105 | 014091105 | 9
0634401101 | 10 | 06344 | 1101 | 063441101 | 063441101 | 9
0634401105 | 10 | 06344 | 1105 | 063441105 | 063441105 | 9
0140901106 | 10 | 01409 | 1106 | 014091106 | 014091106 | 9
0140901107 | 10 | 01409 | 1107 | 014091107 | 014091107 | 9
0140901108 | 10 | 01409 | 1108 | 014091108 | 014091108 | 9
0140901109 | 10 | 01409 | 1109 | 014091109 | 014091109 | 9
0226901102 | 10 | 02269 | 1102 | 022691102 | 022691102 | 9
0634401106 | 10 | 06344 | 1106 | 063441106 | 063441106 | 9
0226901103 | 10 | 02269 | 1103 | 022691103 | 022691103 | 9
1621601102 | 10 | 16216 | 1102 | 162161102 | 162161102 | 9
1634801102 | 10 | 16348 | 1102 | 163481102 | 163481102 | 9
1634801103 | 10 | 16348 | 1103 | 163481103 | 163481103 | 9
1634801106 | 10 | 16348 | 1106 | 163481106 | 163481106 | 9
1634801107 | 10 | 16348 | 1107 | 163481107 | 163481107 | 9
1634801108 | 10 | 16348 | 1108 | 163481108 | 163481108 | 9
0226901106 | 10 | 02269 | 1106 | 022691106 | 022691106 | 9
1634801109 | 10 | 16348 | 1109 | 163481109 | 163481109 | 9
0147202101 | 10 | 01472 | 2101 | 014722101 | 014722101 | 9
1634801110 | 10 | 16348 | 1110 | 163481110 | 163481110 | 9
1634801111 | 10 | 16348 | 1111 | 163481111 | 163481111 | 9
0226901108 | 10 | 02269 | 1108 | 022691108 | 022691108 | 9
0226901101 | 10 | 02269 | 1101 | 022691101 | 022691101 | 9
0147202102 | 10 | 01472 | 2102 | 014722102 | 014722102 | 9
0226901104 | 10 | 02269 | 1104 | 022691104 | 022691104 | 9
0147202103 | 10 | 01472 | 2103 | 014722103 | 014722103 | 9
0226901105 | 10 | 02269 | 1105 | 022691105 | 022691105 | 9
0226901107 | 10 | 02269 | 1107 | 022691107 | 022691107 | 9
0143801102 | 10 | 01438 | 1102 | 014381102 | 014381102 | 9
0143801103 | 10 | 01438 | 1103 | 014381103 | 014381103 | 9
0143801104 | 10 | 01438 | 1104 | 014381104 | 014381104 | 9
1826701110 | 10 | 18267 | 1110 | 182671110 | 182671110 | 9
1826701111 | 10 | 18267 | 1111 | 182671111 | 182671111 | 9
0143801105 | 10 | 01438 | 1105 | 014381105 | 014381105 | 9
0143801107 | 10 | 01438 | 1107 | 014381107 | 014381107 | 9
0143801106 | 10 | 01438 | 1106 | 014381106 | 014381106 | 9
1826701112 | 10 | 18267 | 1112 | 182671112 | 182671112 | 9
1634501701 | 10 | 16345 | 1701 | 163451701 | 163451701 | 9
0241301101 | 10 | 02413 | 1101 | 024131101 | 024131101 | 9
0241301102 | 10 | 02413 | 1102 | 024131102 | 024131102 | 9
0143801108 | 10 | 01438 | 1108 | 014381108 | 014381108 | 9
0241301103 | 10 | 02413 | 1103 | 024131103 | 024131103 | 9
0241301104 | 10 | 02413 | 1104 | 024131104 | 024131104 | 9
022440401 | 9 |  |  | 022440401 | 022440401 | 9
022440402 | 9 |  |  | 022440402 | 022440402 | 9
1825701101 | 10 | 18257 | 1101 | 182571101 | 182571101 | 9
1825701102 | 10 | 18257 | 1102 | 182571102 | 182571102 | 9
1825701103 | 10 | 18257 | 1103 | 182571103 | 182571103 | 9
024110401 | 9 |  |  | 024110401 | 024110401 | 9
024110402 | 9 |  |  | 024110402 | 024110402 | 9
024110403 | 9 |  |  | 024110403 | 024110403 | 9
024110404 | 9 |  |  | 024110404 | 024110404 | 9
024110405 | 9 |  |  | 024110405 | 024110405 | 9
0241001102 | 10 | 02410 | 1102 | 024101102 | 024101102 | 9
0241001101 | 10 | 02410 | 1101 | 024101101 | 024101101 | 9
0241001103 | 10 | 02410 | 1103 | 024101103 | 024101103 | 9
0143501106 | 10 | 01435 | 1106 | 014351106 | 014351106 | 9
0143501107 | 10 | 01435 | 1107 | 014351107 | 014351107 | 9
0143501108 | 10 | 01435 | 1108 | 014351108 | 014351108 | 9
0143501109 | 10 | 01435 | 1109 | 014351109 | 014351109 | 9
1529001101 | 10 | 15290 | 1101 | 152901101 | 152901101 | 9
1529001102 | 10 | 15290 | 1102 | 152901102 | 152901102 | 9
1529001103 | 10 | 15290 | 1103 | 152901103 | 152901103 | 9
1529001104 | 10 | 15290 | 1104 | 152901104 | 152901104 | 9
1529001105 | 10 | 15290 | 1105 | 152901105 | 152901105 | 9
1537501101 | 10 | 15375 | 1101 | 153751101 | 153751101 | 9
1537501102 | 10 | 15375 | 1102 | 153751102 | 153751102 | 9
1537501103 | 10 | 15375 | 1103 | 153751103 | 153751103 | 9
1537501104 | 10 | 15375 | 1104 | 153751104 | 153751104 | 9
1537501105 | 10 | 15375 | 1105 | 153751105 | 153751105 | 9
0144502105 | 10 | 01445 | 2105 | 014452105 | 014452105 | 9
0144502106 | 10 | 01445 | 2106 | 014452106 | 014452106 | 9
0141601105 | 10 | 01416 | 1105 | 014161105 | 014161105 | 9
0141601106 | 10 | 01416 | 1106 | 014161106 | 014161106 | 9
0141601107 | 10 | 01416 | 1107 | 014161107 | 014161107 | 9
0141601108 | 10 | 01416 | 1108 | 014161108 | 014161108 | 9
153731101 | 9 |  |  | 153731101 | 153731101 | 9
153731102 | 9 |  |  | 153731102 | 153731102 | 9
0140502101 | 10 | 01405 | 2101 | 014052101 | 014052101 | 9
0140502103 | 10 | 01405 | 2103 | 014052103 | 014052103 | 9
0147202105 | 10 | 01472 | 2105 | 014722105 | 014722105 | 9
0147202106 | 10 | 01472 | 2106 | 014722106 | 014722106 | 9
0147202107 | 10 | 01472 | 2107 | 014722107 | 014722107 | 9
1537302106 | 10 | 15373 | 2106 | 153732106 | 153732106 | 9
1537302107 | 10 | 15373 | 2107 | 153732107 | 153732107 | 9
2552902105 | 10 | 25529 | 2105 | 255292105 | 255292105 | 9
0142302101 | 10 | 01423 | 2101 | 014232101 | 014232101 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0142302102 | 10 | 01423 | 2102 | 014232102 | 014232102 | 9
2552902106 | 10 | 25529 | 2106 | 255292106 | 255292106 | 9
0142302103 | 10 | 01423 | 2103 | 014232103 | 014232103 | 9
0147202109 | 10 | 01472 | 2109 | 014722109 | 014722109 | 9
0147202110 | 10 | 01472 | 2110 | 014722110 | 014722110 | 9
0147202111 | 10 | 01472 | 2111 | 014722111 | 014722111 | 9
0142302104 | 10 | 01423 | 2104 | 014232104 | 014232104 | 9
1537701101 | 10 | 15377 | 1101 | 153771101 | 153771101 | 9
1537701102 | 10 | 15377 | 1102 | 153771102 | 153771102 | 9
0142302105 | 10 | 01423 | 2105 | 014232105 | 014232105 | 9
1537701104 | 10 | 15377 | 1104 | 153771104 | 153771104 | 9
0142302106 | 10 | 01423 | 2106 | 014232106 | 014232106 | 9
0142302107 | 10 | 01423 | 2107 | 014232107 | 014232107 | 9
0142302108 | 10 | 01423 | 2108 | 014232108 | 014232108 | 9
0628301101 | 10 | 06283 | 1101 | 062831101 | 062831101 | 9
0628301102 | 10 | 06283 | 1102 | 062831102 | 062831102 | 9
0628301103 | 10 | 06283 | 1103 | 062831103 | 062831103 | 9
0142302110 | 10 | 01423 | 2110 | 014232110 | 014232110 | 9
0142302111 | 10 | 01423 | 2111 | 014232111 | 014232111 | 9
0142302112 | 10 | 01423 | 2112 | 014232112 | 014232112 | 9
0142302113 | 10 | 01423 | 2113 | 014232113 | 014232113 | 9
0142302114 | 10 | 01423 | 2114 | 014232114 | 014232114 | 9
1537801102 | 10 | 15378 | 1102 | 153781102 | 153781102 | 9
0142302116 | 10 | 01423 | 2116 | 014232116 | 014232116 | 9
0142302117 | 10 | 01423 | 2117 | 014232117 | 014232117 | 9
1537801103 | 10 | 15378 | 1103 | 153781103 | 153781103 | 9
1537801104 | 10 | 15378 | 1104 | 153781104 | 153781104 | 9
0142302118 | 10 | 01423 | 2118 | 014232118 | 014232118 | 9
1537801105 | 10 | 15378 | 1105 | 153781105 | 153781105 | 9
1537801106 | 10 | 15378 | 1106 | 153781106 | 153781106 | 9
0142302119 | 10 | 01423 | 2119 | 014232119 | 014232119 | 9
1537801107 | 10 | 15378 | 1107 | 153781107 | 153781107 | 9
0145002104 | 10 | 01450 | 2104 | 014502104 | 014502104 | 9
0145002105 | 10 | 01450 | 2105 | 014502105 | 014502105 | 9
0145002106 | 10 | 01450 | 2106 | 014502106 | 014502106 | 9
0145002107 | 10 | 01450 | 2107 | 014502107 | 014502107 | 9
0145002108 | 10 | 01450 | 2108 | 014502108 | 014502108 | 9
0145002109 | 10 | 01450 | 2109 | 014502109 | 014502109 | 9
0145002110 | 10 | 01450 | 2110 | 014502110 | 014502110 | 9
0620601102 | 10 | 06206 | 1102 | 062061102 | 062061102 | 9
0620601103 | 10 | 06206 | 1103 | 062061103 | 062061103 | 9
0620601104 | 10 | 06206 | 1104 | 062061104 | 062061104 | 9
0620601105 | 10 | 06206 | 1105 | 062061105 | 062061105 | 9
0620601106 | 10 | 06206 | 1106 | 062061106 | 062061106 | 9
0624602226 | 10 | 06246 | 2226 | 062462226 | 062462226 | 9
0624602227 | 10 | 06246 | 2227 | 062462227 | 062462227 | 9
0624602225 | 10 | 06246 | 2225 | 062462225 | 062462225 | 9
0624602223 | 10 | 06246 | 2223 | 062462223 | 062462223 | 9
0624602224 | 10 | 06246 | 2224 | 062462224 | 062462224 | 9
0636801105 | 10 | 06368 | 1105 | 063681105 | 063681105 | 9
0636801103 | 10 | 06368 | 1103 | 063681103 | 063681103 | 9
0636801102 | 10 | 06368 | 1102 | 063681102 | 063681102 | 9
0627701101 | 10 | 06277 | 1101 | 062771101 | 062771101 | 9
0627701102 | 10 | 06277 | 1102 | 062771102 | 062771102 | 9
0627701103 | 10 | 06277 | 1103 | 062771103 | 062771103 | 9
0620501102 | 10 | 06205 | 1102 | 062051102 | 062051102 | 9
0620501101 | 10 | 06205 | 1101 | 062051101 | 062051101 | 9
0633201101 | 10 | 06332 | 1101 | 063321101 | 063321101 | 9
0633201102 | 10 | 06332 | 1102 | 063321102 | 063321102 | 9
1030801103 | 10 | 10308 | 1103 | 103081103 | 103081103 | 9
1030801104 | 10 | 10308 | 1104 | 103081104 | 103081104 | 9
1030801105 | 10 | 10308 | 1105 | 103081105 | 103081105 | 9
1030801106 | 10 | 10308 | 1106 | 103081106 | 103081106 | 9
1030801107 | 10 | 10308 | 1107 | 103081107 | 103081107 | 9
1033201101 | 10 | 10332 | 1101 | 103321101 | 103321101 | 9
1031801101 | 10 | 10318 | 1101 | 103181101 | 103181101 | 9
1031801102 | 10 | 10318 | 1102 | 103181102 | 103181102 | 9
1030901101 | 10 | 10309 | 1101 | 103091101 | 103091101 | 9
1030901102 | 10 | 10309 | 1102 | 103091102 | 103091102 | 9
1021701101 | 10 | 10217 | 1101 | 102171101 | 102171101 | 9
1021701102 | 10 | 10217 | 1102 | 102171102 | 102171102 | 9
1021701103 | 10 | 10217 | 1103 | 102171103 | 102171103 | 9
1634501702 | 10 | 16345 | 1702 | 163451702 | 163451702 | 9
163310401 | 9 |  |  | 163310401 | 163310401 | 9
163310402 | 9 |  |  | 163310402 | 163310402 | 9
163310403 | 9 |  |  | 163310403 | 163310403 | 9
163310404 | 9 |  |  | 163310404 | 163310404 | 9
163310405 | 9 |  |  | 163310405 | 163310405 | 9
163310406 | 9 |  |  | 163310406 | 163310406 | 9
1638801101 | 10 | 16388 | 1101 | 163881101 | 163881101 | 9
1627701101 | 10 | 16277 | 1101 | 162771101 | 162771101 | 9
1627701102 | 10 | 16277 | 1102 | 162771102 | 162771102 | 9
1627701103 | 10 | 16277 | 1103 | 162771103 | 162771103 | 9
1627701105 | 10 | 16277 | 1105 | 162771105 | 162771105 | 9
1627701106 | 10 | 16277 | 1106 | 162771106 | 162771106 | 9
1627701107 | 10 | 16277 | 1107 | 162771107 | 162771107 | 9
1620701101 | 10 | 16207 | 1101 | 162071101 | 162071101 | 9
1620701102 | 10 | 16207 | 1102 | 162071102 | 162071102 | 9
1620701103 | 10 | 16207 | 1103 | 162071103 | 162071103 | 9
1620701104 | 10 | 16207 | 1104 | 162071104 | 162071104 | 9
1636802101 | 10 | 16368 | 2101 | 163682101 | 163682101 | 9
1636802102 | 10 | 16368 | 2102 | 163682102 | 163682102 | 9
1621101101 | 10 | 16211 | 1101 | 162111101 | 162111101 | 9
1621101102 | 10 | 16211 | 1102 | 162111102 | 162111102 | 9
0240901101 | 10 | 02409 | 1101 | 024091101 | 024091101 | 9
024090404 | 9 |  |  | 024090404 | 024090404 | 9
024090405 | 9 |  |  | 024090405 | 024090405 | 9
024090406 | 9 |  |  | 024090406 | 024090406 | 9
0240901102 | 10 | 02409 | 1102 | 024091102 | 024091102 | 9
024080401 | 9 |  |  | 024080401 | 024080401 | 9
024080402 | 9 |  |  | 024080402 | 024080402 | 9
1033401101 | 10 | 10334 | 1101 | 103341101 | 103341101 | 9
1035401105 | 10 | 10354 | 1105 | 103541105 | 103541105 | 9
1626101702 | 10 | 16261 | 1702 | 162611702 | 162611702 | 9
1626101703 | 10 | 16261 | 1703 | 162611703 | 162611703 | 9
1626101704 | 10 | 16261 | 1704 | 162611704 | 162611704 | 9
1626101705 | 10 | 16261 | 1705 | 162611705 | 162611705 | 9
1626101701 | 10 | 16261 | 1701 | 162611701 | 162611701 | 9
1626101706 | 10 | 16261 | 1706 | 162611706 | 162611706 | 9
1626101707 | 10 | 16261 | 1707 | 162611707 | 162611707 | 9
1626101708 | 10 | 16261 | 1708 | 162611708 | 162611708 | 9
1630101101 | 10 | 16301 | 1101 | 163011101 | 163011101 | 9
1630101102 | 10 | 16301 | 1102 | 163011102 | 163011102 | 9
1630101103 | 10 | 16301 | 1103 | 163011103 | 163011103 | 9
0820102101 | 10 | 08201 | 2101 | 082012101 | 082012101 | 9
1620901101 | 10 | 16209 | 1101 | 162091101 | 162091101 | 9
0820102102 | 10 | 08201 | 2102 | 082012102 | 082012102 | 9
1620901102 | 10 | 16209 | 1102 | 162091102 | 162091102 | 9
1620901103 | 10 | 16209 | 1103 | 162091103 | 162091103 | 9
162300401 | 9 |  |  | 162300401 | 162300401 | 9
162300402 | 9 |  |  | 162300402 | 162300402 | 9
162300403 | 9 |  |  | 162300403 | 162300403 | 9
0820102103 | 10 | 08201 | 2103 | 082012103 | 082012103 | 9
1632101101 | 10 | 16321 | 1101 | 163211101 | 163211101 | 9
1632101102 | 10 | 16321 | 1102 | 163211102 | 163211102 | 9
1632101103 | 10 | 16321 | 1103 | 163211103 | 163211103 | 9
0144701102 | 10 | 01447 | 1102 | 014471102 | 014471102 | 9
0144701103 | 10 | 01447 | 1103 | 014471103 | 014471103 | 9
0144502107 | 10 | 01445 | 2107 | 014452107 | 014452107 | 9
0144502108 | 10 | 01445 | 2108 | 014452108 | 014452108 | 9
0144701104 | 10 | 01447 | 1104 | 014471104 | 014471104 | 9
0144502109 | 10 | 01445 | 2109 | 014452109 | 014452109 | 9
0820102104 | 10 | 08201 | 2104 | 082012104 | 082012104 | 9
0820102105 | 10 | 08201 | 2105 | 082012105 | 082012105 | 9
1632301101 | 10 | 16323 | 1101 | 163231101 | 163231101 | 9
163270401 | 9 |  |  | 163270401 | 163270401 | 9
163270402 | 9 |  |  | 163270402 | 163270402 | 9
1635401101 | 10 | 16354 | 1101 | 163541101 | 163541101 | 9
1635401102 | 10 | 16354 | 1102 | 163541102 | 163541102 | 9
1637501101 | 10 | 16375 | 1101 | 163751101 | 163751101 | 9
1637501102 | 10 | 16375 | 1102 | 163751102 | 163751102 | 9
1636902101 | 10 | 16369 | 2101 | 163692101 | 163692101 | 9
1636902102 | 10 | 16369 | 2102 | 163692102 | 163692102 | 9
1632001101 | 10 | 16320 | 1101 | 163201101 | 163201101 | 9
1628201701 | 10 | 16282 | 1701 | 162821701 | 162821701 | 9
1628201702 | 10 | 16282 | 1702 | 162821702 | 162821702 | 9
1632001102 | 10 | 16320 | 1102 | 163201102 | 163201102 | 9
1632801101 | 10 | 16328 | 1101 | 163281101 | 163281101 | 9
1632801102 | 10 | 16328 | 1102 | 163281102 | 163281102 | 9
0141601101 | 10 | 01416 | 1101 | 014161101 | 014161101 | 9
0141601102 | 10 | 01416 | 1102 | 014161102 | 014161102 | 9
0141601103 | 10 | 01416 | 1103 | 014161103 | 014161103 | 9
0141601104 | 10 | 01416 | 1104 | 014161104 | 014161104 | 9
1628801102 | 10 | 16288 | 1102 | 162881102 | 162881102 | 9
1628801103 | 10 | 16288 | 1103 | 162881103 | 162881103 | 9
1628801104 | 10 | 16288 | 1104 | 162881104 | 162881104 | 9
1628801105 | 10 | 16288 | 1105 | 162881105 | 162881105 | 9
1628801106 | 10 | 16288 | 1106 | 162881106 | 162881106 | 9
1628801107 | 10 | 16288 | 1107 | 162881107 | 162881107 | 9
162880402 | 9 |  |  | 162880402 | 162880402 | 9
2529001104 | 10 | 25290 | 1104 | 252901104 | 252901104 | 9
1628801109 | 10 | 16288 | 1109 | 162881109 | 162881109 | 9
2529001106 | 10 | 25290 | 1106 | 252901106 | 252901106 | 9
2529001108 | 10 | 25290 | 1108 | 252901108 | 252901108 | 9
2529001110 | 10 | 25290 | 1110 | 252901110 | 252901110 | 9
1628801110 | 10 | 16288 | 1110 | 162881110 | 162881110 | 9
2529001112 | 10 | 25290 | 1112 | 252901112 | 252901112 | 9
1628801111 | 10 | 16288 | 1111 | 162881111 | 162881111 | 9
2531801101 | 10 | 25318 | 1101 | 253181101 | 253181101 | 9
2531801102 | 10 | 25318 | 1102 | 253181102 | 253181102 | 9
162881112 | 9 |  |  | 162881112 | 162881112 | 9
163692101 | 9 |  |  | 163692101 | 163692101 | 9
0821901103 | 10 | 08219 | 1103 | 082191103 | 082191103 | 9
0821901104 | 10 | 08219 | 1104 | 082191104 | 082191104 | 9
0821901105 | 10 | 08219 | 1105 | 082191105 | 082191105 | 9
1536102103 | 10 | 15361 | 2103 | 153612103 | 153612103 | 9
1536102104 | 10 | 15361 | 2104 | 153612104 | 153612104 | 9
1536102105 | 10 | 15361 | 2105 | 153612105 | 153612105 | 9
1536102106 | 10 | 15361 | 2106 | 153612106 | 153612106 | 9
1536102109 | 10 | 15361 | 2109 | 153612109 | 153612109 | 9
1536102110 | 10 | 15361 | 2110 | 153612110 | 153612110 | 9
082191101 | 9 |  |  | 082191101 | 082191101 | 9
0821901102 | 10 | 08219 | 1102 | 082191102 | 082191102 | 9
0144701105 | 10 | 01447 | 1105 | 014471105 | 014471105 | 9
0144701106 | 10 | 01447 | 1106 | 014471106 | 014471106 | 9
0144701107 | 10 | 01447 | 1107 | 014471107 | 014471107 | 9
0144701108 | 10 | 01447 | 1108 | 014471108 | 014471108 | 9
0146602103 | 10 | 01466 | 2103 | 014662103 | 014662103 | 9
0146602104 | 10 | 01466 | 2104 | 014662104 | 014662104 | 9
0146602105 | 10 | 01466 | 2105 | 014662105 | 014662105 | 9
0146602106 | 10 | 01466 | 2106 | 014662106 | 014662106 | 9
1829801103 | 10 | 18298 | 1103 | 182981103 | 182981103 | 9
0146602107 | 10 | 01466 | 2107 | 014662107 | 014662107 | 9
0146602108 | 10 | 01466 | 2108 | 014662108 | 014662108 | 9
0146602109 | 10 | 01466 | 2109 | 014662109 | 014662109 | 9
0146602110 | 10 | 01466 | 2110 | 014662110 | 014662110 | 9
182222101 | 9 |  |  | 182222101 | 182222101 | 9
1536501103 | 10 | 15365 | 1103 | 153651103 | 153651103 | 9
1536501104 | 10 | 15365 | 1104 | 153651104 | 153651104 | 9
1536502105 | 10 | 15365 | 2105 | 153652105 | 153652105 | 9
0146602112 | 10 | 01466 | 2112 | 014662112 | 014662112 | 9
0146602113 | 10 | 01466 | 2113 | 014662113 | 014662113 | 9
0146602114 | 10 | 01466 | 2114 | 014662114 | 014662114 | 9
1536502108 | 10 | 15365 | 2108 | 153652108 | 153652108 | 9
1536502109 | 10 | 15365 | 2109 | 153652109 | 153652109 | 9
1536502110 | 10 | 15365 | 2110 | 153652110 | 153652110 | 9
0829502108 | 10 | 08295 | 2108 | 082952108 | 082952108 | 9
0138001101 | 10 | 01380 | 1101 | 013801101 | 013801101 | 9
0829502109 | 10 | 08295 | 2109 | 082952109 | 082952109 | 9
0829502110 | 10 | 08295 | 2110 | 082952110 | 082952110 | 9
0138001102 | 10 | 01380 | 1102 | 013801102 | 013801102 | 9
0138001103 | 10 | 01380 | 1103 | 013801103 | 013801103 | 9
0138001104 | 10 | 01380 | 1104 | 013801104 | 013801104 | 9
0138001105 | 10 | 01380 | 1105 | 013801105 | 013801105 | 9
0829502111 | 10 | 08295 | 2111 | 082952111 | 082952111 | 9
0829502112 | 10 | 08295 | 2112 | 082952112 | 082952112 | 9
0829502113 | 10 | 08295 | 2113 | 082952113 | 082952113 | 9
0145902106 | 10 | 01459 | 2106 | 014592106 | 014592106 | 9
0120901101 | 10 | 01209 | 1101 | 012091101 | 012091101 | 9
0120901103 | 10 | 01209 | 1103 | 012091103 | 012091103 | 9
0120901104 | 10 | 01209 | 1104 | 012091104 | 012091104 | 9
0120901105 | 10 | 01209 | 1105 | 012091105 | 012091105 | 9
0120901109 | 10 | 01209 | 1109 | 012091109 | 012091109 | 9
1527001109 | 10 | 15270 | 1109 | 152701109 | 152701109 | 9
1527001110 | 10 | 15270 | 1110 | 152701110 | 152701110 | 9
1525301101 | 10 | 15253 | 1101 | 152531101 | 152531101 | 9
1525301102 | 10 | 15253 | 1102 | 152531102 | 152531102 | 9
0120901112 | 10 | 01209 | 1112 | 012091112 | 012091112 | 9
0120901102 | 10 | 01209 | 1102 | 012091102 | 012091102 | 9
0120901116 | 10 | 01209 | 1116 | 012091116 | 012091116 | 9
0120901117 | 10 | 01209 | 1117 | 012091117 | 012091117 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
012090403 | 9 |  |  | 012090403 | 012090403 | 9
012090409 | 9 |  |  | 012090409 | 012090409 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0121001101 | 10 | 01210 | 1101 | 012101101 | 012101101 | 9
0121001103 | 10 | 01210 | 1103 | 012101103 | 012101103 | 9
012110406 | 9 |  |  | 012110406 | 012110406 | 9
012110407 | 9 |  |  | 012110407 | 012110407 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
012110405 | 9 |  |  | 012110405 | 012110405 | 9
| 0 |  |  |  |  | 0
014321101 | 9 |  |  | 014321101 | 014321101 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0132302101 | 10 | 01323 | 2101 | 013232101 | 013232101 | 9
0132302102 | 10 | 01323 | 2102 | 013232102 | 013232102 | 9
0146902101 | 10 | 01469 | 2101 | 014692101 | 014692101 | 9
0146902102 | 10 | 01469 | 2102 | 014692102 | 014692102 | 9
0146902103 | 10 | 01469 | 2103 | 014692103 | 014692103 | 9
0144701109 | 10 | 01447 | 1109 | 014471109 | 014471109 | 9
0144701110 | 10 | 01447 | 1110 | 014471110 | 014471110 | 9
0144701111 | 10 | 01447 | 1111 | 014471111 | 014471111 | 9
0144701112 | 10 | 01447 | 1112 | 014471112 | 014471112 | 9
1521101101 | 10 | 15211 | 1101 | 152111101 | 152111101 | 9
1521101102 | 10 | 15211 | 1102 | 152111102 | 152111102 | 9
1521101103 | 10 | 15211 | 1103 | 152111103 | 152111103 | 9
0833701103 | 10 | 08337 | 1103 | 083371103 | 083371103 | 9
0833701104 | 10 | 08337 | 1104 | 083371104 | 083371104 | 9
1528501102 | 10 | 15285 | 1102 | 152851102 | 152851102 | 9
1528501104 | 10 | 15285 | 1104 | 152851104 | 152851104 | 9
082160401 | 9 |  |  | 082160401 | 082160401 | 9
1528501105 | 10 | 15285 | 1105 | 152851105 | 152851105 | 9
1528501106 | 10 | 15285 | 1106 | 152851106 | 152851106 | 9
1528501107 | 10 | 15285 | 1107 | 152851107 | 152851107 | 9
0833701105 | 10 | 08337 | 1105 | 083371105 | 083371105 | 9
0833701106 | 10 | 08337 | 1106 | 083371106 | 083371106 | 9
0833701107 | 10 | 08337 | 1107 | 083371107 | 083371107 | 9
0833701108 | 10 | 08337 | 1108 | 083371108 | 083371108 | 9
0833701109 | 10 | 08337 | 1109 | 083371109 | 083371109 | 9
0833701110 | 10 | 08337 | 1110 | 083371110 | 083371110 | 9
1526901103 | 10 | 15269 | 1103 | 152691103 | 152691103 | 9
0833701111 | 10 | 08337 | 1111 | 083371111 | 083371111 | 9
1526901104 | 10 | 15269 | 1104 | 152691104 | 152691104 | 9
1526901107 | 10 | 15269 | 1107 | 152691107 | 152691107 | 9
1526901108 | 10 | 15269 | 1108 | 152691108 | 152691108 | 9
1526901109 | 10 | 15269 | 1109 | 152691109 | 152691109 | 9
1526901110 | 10 | 15269 | 1110 | 152691110 | 152691110 | 9
1531302101 | 10 | 15313 | 2101 | 153132101 | 153132101 | 9
1531302102 | 10 | 15313 | 2102 | 153132102 | 153132102 | 9
1531302104 | 10 | 15313 | 2104 | 153132104 | 153132104 | 9
1531302105 | 10 | 15313 | 2105 | 153132105 | 153132105 | 9
1522001101 | 10 | 15220 | 1101 | 152201101 | 152201101 | 9
1522001102 | 10 | 15220 | 1102 | 152201102 | 152201102 | 9
1529201101 | 10 | 15292 | 1101 | 152921101 | 152921101 | 9
1537901101 | 10 | 15379 | 1101 | 153791101 | 153791101 | 9
012200404 | 9 |  |  | 012200404 | 012200404 | 9
012200403 | 9 |  |  | 012200403 | 012200403 | 9
013560401 | 9 |  |  | 013560401 | 013560401 | 9
0132302105 | 10 | 01323 | 2105 | 013232105 | 013232105 | 9
1637101701 | 10 | 16371 | 1701 | 163711701 | 163711701 | 9
1637101703 | 10 | 16371 | 1703 | 163711703 | 163711703 | 9
1637101702 | 10 | 16371 | 1702 | 163711702 | 163711702 | 9
1637101704 | 10 | 16371 | 1704 | 163711704 | 163711704 | 9
163240401 | 9 |  |  | 163240401 | 163240401 | 9
163240402 | 9 |  |  | 163240402 | 163240402 | 9
0135301101 | 10 | 01353 | 1101 | 013531101 | 013531101 | 9
0135301102 | 10 | 01353 | 1102 | 013531102 | 013531102 | 9
0135301103 | 10 | 01353 | 1103 | 013531103 | 013531103 | 9
0135301104 | 10 | 01353 | 1104 | 013531104 | 013531104 | 9
1522601103 | 10 | 15226 | 1103 | 152261103 | 152261103 | 9
1522601104 | 10 | 15226 | 1104 | 152261104 | 152261104 | 9
1522601105 | 10 | 15226 | 1105 | 152261105 | 152261105 | 9
1522601106 | 10 | 15226 | 1106 | 152261106 | 152261106 | 9
1522601107 | 10 | 15226 | 1107 | 152261107 | 152261107 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
1521601101 | 10 | 15216 | 1101 | 152161101 | 152161101 | 9
1521601102 | 10 | 15216 | 1102 | 152161102 | 152161102 | 9
013660401 | 9 |  |  | 013660401 | 013660401 | 9
013660402 | 9 |  |  | 013660402 | 013660402 | 9
1527001107 | 10 | 15270 | 1107 | 152701107 | 152701107 | 9
1527001108 | 10 | 15270 | 1108 | 152701108 | 152701108 | 9
0120101101 | 10 | 01201 | 1101 | 012011101 | 012011101 | 9
0120101102 | 10 | 01201 | 1102 | 012011102 | 012011102 | 9
0120101103 | 10 | 01201 | 1103 | 012011103 | 012011103 | 9
0120101104 | 10 | 01201 | 1104 | 012011104 | 012011104 | 9
0120101105 | 10 | 01201 | 1105 | 012011105 | 012011105 | 9
0120101106 | 10 | 01201 | 1106 | 012011106 | 012011106 | 9
0120101110 | 10 | 01201 | 1110 | 012011110 | 012011110 | 9
0120101112 | 10 | 01201 | 1112 | 012011112 | 012011112 | 9
0120101116 | 10 | 01201 | 1116 | 012011116 | 012011116 | 9
0120101121 | 10 | 01201 | 1121 | 012011121 | 012011121 | 9
012040406 | 9 |  |  | 012040406 | 012040406 | 9
012040407 | 9 |  |  | 012040407 | 012040407 | 9
012040408 | 9 |  |  | 012040408 | 012040408 | 9
012040410 | 9 |  |  | 012040410 | 012040410 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0135302223 | 10 | 01353 | 2223 | 013532223 | 013532223 | 9
013111151 | 9 |  |  | 013111151 | 013111151 | 9
0135302224 | 10 | 01353 | 2224 | 013532224 | 013532224 | 9
0135302110 | 10 | 01353 | 2110 | 013532110 | 013532110 | 9
0135302111 | 10 | 01353 | 2111 | 013532111 | 013532111 | 9
0135302112 | 10 | 01353 | 2112 | 013532112 | 013532112 | 9
0145902105 | 10 | 01459 | 2105 | 014592105 | 014592105 | 9
012541107 | 9 |  |  | 012541107 | 012541107 | 9
0125401109 | 10 | 01254 | 1109 | 012541109 | 012541109 | 9
0125401110 | 10 | 01254 | 1110 | 012541110 | 012541110 | 9
0125401111 | 10 | 01254 | 1111 | 012541111 | 012541111 | 9
0125401112 | 10 | 01254 | 1112 | 012541112 | 012541112 | 9
0125401114 | 10 | 01254 | 1114 | 012541114 | 012541114 | 9
0125401104 | 10 | 01254 | 1104 | 012541104 | 012541104 | 9
0125401105 | 10 | 01254 | 1105 | 012541105 | 012541105 | 9
0125401101 | 10 | 01254 | 1101 | 012541101 | 012541101 | 9
0125401106 | 10 | 01254 | 1106 | 012541106 | 012541106 | 9
0125401115 | 10 | 01254 | 1115 | 012541115 | 012541115 | 9
0432501101 | 10 | 04325 | 1101 | 043251101 | 043251101 | 9
0432501104 | 10 | 04325 | 1104 | 043251104 | 043251104 | 9
0432501105 | 10 | 04325 | 1105 | 043251105 | 043251105 | 9
0432501102 | 10 | 04325 | 1102 | 043251102 | 043251102 | 9
0432501103 | 10 | 04325 | 1103 | 043251103 | 043251103 | 9
0420402204 | 10 | 04204 | 2204 | 042042204 | 042042204 | 9
0420402201 | 10 | 04204 | 2201 | 042042201 | 042042201 | 9
042450411 | 9 |  |  | 042450411 | 042450411 | 9
042450412 | 9 |  |  | 042450412 | 042450412 | 9
042450413 | 9 |  |  | 042450413 | 042450413 | 9
042450414 | 9 |  |  | 042450414 | 042450414 | 9
042450415 | 9 |  |  | 042450415 | 042450415 | 9
0145902112 | 10 | 01459 | 2112 | 014592112 | 014592112 | 9
0145902113 | 10 | 01459 | 2113 | 014592113 | 014592113 | 9
1527602101 | 10 | 15276 | 2101 | 152762101 | 152762101 | 9
1527602102 | 10 | 15276 | 2102 | 152762102 | 152762102 | 9
1522802101 | 10 | 15228 | 2101 | 152282101 | 152282101 | 9
0833302101 | 10 | 08333 | 2101 | 083332101 | 083332101 | 9
0145902108 | 10 | 01459 | 2108 | 014592108 | 014592108 | 9
0145902109 | 10 | 01459 | 2109 | 014592109 | 014592109 | 9
0145902110 | 10 | 01459 | 2110 | 014592110 | 014592110 | 9
0145902111 | 10 | 01459 | 2111 | 014592111 | 014592111 | 9
0830001106 | 10 | 08300 | 1106 | 083001106 | 083001106 | 9
0830001107 | 10 | 08300 | 1107 | 083001107 | 083001107 | 9
0830001108 | 10 | 08300 | 1108 | 083001108 | 083001108 | 9
2523201102 | 10 | 25232 | 1102 | 252321102 | 252321102 | 9
2523201103 | 10 | 25232 | 1103 | 252321103 | 252321103 | 9
2531402101 | 10 | 25314 | 2101 | 253142101 | 253142101 | 9
0830001103 | 10 | 08300 | 1103 | 083001103 | 083001103 | 9
2524601101 | 10 | 25246 | 1101 | 252461101 | 252461101 | 9
2524601102 | 10 | 25246 | 1102 | 252461102 | 252461102 | 9
2524601103 | 10 | 25246 | 1103 | 252461103 | 252461103 | 9
2524601105 | 10 | 25246 | 1105 | 252461105 | 252461105 | 9
2524601107 | 10 | 25246 | 1107 | 252461107 | 252461107 | 9
2531501102 | 10 | 25315 | 1102 | 253151102 | 253151102 | 9
2531501103 | 10 | 25315 | 1103 | 253151103 | 253151103 | 9
2531501106 | 10 | 25315 | 1106 | 253151106 | 253151106 | 9
2531501107 | 10 | 25315 | 1107 | 253151107 | 253151107 | 9
2520602109 | 10 | 25206 | 2109 | 252062109 | 252062109 | 9
0136502203 | 10 | 01365 | 2203 | 013652203 | 013652203 | 9
0136502204 | 10 | 01365 | 2204 | 013652204 | 013652204 | 9
0136502205 | 10 | 01365 | 2205 | 013652205 | 013652205 | 9
2554501101 | 10 | 25545 | 1101 | 255451101 | 255451101 | 9
2554501102 | 10 | 25545 | 1102 | 255451102 | 255451102 | 9
255451103 | 9 |  |  | 255451103 | 255451103 | 9
253461101 | 9 |  |  | 253461101 | 253461101 | 9
2538701104 | 10 | 25387 | 1104 | 253871104 | 253871104 | 9
2542402103 | 10 | 25424 | 2103 | 254242103 | 254242103 | 9
2542402104 | 10 | 25424 | 2104 | 254242104 | 254242104 | 9
2531401103 | 10 | 25314 | 1103 | 253141103 | 253141103 | 9
2531401104 | 10 | 25314 | 1104 | 253141104 | 253141104 | 9
2531402102 | 10 | 25314 | 2102 | 253142102 | 253142102 | 9
2533901101 | 10 | 25339 | 1101 | 253391101 | 253391101 | 9
2533901103 | 10 | 25339 | 1103 | 253391103 | 253391103 | 9
2533901105 | 10 | 25339 | 1105 | 253391105 | 253391105 | 9
2545401103 | 10 | 25454 | 1103 | 254541103 | 254541103 | 9
2545401104 | 10 | 25454 | 1104 | 254541104 | 254541104 | 9
2522601105 | 10 | 25226 | 1105 | 252261105 | 252261105 | 9
2522601104 | 10 | 25226 | 1104 | 252261104 | 252261104 | 9
0838701101 | 10 | 08387 | 1101 | 083871101 | 083871101 | 9
0838701109 | 10 | 08387 | 1109 | 083871109 | 083871109 | 9
0838701110 | 10 | 08387 | 1110 | 083871110 | 083871110 | 9
0838701111 | 10 | 08387 | 1111 | 083871111 | 083871111 | 9
0136502114 | 10 | 01365 | 2114 | 013652114 | 013652114 | 9
0136502115 | 10 | 01365 | 2115 | 013652115 | 013652115 | 9
0136502116 | 10 | 01365 | 2116 | 013652116 | 013652116 | 9
0240102101 | 10 | 02401 | 2101 | 024012101 | 024012101 | 9
0240102102 | 10 | 02401 | 2102 | 024012102 | 024012102 | 9
0240102103 | 10 | 02401 | 2103 | 024012103 | 024012103 | 9
0240101107 | 10 | 02401 | 1107 | 024011107 | 024011107 | 9
0240101108 | 10 | 02401 | 1108 | 024011108 | 024011108 | 9
0240101102 | 10 | 02401 | 1102 | 024011102 | 024011102 | 9
0240101103 | 10 | 02401 | 1103 | 024011103 | 024011103 | 9
0240101104 | 10 | 02401 | 1104 | 024011104 | 024011104 | 9
0240101105 | 10 | 02401 | 1105 | 024011105 | 024011105 | 9
0240101106 | 10 | 02401 | 1106 | 024011106 | 024011106 | 9
1530802106 | 10 | 15308 | 2106 | 153082106 | 153082106 | 9
0240102104 | 10 | 02401 | 2104 | 024012104 | 024012104 | 9
0240102105 | 10 | 02401 | 2105 | 024012105 | 024012105 | 9
1530801109 | 10 | 15308 | 1109 | 153081109 | 153081109 | 9
1530801110 | 10 | 15308 | 1110 | 153081110 | 153081110 | 9
1530801111 | 10 | 15308 | 1111 | 153081111 | 153081111 | 9
1530801112 | 10 | 15308 | 1112 | 153081112 | 153081112 | 9
02402401 | 8 | 02402 | 401 | 024020401 | 024020401 | 9
024020402 | 9 |  |  | 024020402 | 024020402 | 9
02402403 | 8 | 02402 | 403 | 024020403 | 024020403 | 9
024020404 | 9 |  |  | 024020404 | 024020404 | 9
024020405 | 9 |  |  | 024020405 | 024020405 | 9
024020406 | 9 |  |  | 024020406 | 024020406 | 9
024020407 | 9 |  |  | 024020407 | 024020407 | 9
024020408 | 9 |  |  | 024020408 | 024020408 | 9
02402409 | 8 | 02402 | 409 | 024020409 | 024020409 | 9
0240201103 | 10 | 02402 | 1103 | 024021103 | 024021103 | 9
0240201104 | 10 | 02402 | 1104 | 024021104 | 024021104 | 9
0240201101 | 10 | 02402 | 1101 | 024021101 | 024021101 | 9
0240201102 | 10 | 02402 | 1102 | 024021102 | 024021102 | 9
0240201105 | 10 | 02402 | 1105 | 024021105 | 024021105 | 9
0240201106 | 10 | 02402 | 1106 | 024021106 | 024021106 | 9
0240201107 | 10 | 02402 | 1107 | 024021107 | 024021107 | 9
0240301101 | 10 | 02403 | 1101 | 024031101 | 024031101 | 9
0240301102 | 10 | 02403 | 1102 | 024031102 | 024031102 | 9
0240301103 | 10 | 02403 | 1103 | 024031103 | 024031103 | 9
0240301104 | 10 | 02403 | 1104 | 024031104 | 024031104 | 9
0240301105 | 10 | 02403 | 1105 | 024031105 | 024031105 | 9
0240301106 | 10 | 02403 | 1106 | 024031106 | 024031106 | 9
0240301107 | 10 | 02403 | 1107 | 024031107 | 024031107 | 9
0240301108 | 10 | 02403 | 1108 | 024031108 | 024031108 | 9
0240301109 | 10 | 02403 | 1109 | 024031109 | 024031109 | 9
0240301110 | 10 | 02403 | 1110 | 024031110 | 024031110 | 9
0240301111 | 10 | 02403 | 1111 | 024031111 | 024031111 | 9
02404401 | 8 | 02404 | 401 | 024040401 | 024040401 | 9
02404402 | 8 | 02404 | 402 | 024040402 | 024040402 | 9
02404403 | 8 | 02404 | 403 | 024040403 | 024040403 | 9
024040404 | 9 |  |  | 024040404 | 024040404 | 9
02404405 | 8 | 02404 | 405 | 024040405 | 024040405 | 9
2533901106 | 10 | 25339 | 1106 | 253391106 | 253391106 | 9
2533901104 | 10 | 25339 | 1104 | 253391104 | 253391104 | 9
253392108 | 9 |  |  | 253392108 | 253392108 | 9
0136502106 | 10 | 01365 | 2106 | 013652106 | 013652106 | 9
0136502107 | 10 | 01365 | 2107 | 013652107 | 013652107 | 9
0136502108 | 10 | 01365 | 2108 | 013652108 | 013652108 | 9
0136502110 | 10 | 01365 | 2110 | 013652110 | 013652110 | 9
082160403 | 9 |  |  | 082160403 | 082160403 | 9
0821601101 | 10 | 08216 | 1101 | 082161101 | 082161101 | 9
252951108 | 9 |  |  | 252951108 | 252951108 | 9
0821601102 | 10 | 08216 | 1102 | 082161102 | 082161102 | 9
2552902107 | 10 | 25529 | 2107 | 255292107 | 255292107 | 9
2552902108 | 10 | 25529 | 2108 | 255292108 | 255292108 | 9
2552902109 | 10 | 25529 | 2109 | 255292109 | 255292109 | 9
2545301106 | 10 | 25453 | 1106 | 254531106 | 254531106 | 9
2545301107 | 10 | 25453 | 1107 | 254531107 | 254531107 | 9
152251101 | 9 |  |  | 152251101 | 152251101 | 9
1032101101 | 10 | 10321 | 1101 | 103211101 | 103211101 | 9
2545301108 | 10 | 25453 | 1108 | 254531108 | 254531108 | 9
1032101102 | 10 | 10321 | 1102 | 103211102 | 103211102 | 9
1525901101 | 10 | 15259 | 1101 | 152591101 | 152591101 | 9
1525901102 | 10 | 15259 | 1102 | 152591102 | 152591102 | 9
1032401102 | 10 | 10324 | 1102 | 103241102 | 103241102 | 9
1032401103 | 10 | 10324 | 1103 | 103241103 | 103241103 | 9
1032401101 | 10 | 10324 | 1101 | 103241101 | 103241101 | 9
0823101101 | 10 | 08231 | 1101 | 082311101 | 082311101 | 9
0823101102 | 10 | 08231 | 1102 | 082311102 | 082311102 | 9
0823101103 | 10 | 08231 | 1103 | 082311103 | 082311103 | 9
0823101110 | 10 | 08231 | 1110 | 082311110 | 082311110 | 9
0823101111 | 10 | 08231 | 1111 | 082311111 | 082311111 | 9
0834302101 | 10 | 08343 | 2101 | 083432101 | 083432101 | 9
0834302102 | 10 | 08343 | 2102 | 083432102 | 083432102 | 9
0834302103 | 10 | 08343 | 2103 | 083432103 | 083432103 | 9
0834302105 | 10 | 08343 | 2105 | 083432105 | 083432105 | 9
0834302111 | 10 | 08343 | 2111 | 083432111 | 083432111 | 9
0834301108 | 10 | 08343 | 1108 | 083431108 | 083431108 | 9
0834301109 | 10 | 08343 | 1109 | 083431109 | 083431109 | 9
0834301110 | 10 | 08343 | 1110 | 083431110 | 083431110 | 9
0834301111 | 10 | 08343 | 1111 | 083431111 | 083431111 | 9
0834301112 | 10 | 08343 | 1112 | 083431112 | 083431112 | 9
0834301113 | 10 | 08343 | 1113 | 083431113 | 083431113 | 9
0834301114 | 10 | 08343 | 1114 | 083431114 | 083431114 | 9
0834301115 | 10 | 08343 | 1115 | 083431115 | 083431115 | 9
0834301116 | 10 | 08343 | 1116 | 083431116 | 083431116 | 9
0834301117 | 10 | 08343 | 1117 | 083431117 | 083431117 | 9
0831802101 | 10 | 08318 | 2101 | 083182101 | 083182101 | 9
0831802102 | 10 | 08318 | 2102 | 083182102 | 083182102 | 9
0831802103 | 10 | 08318 | 2103 | 083182103 | 083182103 | 9
0831802104 | 10 | 08318 | 2104 | 083182104 | 083182104 | 9
0831802105 | 10 | 08318 | 2105 | 083182105 | 083182105 | 9
0831802106 | 10 | 08318 | 2106 | 083182106 | 083182106 | 9
0831802107 | 10 | 08318 | 2107 | 083182107 | 083182107 | 9
2529401106 | 10 | 25294 | 1106 | 252941106 | 252941106 | 9
2529401107 | 10 | 25294 | 1107 | 252941107 | 252941107 | 9
2536601101 | 10 | 25366 | 1101 | 253661101 | 253661101 | 9
2536601102 | 10 | 25366 | 1102 | 253661102 | 253661102 | 9
2536601104 | 10 | 25366 | 1104 | 253661104 | 253661104 | 9
2536601107 | 10 | 25366 | 1107 | 253661107 | 253661107 | 9
2536601108 | 10 | 25366 | 1108 | 253661108 | 253661108 | 9
2528901112 | 10 | 25289 | 1112 | 252891112 | 252891112 | 9
1032501101 | 10 | 10325 | 1101 | 103251101 | 103251101 | 9
2522901105 | 10 | 25229 | 1105 | 252291105 | 252291105 | 9
2541201108 | 10 | 25412 | 1108 | 254121108 | 254121108 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
1522401101 | 10 | 15224 | 1101 | 152241101 | 152241101 | 9
1522401102 | 10 | 15224 | 1102 | 152241102 | 152241102 | 9
0134701126 | 10 | 01347 | 1126 | 013471126 | 013471126 | 9
0220301119 | 10 | 02203 | 1119 | 022031119 | 022031119 | 9
0228701113 | 10 | 02287 | 1113 | 022871113 | 022871113 | 9
022871114 | 9 |  |  | 022871114 | 022871114 | 9
022871115 | 9 |  |  | 022871115 | 022871115 | 9
022871117 | 9 |  |  | 022871117 | 022871117 | 9
0228701118 | 10 | 02287 | 1118 | 022871118 | 022871118 | 9
022530403 | 9 |  |  | 022530403 | 022530403 | 9
1031302101 | 10 | 10313 | 2101 | 103132101 | 103132101 | 9
1030701103 | 10 | 10307 | 1103 | 103071103 | 103071103 | 9
0120901110 | 10 | 01209 | 1110 | 012091110 | 012091110 | 9
0120901111 | 10 | 01209 | 1111 | 012091111 | 012091111 | 9
0120901118 | 10 | 01209 | 1118 | 012091118 | 012091118 | 9
0120901115 | 10 | 01209 | 1115 | 012091115 | 012091115 | 9
012091114 | 9 |  |  | 012091114 | 012091114 | 9
0120901108 | 10 | 01209 | 1108 | 012091108 | 012091108 | 9
0120901106 | 10 | 01209 | 1106 | 012091106 | 012091106 | 9
02207409 | 8 | 02207 | 409 | 022070409 | 022070409 | 9
| 0 |  |  |  |  | 0
1033501101 | 10 | 10335 | 1101 | 103351101 | 103351101 | 9
1033501104 | 10 | 10335 | 1104 | 103351104 | 103351104 | 9
1034001101 | 10 | 10340 | 1101 | 103401101 | 103401101 | 9
1034001102 | 10 | 10340 | 1102 | 103401102 | 103401102 | 9
1034401101 | 10 | 10344 | 1101 | 103441101 | 103441101 | 9
1034401102 | 10 | 10344 | 1102 | 103441102 | 103441102 | 9
1034401103 | 10 | 10344 | 1103 | 103441103 | 103441103 | 9
1034501101 | 10 | 10345 | 1101 | 103451101 | 103451101 | 9
1034601101 | 10 | 10346 | 1101 | 103461101 | 103461101 | 9
1522901101 | 10 | 15229 | 1101 | 152291101 | 152291101 | 9
1522901102 | 10 | 15229 | 1102 | 152291102 | 152291102 | 9
2527001104 | 10 | 25270 | 1104 | 252701104 | 252701104 | 9
2527001106 | 10 | 25270 | 1106 | 252701106 | 252701106 | 9
2527001110 | 10 | 25270 | 1110 | 252701110 | 252701110 | 9
2531601106 | 10 | 25316 | 1106 | 253161106 | 253161106 | 9
2531601107 | 10 | 25316 | 1107 | 253161107 | 253161107 | 9
2531601108 | 10 | 25316 | 1108 | 253161108 | 253161108 | 9
2531601109 | 10 | 25316 | 1109 | 253161109 | 253161109 | 9
2531601116 | 10 | 25316 | 1116 | 253161116 | 253161116 | 9
2526801104 | 10 | 25268 | 1104 | 252681104 | 252681104 | 9
2526801108 | 10 | 25268 | 1108 | 252681108 | 252681108 | 9
1025501101 | 10 | 10255 | 1101 | 102551101 | 102551101 | 9
1027801101 | 10 | 10278 | 1101 | 102781101 | 102781101 | 9
0835301103 | 10 | 08353 | 1103 | 083531103 | 083531103 | 9
0835301104 | 10 | 08353 | 1104 | 083531104 | 083531104 | 9
0835301105 | 10 | 08353 | 1105 | 083531105 | 083531105 | 9
0835301106 | 10 | 08353 | 1106 | 083531106 | 083531106 | 9
0835301107 | 10 | 08353 | 1107 | 083531107 | 083531107 | 9
0835301108 | 10 | 08353 | 1108 | 083531108 | 083531108 | 9
0835301109 | 10 | 08353 | 1109 | 083531109 | 083531109 | 9
1030201101 | 10 | 10302 | 1101 | 103021101 | 103021101 | 9
0835301110 | 10 | 08353 | 1110 | 083531110 | 083531110 | 9
0835301111 | 10 | 08353 | 1111 | 083531111 | 083531111 | 9
0835301112 | 10 | 08353 | 1112 | 083531112 | 083531112 | 9
0828301101 | 10 | 08283 | 1101 | 082831101 | 082831101 | 9
102520402 | 9 |  |  | 102520402 | 102520402 | 9
0828301103 | 10 | 08283 | 1103 | 082831103 | 082831103 | 9
102520403 | 9 |  |  | 102520403 | 102520403 | 9
0828301105 | 10 | 08283 | 1105 | 082831105 | 082831105 | 9
0828301108 | 10 | 08283 | 1108 | 082831108 | 082831108 | 9
0828301109 | 10 | 08283 | 1109 | 082831109 | 082831109 | 9
0136502109 | 10 | 01365 | 2109 | 013652109 | 013652109 | 9
0136502111 | 10 | 01365 | 2111 | 013652111 | 013652111 | 9
0136502112 | 10 | 01365 | 2112 | 013652112 | 013652112 | 9
0136502113 | 10 | 01365 | 2113 | 013652113 | 013652113 | 9
0828302110 | 10 | 08283 | 2110 | 082832110 | 082832110 | 9
102530401 | 9 |  |  | 102530401 | 102530401 | 9
0828302111 | 10 | 08283 | 2111 | 082832111 | 082832111 | 9
0828302112 | 10 | 08283 | 2112 | 082832112 | 082832112 | 9
0828302113 | 10 | 08283 | 2113 | 082832113 | 082832113 | 9
0828302114 | 10 | 08283 | 2114 | 082832114 | 082832114 | 9
0828302115 | 10 | 08283 | 2115 | 082832115 | 082832115 | 9
0838902101 | 10 | 08389 | 2101 | 083892101 | 083892101 | 9
0838902102 | 10 | 08389 | 2102 | 083892102 | 083892102 | 9
0838902103 | 10 | 08389 | 2103 | 083892103 | 083892103 | 9
0838902104 | 10 | 08389 | 2104 | 083892104 | 083892104 | 9
0838902105 | 10 | 08389 | 2105 | 083892105 | 083892105 | 9
0838902106 | 10 | 08389 | 2106 | 083892106 | 083892106 | 9
0838902107 | 10 | 08389 | 2107 | 083892107 | 083892107 | 9
0838902108 | 10 | 08389 | 2108 | 083892108 | 083892108 | 9
0838902109 | 10 | 08389 | 2109 | 083892109 | 083892109 | 9
0832402104 | 10 | 08324 | 2104 | 083242104 | 083242104 | 9
0832402105 | 10 | 08324 | 2105 | 083242105 | 083242105 | 9
0832402106 | 10 | 08324 | 2106 | 083242106 | 083242106 | 9
0832402108 | 10 | 08324 | 2108 | 083242108 | 083242108 | 9
0832402109 | 10 | 08324 | 2109 | 083242109 | 083242109 | 9
0832402110 | 10 | 08324 | 2110 | 083242110 | 083242110 | 9
0832402111 | 10 | 08324 | 2111 | 083242111 | 083242111 | 9
0839102109 | 10 | 08391 | 2109 | 083912109 | 083912109 | 9
0839102110 | 10 | 08391 | 2110 | 083912110 | 083912110 | 9
| 0 |  |  |  |  | 0
0839102111 | 10 | 08391 | 2111 | 083912111 | 083912111 | 9
0823402101 | 10 | 08234 | 2101 | 082342101 | 082342101 | 9
0823402102 | 10 | 08234 | 2102 | 082342102 | 082342102 | 9
0823402106 | 10 | 08234 | 2106 | 082342106 | 082342106 | 9
0823402107 | 10 | 08234 | 2107 | 082342107 | 082342107 | 9
0823402108 | 10 | 08234 | 2108 | 082342108 | 082342108 | 9
082250403 | 9 |  |  | 082250403 | 082250403 | 9
082250404 | 9 |  |  | 082250404 | 082250404 | 9
082250405 | 9 |  |  | 082250405 | 082250405 | 9
082250407 | 9 |  |  | 082250407 | 082250407 | 9
082250408 | 9 |  |  | 082250408 | 082250408 | 9
024052101 | 9 |  |  | 024052101 | 024052101 | 9
024050401 | 9 |  |  | 024050401 | 024050401 | 9
082250410 | 9 |  |  | 082250410 | 082250410 | 9
0822501109 | 10 | 08225 | 1109 | 082251109 | 082251109 | 9
0822501110 | 10 | 08225 | 1110 | 082251110 | 082251110 | 9
024050402 | 9 |  |  | 024050402 | 024050402 | 9
0822501111 | 10 | 08225 | 1111 | 082251111 | 082251111 | 9
024050403 | 9 |  |  | 024050403 | 024050403 | 9
024050404 | 9 |  |  | 024050404 | 024050404 | 9
024050405 | 9 |  |  | 024050405 | 024050405 | 9
0822501112 | 10 | 08225 | 1112 | 082251112 | 082251112 | 9
024060401 | 9 |  |  | 024060401 | 024060401 | 9
024060402 | 9 |  |  | 024060402 | 024060402 | 9
0822501113 | 10 | 08225 | 1113 | 082251113 | 082251113 | 9
0822601101 | 10 | 08226 | 1101 | 082261101 | 082261101 | 9
0822601102 | 10 | 08226 | 1102 | 082261102 | 082261102 | 9
0822601103 | 10 | 08226 | 1103 | 082261103 | 082261103 | 9
0822601104 | 10 | 08226 | 1104 | 082261104 | 082261104 | 9
0822601105 | 10 | 08226 | 1105 | 082261105 | 082261105 | 9
0822601106 | 10 | 08226 | 1106 | 082261106 | 082261106 | 9
02406403 | 8 | 02406 | 403 | 024060403 | 024060403 | 9
0822601107 | 10 | 08226 | 1107 | 082261107 | 082261107 | 9
02406404 | 8 | 02406 | 404 | 024060404 | 024060404 | 9
0822601108 | 10 | 08226 | 1108 | 082261108 | 082261108 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0226401104 | 10 | 02264 | 1104 | 022641104 | 022641104 | 9
0226401105 | 10 | 02264 | 1105 | 022641105 | 022641105 | 9
0226401107 | 10 | 02264 | 1107 | 022641107 | 022641107 | 9
0226401112 | 10 | 02264 | 1112 | 022641112 | 022641112 | 9
0226401102 | 10 | 02264 | 1102 | 022641102 | 022641102 | 9
0822601109 | 10 | 08226 | 1109 | 082261109 | 082261109 | 9
0822601110 | 10 | 08226 | 1110 | 082261110 | 082261110 | 9
0226401108 | 10 | 02264 | 1108 | 022641108 | 022641108 | 9
0226401109 | 10 | 02264 | 1109 | 022641109 | 022641109 | 9
0226401110 | 10 | 02264 | 1110 | 022641110 | 022641110 | 9
0822601111 | 10 | 08226 | 1111 | 082261111 | 082261111 | 9
0226401101 | 10 | 02264 | 1101 | 022641101 | 022641101 | 9
0822601112 | 10 | 08226 | 1112 | 082261112 | 082261112 | 9
0226401103 | 10 | 02264 | 1103 | 022641103 | 022641103 | 9
0226401106 | 10 | 02264 | 1106 | 022641106 | 022641106 | 9
0822601113 | 10 | 08226 | 1113 | 082261113 | 082261113 | 9
0226401111 | 10 | 02264 | 1111 | 022641111 | 022641111 | 9
0822601114 | 10 | 08226 | 1114 | 082261114 | 082261114 | 9
0226401115 | 10 | 02264 | 1115 | 022641115 | 022641115 | 9
| 0 |  |  |  |  | 0
0822601115 | 10 | 08226 | 1115 | 082261115 | 082261115 | 9
0225701102 | 10 | 02257 | 1102 | 022571102 | 022571102 | 9
0225701104 | 10 | 02257 | 1104 | 022571104 | 022571104 | 9
0225701109 | 10 | 02257 | 1109 | 022571109 | 022571109 | 9
0225701112 | 10 | 02257 | 1112 | 022571112 | 022571112 | 9
022570401 | 9 |  |  | 022570401 | 022570401 | 9
| 0 |  |  |  |  | 0
022570404 | 9 |  |  | 022570404 | 022570404 | 9
0225701105 | 10 | 02257 | 1105 | 022571105 | 022571105 | 9
0225701106 | 10 | 02257 | 1106 | 022571106 | 022571106 | 9
0225701107 | 10 | 02257 | 1107 | 022571107 | 022571107 | 9
0225701108 | 10 | 02257 | 1108 | 022571108 | 022571108 | 9
0225701101 | 10 | 02257 | 1101 | 022571101 | 022571101 | 9
0225701110 | 10 | 02257 | 1110 | 022571110 | 022571110 | 9
0225701113 | 10 | 02257 | 1113 | 022571113 | 022571113 | 9
0225701114 | 10 | 02257 | 1114 | 022571114 | 022571114 | 9
0225701103 | 10 | 02257 | 1103 | 022571103 | 022571103 | 9
0225701111 | 10 | 02257 | 1111 | 022571111 | 022571111 | 9
0225701115 | 10 | 02257 | 1115 | 022571115 | 022571115 | 9
| 0 |  |  |  |  | 0
022600401 | 9 |  |  | 022600401 | 022600401 | 9
022600403 | 9 |  |  | 022600403 | 022600403 | 9
024130401 | 9 |  |  | 024130401 | 024130401 | 9
| 0 |  |  |  |  | 0
2528101102 | 10 | 25281 | 1102 | 252811102 | 252811102 | 9
022550401 | 9 |  |  | 022550401 | 022550401 | 9
0221001101 | 10 | 02210 | 1101 | 022101101 | 022101101 | 9
0221001102 | 10 | 02210 | 1102 | 022101102 | 022101102 | 9
0221001103 | 10 | 02210 | 1103 | 022101103 | 022101103 | 9
0221001104 | 10 | 02210 | 1104 | 022101104 | 022101104 | 9
0221001106 | 10 | 02210 | 1106 | 022101106 | 022101106 | 9
0837001101 | 10 | 08370 | 1101 | 083701101 | 083701101 | 9
0837001104 | 10 | 08370 | 1104 | 083701104 | 083701104 | 9
0837001105 | 10 | 08370 | 1105 | 083701105 | 083701105 | 9
0837001106 | 10 | 08370 | 1106 | 083701106 | 083701106 | 9
0837001107 | 10 | 08370 | 1107 | 083701107 | 083701107 | 9
0837001108 | 10 | 08370 | 1108 | 083701108 | 083701108 | 9
0837001109 | 10 | 08370 | 1109 | 083701109 | 083701109 | 9
0837001110 | 10 | 08370 | 1110 | 083701110 | 083701110 | 9
0833902102 | 10 | 08339 | 2102 | 083392102 | 083392102 | 9
0833902106 | 10 | 08339 | 2106 | 083392106 | 083392106 | 9
0221001107 | 10 | 02210 | 1107 | 022101107 | 022101107 | 9
0221001110 | 10 | 02210 | 1110 | 022101110 | 022101110 | 9
0833902107 | 10 | 08339 | 2107 | 083392107 | 083392107 | 9
0221001105 | 10 | 02210 | 1105 | 022101105 | 022101105 | 9
0221001108 | 10 | 02210 | 1108 | 022101108 | 022101108 | 9
012130401 | 9 |  |  | 012130401 | 012130401 | 9
012130402 | 9 |  |  | 012130402 | 012130402 | 9
012130403 | 9 |  |  | 012130403 | 012130403 | 9
012130404 | 9 |  |  | 012130404 | 012130404 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0221001109 | 10 | 02210 | 1109 | 022101109 | 022101109 | 9
0221001111 | 10 | 02210 | 1111 | 022101111 | 022101111 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
163801701 | 9 |  |  | 163801701 | 163801701 | 9
163801703 | 9 |  |  | 163801703 | 163801703 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0220301102 | 10 | 02203 | 1102 | 022031102 | 022031102 | 9
0220301105 | 10 | 02203 | 1105 | 022031105 | 022031105 | 9
0220301106 | 10 | 02203 | 1106 | 022031106 | 022031106 | 9
0220301107 | 10 | 02203 | 1107 | 022031107 | 022031107 | 9
0220301109 | 10 | 02203 | 1109 | 022031109 | 022031109 | 9
0220301110 | 10 | 02203 | 1110 | 022031110 | 022031110 | 9
0220301112 | 10 | 02203 | 1112 | 022031112 | 022031112 | 9
022031121 | 9 |  |  | 022031121 | 022031121 | 9
2529301104 | 10 | 25293 | 1104 | 252931104 | 252931104 | 9
1021101101 | 10 | 10211 | 1101 | 102111101 | 102111101 | 9
1021101102 | 10 | 10211 | 1102 | 102111102 | 102111102 | 9
253642104 | 9 |  |  | 253642104 | 253642104 | 9
012160401 | 9 |  |  | 012160401 | 012160401 | 9
012160402 | 9 |  |  | 012160402 | 012160402 | 9
2536701101 | 10 | 25367 | 1101 | 253671101 | 253671101 | 9
2536701102 | 10 | 25367 | 1102 | 253671102 | 253671102 | 9
2536701103 | 10 | 25367 | 1103 | 253671103 | 253671103 | 9
0836101104 | 10 | 08361 | 1104 | 083611104 | 083611104 | 9
0228701121 | 10 | 02287 | 1121 | 022871121 | 022871121 | 9
022871123 | 9 |  |  | 022871123 | 022871123 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0228701112 | 10 | 02287 | 1112 | 022871112 | 022871112 | 9
022871116 | 9 |  |  | 022871116 | 022871116 | 9
0228701119 | 10 | 02287 | 1119 | 022871119 | 022871119 | 9
0228701120 | 10 | 02287 | 1120 | 022871120 | 022871120 | 9
0228701122 | 10 | 02287 | 1122 | 022871122 | 022871122 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
022873411 | 9 |  |  | 022873411 | 022873411 | 9
| 0 |  |  |  |  | 0
0134701128 | 10 | 01347 | 1128 | 013471128 | 013471128 | 9
0134701130 | 10 | 01347 | 1130 | 013471130 | 013471130 | 9
0134701125 | 10 | 01347 | 1125 | 013471125 | 013471125 | 9
0134701119 | 10 | 01347 | 1119 | 013471119 | 013471119 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0220301101 | 10 | 02203 | 1101 | 022031101 | 022031101 | 9
0220301103 | 10 | 02203 | 1103 | 022031103 | 022031103 | 9
1027001101 | 10 | 10270 | 1101 | 102701101 | 102701101 | 9
1027001102 | 10 | 10270 | 1102 | 102701102 | 102701102 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
1027001103 | 10 | 10270 | 1103 | 102701103 | 102701103 | 9
0220301116 | 10 | 02203 | 1116 | 022031116 | 022031116 | 9
| 0 |  |  |  |  | 0
0220301104 | 10 | 02203 | 1104 | 022031104 | 022031104 | 9
0220301108 | 10 | 02203 | 1108 | 022031108 | 022031108 | 9
0220301111 | 10 | 02203 | 1111 | 022031111 | 022031111 | 9
0220301113 | 10 | 02203 | 1113 | 022031113 | 022031113 | 9
0220301114 | 10 | 02203 | 1114 | 022031114 | 022031114 | 9
0220301115 | 10 | 02203 | 1115 | 022031115 | 022031115 | 9
0220301117 | 10 | 02203 | 1117 | 022031117 | 022031117 | 9
0220301118 | 10 | 02203 | 1118 | 022031118 | 022031118 | 9
1028102101 | 10 | 10281 | 2101 | 102812101 | 102812101 | 9
1026001101 | 10 | 10260 | 1101 | 102601101 | 102601101 | 9
103330401 | 9 |  |  | 103330401 | 103330401 | 9
103330402 | 9 |  |  | 103330402 | 103330402 | 9
1033301103 | 10 | 10333 | 1103 | 103331103 | 103331103 | 9
1033301104 | 10 | 10333 | 1104 | 103331104 | 103331104 | 9
0220701101 | 10 | 02207 | 1101 | 022071101 | 022071101 | 9
0220701103 | 10 | 02207 | 1103 | 022071103 | 022071103 | 9
0220701105 | 10 | 02207 | 1105 | 022071105 | 022071105 | 9
0220701107 | 10 | 02207 | 1107 | 022071107 | 022071107 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
1034801101 | 10 | 10348 | 1101 | 103481101 | 103481101 | 9
1034801102 | 10 | 10348 | 1102 | 103481102 | 103481102 | 9
1035801101 | 10 | 10358 | 1101 | 103581101 | 103581101 | 9
1024901101 | 10 | 10249 | 1101 | 102491101 | 102491101 | 9
1024901102 | 10 | 10249 | 1102 | 102491102 | 102491102 | 9
1024901103 | 10 | 10249 | 1103 | 102491103 | 102491103 | 9
1033301101 | 10 | 10333 | 1101 | 103331101 | 103331101 | 9
1024901105 | 10 | 10249 | 1105 | 102491105 | 102491105 | 9
1033301102 | 10 | 10333 | 1102 | 103331102 | 103331102 | 9
1024901106 | 10 | 10249 | 1106 | 102491106 | 102491106 | 9
1032601101 | 10 | 10326 | 1101 | 103261101 | 103261101 | 9
1032601102 | 10 | 10326 | 1102 | 103261102 | 103261102 | 9
1032601103 | 10 | 10326 | 1103 | 103261103 | 103261103 | 9
1033101101 | 10 | 10331 | 1101 | 103311101 | 103311101 | 9
1033101102 | 10 | 10331 | 1102 | 103311102 | 103311102 | 9
1023601101 | 10 | 10236 | 1101 | 102361101 | 102361101 | 9
1029301101 | 10 | 10293 | 1101 | 102931101 | 102931101 | 9
1029301102 | 10 | 10293 | 1102 | 102931102 | 102931102 | 9
1029301103 | 10 | 10293 | 1103 | 102931103 | 102931103 | 9
2101092127 | 10 | 21010 | 2127 | 210102127 | 210102127 | 9
103491101 | 9 |  |  | 103491101 | 103491101 | 9
103491102 | 9 |  |  | 103491102 | 103491102 | 9
103721101 | 9 |  |  | 103721101 | 103721101 | 9
1523301108 | 10 | 15233 | 1108 | 152331108 | 152331108 | 9
1523301107 | 10 | 15233 | 1107 | 152331107 | 152331107 | 9
1523301105 | 10 | 15233 | 1105 | 152331105 | 152331105 | 9
| 0 |  |  |  |  | 0
02207406 | 8 | 02207 | 406 | 022070406 | 022070406 | 9
02207407 | 8 | 02207 | 407 | 022070407 | 022070407 | 9
02207408 | 8 | 02207 | 408 | 022070408 | 022070408 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0228701103 | 10 | 02287 | 1103 | 022871103 | 022871103 | 9
0228701106 | 10 | 02287 | 1106 | 022871106 | 022871106 | 9
| 0 |  |  |  |  | 0
0228701110 | 10 | 02287 | 1110 | 022871110 | 022871110 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0222201101 | 10 | 02222 | 1101 | 022221101 | 022221101 | 9
0222201102 | 10 | 02222 | 1102 | 022221102 | 022221102 | 9
0222201103 | 10 | 02222 | 1103 | 022221103 | 022221103 | 9
0222201104 | 10 | 02222 | 1104 | 022221104 | 022221104 | 9
0222201105 | 10 | 02222 | 1105 | 022221105 | 022221105 | 9
0222201106 | 10 | 02222 | 1106 | 022221106 | 022221106 | 9
0222201107 | 10 | 02222 | 1107 | 022221107 | 022221107 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
102021101 | 9 |  |  | 102021101 | 102021101 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0228001101 | 10 | 02280 | 1101 | 022801101 | 022801101 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0228001102 | 10 | 02280 | 1102 | 022801102 | 022801102 | 9
0228001103 | 10 | 02280 | 1103 | 022801103 | 022801103 | 9
0228001104 | 10 | 02280 | 1104 | 022801104 | 022801104 | 9
0228001105 | 10 | 02280 | 1105 | 022801105 | 022801105 | 9
0228001106 | 10 | 02280 | 1106 | 022801106 | 022801106 | 9
0228001112 | 10 | 02280 | 1112 | 022801112 | 022801112 | 9
0228001113 | 10 | 02280 | 1113 | 022801113 | 022801113 | 9
0228001121 | 10 | 02280 | 1121 | 022801121 | 022801121 | 9
0228001122 | 10 | 02280 | 1122 | 022801122 | 022801122 | 9
0228001123 | 10 | 02280 | 1123 | 022801123 | 022801123 | 9
0228001124 | 10 | 02280 | 1124 | 022801124 | 022801124 | 9
0228001125 | 10 | 02280 | 1125 | 022801125 | 022801125 | 9
0228001126 | 10 | 02280 | 1126 | 022801126 | 022801126 | 9
0228001129 | 10 | 02280 | 1129 | 022801129 | 022801129 | 9
1030301101 | 10 | 10303 | 1101 | 103031101 | 103031101 | 9
1030301102 | 10 | 10303 | 1102 | 103031102 | 103031102 | 9
1028301101 | 10 | 10283 | 1101 | 102831101 | 102831101 | 9
0228001130 | 10 | 02280 | 1130 | 022801130 | 022801130 | 9
0228001131 | 10 | 02280 | 1131 | 022801131 | 022801131 | 9
0228001132 | 10 | 02280 | 1132 | 022801132 | 022801132 | 9
0228001133 | 10 | 02280 | 1133 | 022801133 | 022801133 | 9
0228001134 | 10 | 02280 | 1134 | 022801134 | 022801134 | 9
1028301102 | 10 | 10283 | 1102 | 102831102 | 102831102 | 9
1028301106 | 10 | 10283 | 1106 | 102831106 | 102831106 | 9
1028301103 | 10 | 10283 | 1103 | 102831103 | 102831103 | 9
1028301104 | 10 | 10283 | 1104 | 102831104 | 102831104 | 9
1028301105 | 10 | 10283 | 1105 | 102831105 | 102831105 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
022530401 | 9 |  |  | 022530401 | 022530401 | 9
022530402 | 9 |  |  | 022530402 | 022530402 | 9
1034601102 | 10 | 10346 | 1102 | 103461102 | 103461102 | 9
1035601101 | 10 | 10356 | 1101 | 103561101 | 103561101 | 9
1035601102 | 10 | 10356 | 1102 | 103561102 | 103561102 | 9
1035201102 | 10 | 10352 | 1102 | 103521102 | 103521102 | 9
1035201103 | 10 | 10352 | 1103 | 103521103 | 103521103 | 9
1035201104 | 10 | 10352 | 1104 | 103521104 | 103521104 | 9
0228001108 | 10 | 02280 | 1108 | 022801108 | 022801108 | 9
0120202216 | 10 | 01202 | 2216 | 012022216 | 012022216 | 9
0120202218 | 10 | 01202 | 2218 | 012022218 | 012022218 | 9
0120202215 | 10 | 01202 | 2215 | 012022215 | 012022215 | 9
0120202217 | 10 | 01202 | 2217 | 012022217 | 012022217 | 9
0120202211 | 10 | 01202 | 2211 | 012022211 | 012022211 | 9
1524601101 | 10 | 15246 | 1101 | 152461101 | 152461101 | 9
0120202212 | 10 | 01202 | 2212 | 012022212 | 012022212 | 9
0120202214 | 10 | 01202 | 2214 | 012022214 | 012022214 | 9
0836101107 | 10 | 08361 | 1107 | 083611107 | 083611107 | 9
0836101108 | 10 | 08361 | 1108 | 083611108 | 083611108 | 9
1524601102 | 10 | 15246 | 1102 | 152461102 | 152461102 | 9
0120201103 | 10 | 01202 | 1103 | 012021103 | 012021103 | 9
0120201104 | 10 | 01202 | 1104 | 012021104 | 012021104 | 9
0836101109 | 10 | 08361 | 1109 | 083611109 | 083611109 | 9
022340402 | 9 |  |  | 022340402 | 022340402 | 9
022490401 | 9 |  |  | 022490401 | 022490401 | 9
022490402 | 9 |  |  | 022490402 | 022490402 | 9
022490403 | 9 |  |  | 022490403 | 022490403 | 9
012541102 | 9 |  |  | 012541102 | 012541102 | 9
022500401 | 9 |  |  | 022500401 | 022500401 | 9
022500402 | 9 |  |  | 022500402 | 022500402 | 9
022500403 | 9 |  |  | 022500403 | 022500403 | 9
022480401 | 9 |  |  | 022480401 | 022480401 | 9
022480402 | 9 |  |  | 022480402 | 022480402 | 9
022781103 | 9 |  |  | 022781103 | 022781103 | 9
022550402 | 9 |  |  | 022550402 | 022550402 | 9
022550403 | 9 |  |  | 022550403 | 022550403 | 9
022400401 | 9 |  |  | 022400401 | 022400401 | 9
022400402 | 9 |  |  | 022400402 | 022400402 | 9
022610401 | 9 |  |  | 022610401 | 022610401 | 9
022610402 | 9 |  |  | 022610402 | 022610402 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0120601102 | 10 | 01206 | 1102 | 012061102 | 012061102 | 9
0836701104 | 10 | 08367 | 1104 | 083671104 | 083671104 | 9
0836701105 | 10 | 08367 | 1105 | 083671105 | 083671105 | 9
0836701106 | 10 | 08367 | 1106 | 083671106 | 083671106 | 9
0836701107 | 10 | 08367 | 1107 | 083671107 | 083671107 | 9
0121001102 | 10 | 01210 | 1102 | 012101102 | 012101102 | 9
0121001104 | 10 | 01210 | 1104 | 012101104 | 012101104 | 9
0836701108 | 10 | 08367 | 1108 | 083671108 | 083671108 | 9
0836701109 | 10 | 08367 | 1109 | 083671109 | 083671109 | 9
0836701110 | 10 | 08367 | 1110 | 083671110 | 083671110 | 9
253642103 | 9 |  |  | 253642103 | 253642103 | 9
2536501111 | 10 | 25365 | 1111 | 253651111 | 253651111 | 9
2536501112 | 10 | 25365 | 1112 | 253651112 | 253651112 | 9
0120601103 | 10 | 01206 | 1103 | 012061103 | 012061103 | 9
0120601101 | 10 | 01206 | 1101 | 012061101 | 012061101 | 9
022801120 | 9 |  |  | 022801120 | 022801120 | 9
0228001128 | 10 | 02280 | 1128 | 022801128 | 022801128 | 9
022801135 | 9 |  |  | 022801135 | 022801135 | 9
022801136 | 9 |  |  | 022801136 | 022801136 | 9
022801107 | 9 |  |  | 022801107 | 022801107 | 9
0228001127 | 10 | 02280 | 1127 | 022801127 | 022801127 | 9
022801137 | 9 |  |  | 022801137 | 022801137 | 9
022801138 | 9 |  |  | 022801138 | 022801138 | 9
022801140 | 9 |  |  | 022801140 | 022801140 | 9
022801141 | 9 |  |  | 022801141 | 022801141 | 9
| 0 |  |  |  |  | 0
1030701104 | 10 | 10307 | 1104 | 103071104 | 103071104 | 9
1030701105 | 10 | 10307 | 1105 | 103071105 | 103071105 | 9
1030701106 | 10 | 10307 | 1106 | 103071106 | 103071106 | 9
1029701101 | 10 | 10297 | 1101 | 102971101 | 102971101 | 9
1029701102 | 10 | 10297 | 1102 | 102971102 | 102971102 | 9
1029701103 | 10 | 10297 | 1103 | 102971103 | 102971103 | 9
1029701104 | 10 | 10297 | 1104 | 102971104 | 102971104 | 9
1029701105 | 10 | 10297 | 1105 | 102971105 | 102971105 | 9
1029701107 | 10 | 10297 | 1107 | 102971107 | 102971107 | 9
1029701109 | 10 | 10297 | 1109 | 102971109 | 102971109 | 9
1029701110 | 10 | 10297 | 1110 | 102971110 | 102971110 | 9
1029701111 | 10 | 10297 | 1111 | 102971111 | 102971111 | 9
102650401 | 9 |  |  | 102650401 | 102650401 | 9
| 0 |  |  |  |  | 0
0223301101 | 10 | 02233 | 1101 | 022331101 | 022331101 | 9
0223301102 | 10 | 02233 | 1102 | 022331102 | 022331102 | 9
0223301103 | 10 | 02233 | 1103 | 022331103 | 022331103 | 9
0223301104 | 10 | 02233 | 1104 | 022331104 | 022331104 | 9
0223301105 | 10 | 02233 | 1105 | 022331105 | 022331105 | 9
0223301106 | 10 | 02233 | 1106 | 022331106 | 022331106 | 9
0223301107 | 10 | 02233 | 1107 | 022331107 | 022331107 | 9
0223301108 | 10 | 02233 | 1108 | 022331108 | 022331108 | 9
0223301109 | 10 | 02233 | 1109 | 022331109 | 022331109 | 9
0228001109 | 10 | 02280 | 1109 | 022801109 | 022801109 | 9
022801114 | 9 |  |  | 022801114 | 022801114 | 9
022801115 | 9 |  |  | 022801115 | 022801115 | 9
022801116 | 9 |  |  | 022801116 | 022801116 | 9
022801117 | 9 |  |  | 022801117 | 022801117 | 9
0120601105 | 10 | 01206 | 1105 | 012061105 | 012061105 | 9
022801110 | 9 |  |  | 022801110 | 022801110 | 9
0228001111 | 10 | 02280 | 1111 | 022801111 | 022801111 | 9
0228001119 | 10 | 02280 | 1119 | 022801119 | 022801119 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0220101105 | 10 | 02201 | 1105 | 022011105 | 022011105 | 9
0220101106 | 10 | 02201 | 1106 | 022011106 | 022011106 | 9
0220101112 | 10 | 02201 | 1112 | 022011112 | 022011112 | 9
0220101114 | 10 | 02201 | 1114 | 022011114 | 022011114 | 9
0220101115 | 10 | 02201 | 1115 | 022011115 | 022011115 | 9
0220101121 | 10 | 02201 | 1121 | 022011121 | 022011121 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0220101117 | 10 | 02201 | 1117 | 022011117 | 022011117 | 9
0220101123 | 10 | 02201 | 1123 | 022011123 | 022011123 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
022010401 | 9 |  |  | 022010401 | 022010401 | 9
022010402 | 9 |  |  | 022010402 | 022010402 | 9
0220101101 | 10 | 02201 | 1101 | 022011101 | 022011101 | 9
0220101102 | 10 | 02201 | 1102 | 022011102 | 022011102 | 9
022011104 | 9 |  |  | 022011104 | 022011104 | 9
0220101107 | 10 | 02201 | 1107 | 022011107 | 022011107 | 9
022011108 | 9 |  |  | 022011108 | 022011108 | 9
0220101109 | 10 | 02201 | 1109 | 022011109 | 022011109 | 9
022011110 | 9 |  |  | 022011110 | 022011110 | 9
0220101111 | 10 | 02201 | 1111 | 022011111 | 022011111 | 9
0220101113 | 10 | 02201 | 1113 | 022011113 | 022011113 | 9
022011116 | 9 |  |  | 022011116 | 022011116 | 9
022011118 | 9 |  |  | 022011118 | 022011118 | 9
022011120 | 9 |  |  | 022011120 | 022011120 | 9
022011124 | 9 |  |  | 022011124 | 022011124 | 9
022011125 | 9 |  |  | 022011125 | 022011125 | 9
1033901101 | 10 | 10339 | 1101 | 103391101 | 103391101 | 9
1033901102 | 10 | 10339 | 1102 | 103391102 | 103391102 | 9
1035401103 | 10 | 10354 | 1103 | 103541103 | 103541103 | 9
1035401104 | 10 | 10354 | 1104 | 103541104 | 103541104 | 9
1035401101 | 10 | 10354 | 1101 | 103541101 | 103541101 | 9
1035401102 | 10 | 10354 | 1102 | 103541102 | 103541102 | 9
1031901101 | 10 | 10319 | 1101 | 103191101 | 103191101 | 9
1032001101 | 10 | 10320 | 1101 | 103201101 | 103201101 | 9
1032001102 | 10 | 10320 | 1102 | 103201102 | 103201102 | 9
1032201101 | 10 | 10322 | 1101 | 103221101 | 103221101 | 9
| 0 |  |  |  |  | 0
1025201101 | 10 | 10252 | 1101 | 102521101 | 102521101 | 9
1025201102 | 10 | 10252 | 1102 | 102521102 | 102521102 | 9
1025201103 | 10 | 10252 | 1103 | 102521103 | 102521103 | 9
1025201104 | 10 | 10252 | 1104 | 102521104 | 102521104 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
024251103 | 9 |  |  | 024251103 | 024251103 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0833701112 | 10 | 08337 | 1112 | 083371112 | 083371112 | 9
0833701113 | 10 | 08337 | 1113 | 083371113 | 083371113 | 9
0833701114 | 10 | 08337 | 1114 | 083371114 | 083371114 | 9
0833701115 | 10 | 08337 | 1115 | 083371115 | 083371115 | 9
0836101105 | 10 | 08361 | 1105 | 083611105 | 083611105 | 9
1021201101 | 10 | 10212 | 1101 | 102121101 | 102121101 | 9
1021201102 | 10 | 10212 | 1102 | 102121102 | 102121102 | 9
022781101 | 9 |  |  | 022781101 | 022781101 | 9
022781103 | 9 |  |  | 022781103 | 022781103 | 9
022781102 | 9 |  |  | 022781102 | 022781102 | 9
022780401 | 9 |  |  | 022780401 | 022780401 | 9
022780402 | 9 |  |  | 022780402 | 022780402 | 9
022780403 | 9 |  |  | 022780403 | 022780403 | 9
022780404 | 9 |  |  | 022780404 | 022780404 | 9
0829901101 | 10 | 08299 | 1101 | 082991101 | 082991101 | 9
0829901102 | 10 | 08299 | 1102 | 082991102 | 082991102 | 9
022780405 | 9 |  |  | 022780405 | 022780405 | 9
0829901103 | 10 | 08299 | 1103 | 082991103 | 082991103 | 9
0829901104 | 10 | 08299 | 1104 | 082991104 | 082991104 | 9
022780407 | 9 |  |  | 022780407 | 022780407 | 9
022780408 | 9 |  |  | 022780408 | 022780408 | 9
0829901105 | 10 | 08299 | 1105 | 082991105 | 082991105 | 9
0141001101 | 10 | 01410 | 1101 | 014101101 | 014101101 | 9
0829901106 | 10 | 08299 | 1106 | 082991106 | 082991106 | 9
0829901107 | 10 | 08299 | 1107 | 082991107 | 082991107 | 9
0829901108 | 10 | 08299 | 1108 | 082991108 | 082991108 | 9
0829901109 | 10 | 08299 | 1109 | 082991109 | 082991109 | 9
0829901110 | 10 | 08299 | 1110 | 082991110 | 082991110 | 9
0836101106 | 10 | 08361 | 1106 | 083611106 | 083611106 | 9
0141001102 | 10 | 01410 | 1102 | 014101102 | 014101102 | 9
0141001105 | 10 | 01410 | 1105 | 014101105 | 014101105 | 9
013850401 | 9 |  |  | 013850401 | 013850401 | 9
0120202213 | 10 | 01202 | 2213 | 012022213 | 012022213 | 9
1524601103 | 10 | 15246 | 1103 | 152461103 | 152461103 | 9
012960401 | 9 |  |  | 012960401 | 012960401 | 9
0836101110 | 10 | 08361 | 1110 | 083611110 | 083611110 | 9
0836101111 | 10 | 08361 | 1111 | 083611111 | 083611111 | 9
1524601104 | 10 | 15246 | 1104 | 152461104 | 152461104 | 9
012960402 | 9 |  |  | 012960402 | 012960402 | 9
0134302206 | 10 | 01343 | 2206 | 013432206 | 013432206 | 9
0134302207 | 10 | 01343 | 2207 | 013432207 | 013432207 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0134302208 | 10 | 01343 | 2208 | 013432208 | 013432208 | 9
1524901101 | 10 | 15249 | 1101 | 152491101 | 152491101 | 9
1524901102 | 10 | 15249 | 1102 | 152491102 | 152491102 | 9
022280401 | 9 |  |  | 022280401 | 022280401 | 9
022280403 | 9 |  |  | 022280403 | 022280403 | 9
022280405 | 9 |  |  | 022280405 | 022280405 | 9
022280402 | 9 |  |  | 022280402 | 022280402 | 9
022280406 | 9 |  |  | 022280406 | 022280406 | 9
022280408 | 9 |  |  | 022280408 | 022280408 | 9
0834201106 | 10 | 08342 | 1106 | 083421106 | 083421106 | 9
0834201108 | 10 | 08342 | 1108 | 083421108 | 083421108 | 9
0834201109 | 10 | 08342 | 1109 | 083421109 | 083421109 | 9
083421110 | 9 |  |  | 083421110 | 083421110 | 9
0834201111 | 10 | 08342 | 1111 | 083421111 | 083421111 | 9
0834201112 | 10 | 08342 | 1112 | 083421112 | 083421112 | 9
0834201113 | 10 | 08342 | 1113 | 083421113 | 083421113 | 9
0135302225 | 10 | 01353 | 2225 | 013532225 | 013532225 | 9
0135302227 | 10 | 01353 | 2227 | 013532227 | 013532227 | 9
0135302107 | 10 | 01353 | 2107 | 013532107 | 013532107 | 9
0135302109 | 10 | 01353 | 2109 | 013532109 | 013532109 | 9
0135302226 | 10 | 01353 | 2226 | 013532226 | 013532226 | 9
0135302108 | 10 | 01353 | 2108 | 013532108 | 013532108 | 9
0143002102 | 10 | 01430 | 2102 | 014302102 | 014302102 | 9
0143002103 | 10 | 01430 | 2103 | 014302103 | 014302103 | 9
0836101112 | 10 | 08361 | 1112 | 083611112 | 083611112 | 9
0143002104 | 10 | 01430 | 2104 | 014302104 | 014302104 | 9
0143002105 | 10 | 01430 | 2105 | 014302105 | 014302105 | 9
0836101113 | 10 | 08361 | 1113 | 083611113 | 083611113 | 9
0143002106 | 10 | 01430 | 2106 | 014302106 | 014302106 | 9
0143002107 | 10 | 01430 | 2107 | 014302107 | 014302107 | 9
0143002108 | 10 | 01430 | 2108 | 014302108 | 014302108 | 9
0836101114 | 10 | 08361 | 1114 | 083611114 | 083611114 | 9
0836101115 | 10 | 08361 | 1115 | 083611115 | 083611115 | 9
0143002109 | 10 | 01430 | 2109 | 014302109 | 014302109 | 9
0829201108 | 10 | 08292 | 1108 | 082921108 | 082921108 | 9
0143002110 | 10 | 01430 | 2110 | 014302110 | 014302110 | 9
0146502104 | 10 | 01465 | 2104 | 014652104 | 014652104 | 9
0146502105 | 10 | 01465 | 2105 | 014652105 | 014652105 | 9
0146502106 | 10 | 01465 | 2106 | 014652106 | 014652106 | 9
0146502107 | 10 | 01465 | 2107 | 014652107 | 014652107 | 9
0146502108 | 10 | 01465 | 2108 | 014652108 | 014652108 | 9
0146502109 | 10 | 01465 | 2109 | 014652109 | 014652109 | 9
0146502110 | 10 | 01465 | 2110 | 014652110 | 014652110 | 9
1029101102 | 10 | 10291 | 1102 | 102911102 | 102911102 | 9
1029101103 | 10 | 10291 | 1103 | 102911103 | 102911103 | 9
1029101105 | 10 | 10291 | 1105 | 102911105 | 102911105 | 9
1029101106 | 10 | 10291 | 1106 | 102911106 | 102911106 | 9
014150401 | 9 |  |  | 014150401 | 014150401 | 9
1029101107 | 10 | 10291 | 1107 | 102911107 | 102911107 | 9
1029101109 | 10 | 10291 | 1109 | 102911109 | 102911109 | 9
1029101110 | 10 | 10291 | 1110 | 102911110 | 102911110 | 9
153711101 | 9 |  |  | 153711101 | 153711101 | 9
0834201102 | 10 | 08342 | 1102 | 083421102 | 083421102 | 9
0834201103 | 10 | 08342 | 1103 | 083421103 | 083421103 | 9
0834201104 | 10 | 08342 | 1104 | 083421104 | 083421104 | 9
0834201105 | 10 | 08342 | 1105 | 083421105 | 083421105 | 9
1537002109 | 10 | 15370 | 2109 | 153702109 | 153702109 | 9
153711102 | 9 |  |  | 153711102 | 153711102 | 9
153761101 | 9 |  |  | 153761101 | 153761101 | 9
153761102 | 9 |  |  | 153761102 | 153761102 | 9
1537601105 | 10 | 15376 | 1105 | 153761105 | 153761105 | 9
1528101101 | 10 | 15281 | 1101 | 152811101 | 152811101 | 9
1528101102 | 10 | 15281 | 1102 | 152811102 | 152811102 | 9
1528101104 | 10 | 15281 | 1104 | 152811104 | 152811104 | 9
1528101105 | 10 | 15281 | 1105 | 152811105 | 152811105 | 9
2525601101 | 10 | 25256 | 1101 | 252561101 | 252561101 | 9
0836301101 | 10 | 08363 | 1101 | 083631101 | 083631101 | 9
0836301102 | 10 | 08363 | 1102 | 083631102 | 083631102 | 9
0836301103 | 10 | 08363 | 1103 | 083631103 | 083631103 | 9
0836301104 | 10 | 08363 | 1104 | 083631104 | 083631104 | 9
0820301102 | 10 | 08203 | 1102 | 082031102 | 082031102 | 9
0820301103 | 10 | 08203 | 1103 | 082031103 | 082031103 | 9
0820301104 | 10 | 08203 | 1104 | 082031104 | 082031104 | 9
0820301105 | 10 | 08203 | 1105 | 082031105 | 082031105 | 9
0836301105 | 10 | 08363 | 1105 | 083631105 | 083631105 | 9
0836301106 | 10 | 08363 | 1106 | 083631106 | 083631106 | 9
0836301107 | 10 | 08363 | 1107 | 083631107 | 083631107 | 9
0836301108 | 10 | 08363 | 1108 | 083631108 | 083631108 | 9
2520801102 | 10 | 25208 | 1102 | 252081102 | 252081102 | 9
2526601105 | 10 | 25266 | 1105 | 252661105 | 252661105 | 9
253411106 | 9 |  |  | 253411106 | 253411106 | 9
253411107 | 9 |  |  | 253411107 | 253411107 | 9
2521701101 | 10 | 25217 | 1101 | 252171101 | 252171101 | 9
0836301109 | 10 | 08363 | 1109 | 083631109 | 083631109 | 9
0836301110 | 10 | 08363 | 1110 | 083631110 | 083631110 | 9
0836301111 | 10 | 08363 | 1111 | 083631111 | 083631111 | 9
0836301112 | 10 | 08363 | 1112 | 083631112 | 083631112 | 9
2521701102 | 10 | 25217 | 1102 | 252171102 | 252171102 | 9
2521701117 | 10 | 25217 | 1117 | 252171117 | 252171117 | 9
0820301106 | 10 | 08203 | 1106 | 082031106 | 082031106 | 9
0820301107 | 10 | 08203 | 1107 | 082031107 | 082031107 | 9
0820301108 | 10 | 08203 | 1108 | 082031108 | 082031108 | 9
0820301109 | 10 | 08203 | 1109 | 082031109 | 082031109 | 9
0820301110 | 10 | 08203 | 1110 | 082031110 | 082031110 | 9
0820301111 | 10 | 08203 | 1111 | 082031111 | 082031111 | 9
0820301112 | 10 | 08203 | 1112 | 082031112 | 082031112 | 9
0820301113 | 10 | 08203 | 1113 | 082031113 | 082031113 | 9
0820301114 | 10 | 08203 | 1114 | 082031114 | 082031114 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
022091102 | 9 |  |  | 022091102 | 022091102 | 9
022091101 | 9 |  |  | 022091101 | 022091101 | 9
0829201107 | 10 | 08292 | 1107 | 082921107 | 082921107 | 9
0829201109 | 10 | 08292 | 1109 | 082921109 | 082921109 | 9
0829201110 | 10 | 08292 | 1110 | 082921110 | 082921110 | 9
| 0 |  |  |  |  | 0
02209401 | 8 | 02209 | 401 | 022090401 | 022090401 | 9
02209403 | 8 | 02209 | 403 | 022090403 | 022090403 | 9
0838001101 | 10 | 08380 | 1101 | 083801101 | 083801101 | 9
02209405 | 8 | 02209 | 405 | 022090405 | 022090405 | 9
0838001103 | 10 | 08380 | 1103 | 083801103 | 083801103 | 9
02209407 | 8 | 02209 | 407 | 022090407 | 022090407 | 9
02209409 | 8 | 02209 | 409 | 022090409 | 022090409 | 9
0838001104 | 10 | 08380 | 1104 | 083801104 | 083801104 | 9
02209411 | 8 | 02209 | 411 | 022090411 | 022090411 | 9
02209413 | 8 | 02209 | 413 | 022090413 | 022090413 | 9
0838001105 | 10 | 08380 | 1105 | 083801105 | 083801105 | 9
02209402 | 8 | 02209 | 402 | 022090402 | 022090402 | 9
02209404 | 8 | 02209 | 404 | 022090404 | 022090404 | 9
02209406 | 8 | 02209 | 406 | 022090406 | 022090406 | 9
02209408 | 8 | 02209 | 408 | 022090408 | 022090408 | 9
02209410 | 8 | 02209 | 410 | 022090410 | 022090410 | 9
02209412 | 8 | 02209 | 412 | 022090412 | 022090412 | 9
02209414 | 8 | 02209 | 414 | 022090414 | 022090414 | 9
0838001106 | 10 | 08380 | 1106 | 083801106 | 083801106 | 9
0838001107 | 10 | 08380 | 1107 | 083801107 | 083801107 | 9
0838001108 | 10 | 08380 | 1108 | 083801108 | 083801108 | 9
0838001109 | 10 | 08380 | 1109 | 083801109 | 083801109 | 9
0838001110 | 10 | 08380 | 1110 | 083801110 | 083801110 | 9
0838001111 | 10 | 08380 | 1111 | 083801111 | 083801111 | 9
0838002114 | 10 | 08380 | 2114 | 083802114 | 083802114 | 9
0838002115 | 10 | 08380 | 2115 | 083802115 | 083802115 | 9
0838002116 | 10 | 08380 | 2116 | 083802116 | 083802116 | 9
0838002117 | 10 | 08380 | 2117 | 083802117 | 083802117 | 9
0838002118 | 10 | 08380 | 2118 | 083802118 | 083802118 | 9
0838002119 | 10 | 08380 | 2119 | 083802119 | 083802119 | 9
02226402 | 8 | 02226 | 402 | 022260402 | 022260402 | 9
022260404 | 9 |  |  | 022260404 | 022260404 | 9
022260406 | 9 |  |  | 022260406 | 022260406 | 9
022260408 | 9 |  |  | 022260408 | 022260408 | 9
02226401 | 8 | 02226 | 401 | 022260401 | 022260401 | 9
022260403 | 9 |  |  | 022260403 | 022260403 | 9
02226405 | 8 | 02226 | 405 | 022260405 | 022260405 | 9
022260407 | 9 |  |  | 022260407 | 022260407 | 9
022260409 | 9 |  |  | 022260409 | 022260409 | 9
0833902108 | 10 | 08339 | 2108 | 083392108 | 083392108 | 9
254071108 | 9 |  |  | 254071108 | 254071108 | 9
0829201101 | 10 | 08292 | 1101 | 082921101 | 082921101 | 9
0829201102 | 10 | 08292 | 1102 | 082921102 | 082921102 | 9
0829201103 | 10 | 08292 | 1103 | 082921103 | 082921103 | 9
0829201104 | 10 | 08292 | 1104 | 082921104 | 082921104 | 9
0829201105 | 10 | 08292 | 1105 | 082921105 | 082921105 | 9
0829201111 | 10 | 08292 | 1111 | 082921111 | 082921111 | 9
0829201112 | 10 | 08292 | 1112 | 082921112 | 082921112 | 9
0829201113 | 10 | 08292 | 1113 | 082921113 | 082921113 | 9
0829201114 | 10 | 08292 | 1114 | 082921114 | 082921114 | 9
0829201116 | 10 | 08292 | 1116 | 082921116 | 082921116 | 9
0829201117 | 10 | 08292 | 1117 | 082921117 | 082921117 | 9
0829201118 | 10 | 08292 | 1118 | 082921118 | 082921118 | 9
0829201119 | 10 | 08292 | 1119 | 082921119 | 082921119 | 9
022130403 | 9 |  |  | 022130403 | 022130403 | 9
022130406 | 9 |  |  | 022130406 | 022130406 | 9
022270401 | 9 |  |  | 022270401 | 022270401 | 9
253911107 | 9 |  |  | 253911107 | 253911107 | 9
2528201105 | 10 | 25282 | 1105 | 252821105 | 252821105 | 9
| 0 |  |  |  |  | 0
022270403 | 9 |  |  | 022270403 | 022270403 | 9
022270402 | 9 |  |  | 022270402 | 022270402 | 9
022270404 | 9 |  |  | 022270404 | 022270404 | 9
022270405 | 9 |  |  | 022270405 | 022270405 | 9
022270406 | 9 |  |  | 022270406 | 022270406 | 9
02213401 | 8 | 02213 | 401 | 022130401 | 022130401 | 9
02213405 | 8 | 02213 | 405 | 022130405 | 022130405 | 9
02213407 | 8 | 02213 | 407 | 022130407 | 022130407 | 9
02213409 | 8 | 02213 | 409 | 022130409 | 022130409 | 9
02213411 | 8 | 02213 | 411 | 022130411 | 022130411 | 9
02213402 | 8 | 02213 | 402 | 022130402 | 022130402 | 9
02213404 | 8 | 02213 | 404 | 022130404 | 022130404 | 9
02213408 | 8 | 02213 | 408 | 022130408 | 022130408 | 9
02213410 | 8 | 02213 | 410 | 022130410 | 022130410 | 9
| 0 |  |  |  |  | 0
022781102 | 9 |  |  | 022781102 | 022781102 | 9
022781101 | 9 |  |  | 022781101 | 022781101 | 9
| 0 |  |  |  |  | 0
0120601104 | 10 | 01206 | 1104 | 012061104 | 012061104 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
012541103 | 9 |  |  | 012541103 | 012541103 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
0134701118 | 10 | 01347 | 1118 | 013471118 | 013471118 | 9
0134701120 | 10 | 01347 | 1120 | 013471120 | 013471120 | 9
0134701121 | 10 | 01347 | 1121 | 013471121 | 013471121 | 9
0134701123 | 10 | 01347 | 1123 | 013471123 | 013471123 | 9
0134701124 | 10 | 01347 | 1124 | 013471124 | 013471124 | 9
0134701122 | 10 | 01347 | 1122 | 013471122 | 013471122 | 9
0134701127 | 10 | 01347 | 1127 | 013471127 | 013471127 | 9
0134701129 | 10 | 01347 | 1129 | 013471129 | 013471129 | 9
0430501101 | 10 | 04305 | 1101 | 043051101 | 043051101 | 9
2585901101 | 10 | 25859 | 1101 | 258591101 | 258591101 | 9
2531601112 | 10 | 25316 | 1112 | 253161112 | 253161112 | 9
0836701113 | 10 | 08367 | 1113 | 083671113 | 083671113 | 9
0836701114 | 10 | 08367 | 1114 | 083671114 | 083671114 | 9
0420201102 | 10 | 04202 | 1102 | 042021102 | 042021102 | 9
0420201103 | 10 | 04202 | 1103 | 042021103 | 042021103 | 9
042021104 | 9 |  |  | 042021104 | 042021104 | 9
0420201109 | 10 | 04202 | 1109 | 042021109 | 042021109 | 9
0420201110 | 10 | 04202 | 1110 | 042021110 | 042021110 | 9
| 0 |  |  |  |  | 0
0420201112 | 10 | 04202 | 1112 | 042021112 | 042021112 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
012090401 | 9 |  |  | 012090401 | 012090401 | 9
012090408 | 9 |  |  | 012090408 | 012090408 | 9
083421107 | 9 |  |  | 083421107 | 083421107 | 9
012111103 | 9 |  |  | 012111103 | 012111103 | 9
0121101104 | 10 | 01211 | 1104 | 012111104 | 012111104 | 9
0121101106 | 10 | 01211 | 1106 | 012111106 | 012111106 | 9
012111108 | 9 |  |  | 012111108 | 012111108 | 9
| 0 |  |  |  |  | 0
02412401 | 8 | 02412 | 401 | 024120401 | 024120401 | 9
02412402 | 8 | 02412 | 402 | 024120402 | 024120402 | 9
| 0 |  |  |  |  | 0
| 0 |  |  |  |  | 0
02412403 | 8 | 02412 | 403 | 024120403 | 024120403 | 9
02412404 | 8 | 02412 | 404 | 024120404 | 024120404 | 9
024161103 | 9 |  |  | 024161103 | 024161103 | 9
024130403 | 9 |  |  | 024130403 | 024130403 | 9
024130404 | 9 |  |  | 024130404 | 024130404 | 9
024130402 | 9 |  |  | 024130402 | 024130402 | 9
0834801102 | 10 | 08348 | 1102 | 083481102 | 083481102 | 9
0834801103 | 10 | 08348 | 1103 | 083481103 | 083481103 | 9
0834801104 | 10 | 08348 | 1104 | 083481104 | 083481104 | 9
0834801105 | 10 | 08348 | 1105 | 083481105 | 083481105 | 9
0834801106 | 10 | 08348 | 1106 | 083481106 | 083481106 | 9
0834801107 | 10 | 08348 | 1107 | 083481107 | 083481107 | 9
0834801108 | 10 | 08348 | 1108 | 083481108 | 083481108 | 9
0834801109 | 10 | 08348 | 1109 | 083481109 | 083481109 | 9
0834801110 | 10 | 08348 | 1110 | 083481110 | 083481110 | 9
0834801111 | 10 | 08348 | 1111 | 083481111 | 083481111 | 9
0834801112 | 10 | 08348 | 1112 | 083481112 | 083481112 | 9
0834801113 | 10 | 08348 | 1113 | 083481113 | 083481113 | 9
2527601116 | 10 | 25276 | 1116 | 252761116 | 252761116 | 9
| 0 |  |  |  |  | 0
1824002107 | 10 | 18240 | 2107 | 182402107 | 182402107 | 9
183011101 | 9 |  |  | 183011101 | 183011101 | 9
1830101102 | 10 | 18301 | 1102 | 183011102 | 183011102 | 9
1821301101 | 10 | 18213 | 1101 | 182131101 | 182131101 | 9
1821301102 | 10 | 18213 | 1102 | 182131102 | 182131102 | 9
251511101 | 9 |  |  | 251511101 | 251511101 | 9
1828502203 | 10 | 18285 | 2203 | 182852203 | 182852203 | 9
022101112 | 9 |  |  | 022101112 | 022101112 | 9
255361112 | 9 |  |  | 255361112 | 255361112 | 9